## Hold Register
Holding Registers, Function code 03/10
Address Register | Parameter | Modbus Protocol Start Address(Hex) |  | Valid Range | Mode
|  | Hi Byte | Lo Byte
40001 | Demand Time | 00 | 00 | Read minutes into first demand calculation. When the Demand Time reaches the Demand Period then the demand values are valid. Length : 4 byte Data Format : Float | ro
40003 | Demand Period | 00 | 02 | Write demand period: 0~60 minutes.Default 60. Setting the period to 0 will cause the “Phase # current demand” parameters to show the “Phase # current values”; and “Max. phase # current demand” to show the maximum value of the “Phase # current” parameter since last demand reset. Length : 4 byte Data Format : Float | r/w
40011 | System Type | 00 | 0A | Write system type: 3p4w = 3, 3p3w = 2 &1p2w= 1 Default, 3 Length : 4 byte Data Format : Float (KPPA is asked) | r/w
40013 | Pulse 1 Width | 00 | OC | Write pulse on period in milliseconds: 60, 100 or 200, default 200. Length : 4 byte Data Format : Float | r/w
40015 | Key Parameter Programming Authorization (KPPA) | 00 | 0E | Read: to get the status of the KPPA 0 = not authorized；1 = authorized Write the correct password to get KPPA,enable to program key parameters. Length : 4 byte Data Format : Float | r/w
40019 | Parity and Stop bits | 00 | 12 | Write the network port parity/stop bits for MODBUS Protocol, where: 0 = One stop bit and no parity, default. 1 = One stop bit and even parity. 2 = One stop bit and odd parity.3 = Two stop bits and no parity. Length : 4 byte Data Format : Float | r/w
40021 | Modbus Address | 00 | 14 | Write the network port node Address: 1 to 247 for MODBUS Protocol, default 1. Length : 4 byte Data Format : Float | r/w
40023 | Pulse 1 Rate | 00 | 16 | Write pulse rate index: n= 0 to 6 0- - 0.001 kwh/imp,(default) 1--0.01kwh/imp 2--0.1kwh/imp 3--1kwh/imp 4-10kwh/imp 5-100kwh/imp 6-1000kwh/imp Length : 4 byte Data Format : Float | r/w
40025 | Password | 00 | 18 | Read: to get the password of the meter Write: to program the new password of the meter Default 1000 Length : 4 byte Data Format : Float | r/w
40029 | Network Baud Rate | 00 | 1C | Write the network port baud rate for MODBUS Protocol, where: 0= 2400 baud. 1 = 4800 baud. 2= 9600 baud, (default) 3= 19200 baud. 4 = 38400 baud 5= 1200 band Length : 4 byte Data Format : Float | r/w
40063 | CT ratio | 00 | 3E | CT Ratio range: 1~2000 CT Ratio = primary current /secondary current Requires password Length: 4 bytes Data Format: Float | r/w
40065 | PT ratio | 00 | 40 | PT Ratio range:1~2000 PT ratio= primary voltage /secondary voltage Requires password Length: 4 bytes Data Format: Float | r/w
40087 | Pulse 1 Energy Type | 00 | 56 | Write MODBUS Protocol input parameter for pulse output 1： 1: import active energy 2: total active energy 4: export active energy, (default) 5: import reactive energy 6: total reactive energy 8: export reactive energy Length : 4 byte Data Format : Float | r/w
461457 | Reset | F0 | 10 | 00 00 : reset the demand informaiton 00 03 : reset energy information Length : 2 byte Data Format:Hex | wo
464513 | Serial number | FC | 00 | Serial number Length: 4 bytes Data Format:Unsigned Int 32 | ro

## Input Register
Input Registers, Function code 04
Address (Register) | Input Register Parameter |  |  |  | Modbus Protocol Start Address(Hex) |  | 3Ø | 3Ø | 1Ø
| Description | Length （byte） | Data Format | Units | Hi byte | Lo byte | 4W | 3W | 2W
30001 | Phase 1 line to neutral volts | 4 | Float | V | 00 | 00 | ● | - | ●
30003 | Phase 2 line to neutral volts | 4 | Float | V | 00 | 02 | ● | - | -
30005 | Phase 3 line to neutral volts | 4 | Float | V | 00 | 04 | ● | - | -
30007 | Phase 1 current | 4 | Float | A | 00 | 06 | ● | ● | ●
30009 | Phase 2 current | 4 | Float | A | 00 | 08 | ● | ● | -
30011 | Phase 3 current | 4 | Float | A | 00 | 0A | ● | ● | -
30013 | Phase 1 active power | 4 | Float | W | 00 | 0C | ● | - | ●
30015 | Phase 2 active power | 4 | Float | W | 00 | 0E | ● | - | -
30017 | Phase 3 active power | 4 | Float | W | 00 | 10 | ● | - | -
30019 | Phase 1 apparent power | 4 | Float | VA | 00 | 12 | ● | - | ●
30021 | Phase 2 apparent power | 4 | Float | VA | 00 | 14 | ● | - | -
30023 | Phase 3 apparent power | 4 | Float | VA | 00 | 16 | ● | - | -
30025 | Phase 1 reactive power | 4 | Float | VAr | 00 | 18 | ● | - | ●
30027 | Phase 2 reactive power | 4 | Float | VAr | 00 | 1A | ● | - | -
30029 | Phase 3 reactive power | 4 | Float | VAr | 00 | 1C | ● | - | -
30031 | Phase 1 power factor(1) | 4 | Float | None | 00 | 1E | ● | - | ●
30033 | Phase 2 power factor(1) | 4 | Float | None | 00 | 20 | ● | - | -
30035 | Phase 3 power factor(1) | 4 | Float | None | 00 | 22 | ● | - | -
30037 | Phase 1 phase angle | 4 | Float | Degrees | 00 | 24 | ● | - | ●
30039 | Phase 2 phase angle | 4 | Float | Degrees | 00 | 26 | ● | - | -
30041 | Phase 3 phase angle | 4 | Float | Degrees | 00 | 28 | ● | - | -
30043 | Average line to neutral volts | 4 | Float | V | 00 | 2A | ● | - | -
30047 | Average line current | 4 | Float | A | 00 | 2E | ● | ● | ●
30049 | Sum of line currents | 4 | Float | A | 00 | 30 | ● | ● | ●
30053 | Total system power | 4 | Float | W | 00 | 34 | ● | ● | ●
30057 | Total system volt amps | 4 | Float | VA | 00 | 38 | ● | ● | ●
30061 | Total system Var | 4 | Float | VAr | 00 | 3C | ● | ● | ●
30063 | Total system power factor(1) | 4 | Float | None | 00 | 3E | ● | ● | ●
30067 | Total system phase angle | 4 | Float | Degrees | 00 | 42 | ● | ● | ●
30071 | Frequency of supply voltages | 4 | Float | Hz | 00 | 46 | ● | ● | ●
30073 | Import Wh since last reset | 4 | Float | kWh | 00 | 48 | ● | ● | ●
30075 | E-port Wh since last reset | 4 | Float | kWH | 00 | 4A | ● | ● | ●
30077 | Import VArh since last reset | 4 | Float | kVArh | 00 | 4C | ● | ● | ●
30079 | E-port VArh since last reset | 4 | Float | kVArh | 00 | 4E | ● | ● | ●
30081 | VAh since last reset | 4 | Float | kVAh | 00 | 50 | ● | ● | ●
30083 | Ah since last reset | 4 | Float | Ah | 00 | 52 | ● | ● | ●
30085 | Total system power demand(2) | 4 | Float | W | 00 | 54 | ● | ● | ●
30087 | Ma-imum total system power demand(2) | 4 | Float | W | 00 | 56 | ● | ● | ●
30101 | Total system VA demand | 4 | Float | VA | 00 | 64 | ● | ● | ●
30103 | Ma-imum total system VA demand | 4 | Float | VA | 00 | 66 | ● | ● | ●
30105 | Neutral current demand | 4 | Float | Amps | 00 | 68 | ● | - | -
30107 | Ma-imum neutral current demand | 4 | Float | Amps | 00 | 6A | ● | - | -
30109 | Total system reactive power demand(2) | 4 | Float | VAr | 00 | 6C | ● | - | ●
30111 | Ma-imum total system reactive power demand(2) | 4 | Float | VAr | 00 | 6E | ● | - | ●
30201 | Line 1 to Line 2 volts | 4 | Float | V | 00 | C8 | ● | ● | -
30203 | Line 2 to Line 3 volts | 4 | Float | V | 00 | CA | ● | ● | -
30205 | Line 3 to Line 1 volts | 4 | Float | V | 00 | CC | ● | ● | -
30207 | Average line to line volts | 4 | Float | V | 00 | CE | ● | ● | -
30225 | Neutral current | 4 | Float | A | 00 | E0 | ● | - | -
30235 | Phase 1 L/N volts THD | 4 | Float | % | 00 | EA | ● | - | ●
30237 | Phase 2 L/N volts THD | 4 | Float | % | 00 | EC | ● | - | -
30239 | Phase 3 L/N volts THD | 4 | Float | % | 00 | EE | ● | - | -
30241 | Phase 1 Current THD | 4 | Float | % | 00 | F0 | ● | ● | ●
30243 | Phase 2 Current THD | 4 | Float | % | 00 | F2 | ● | ● | -
30245 | Phase 3 Current THD | 4 | Float | % | 00 | F4 | ● | ● | -
30249 | Average line to neutral volts THD | 4 | Float | % | 00 | F8 | ● | - | ●
30251 | Average line current THD | 4 | Float | % | 00 | FA | ● | ● | ●
30259 | Phase 1 current demand | 4 | Float | A | 01 | 02 | ● | ● | ●
30261 | Phase 2 current demand | 4 | Float | A | 01 | 04 | ● | ● | -
30263 | Phase 3 current demand | 4 | Float | A | 01 | 06 | ● | ● | -
30265 | Ma-imum phase 1 current demand | 4 | Float | A | 01 | 08 | ● | ● | ●
30267 | Ma-imum phase 2 current demand | 4 | Float | A | 01 | 0A | ● | ● | -
30269 | Ma-imum phase 3 current demand | 4 | Float | A | 01 | 0C | ● | ● | -
30335 | Line 1 to line 2 volts THD | 4 | Float | ％ | 01 | 4E | ● | ● | -
30337 | Line 2 to line 3 volts THD | 4 | Float | ％ | 01 | 50 | ● | ● | -
30339 | Line 3 to line 1 volts THD | 4 | Float | ％ | 01 | 52 | ● | ● | -
30341 | Average line to line volts THD | 4 | Float | ％ | 01 | 54 | ● | ● | -
30343 | Total kwh(3) | 4 | Float | kWh | 01 | 56 | ● | ● | ●
30345 | Total kvarh(3) | 4 | Float | kVArh | 01 | 58 | ● | ● | ●
30347 | L1 import kwh | 4 | Float | kWh | 01 | 5A | ● | ● | ●
30349 | L2 import kwh | 4 | Float | kWh | 01 | 5C | ● | ● | -
30351 | L3 import kWh | 4 | Float | kWh | 01 | 5E | ● | ● | -
30353 | L1 e-port kWh | 4 | Float | kWh | 01 | 60 | ● | ● | ●
30355 | L2 e-port kwh | 4 | Float | kWh | 01 | 62 | ● | ● | -
30357 | L3 e-port kWh | 4 | Float | kWh | 01 | 64 | ● | ● | -
30359 | L1 total kwh | 4 | Float | kWh | 01 | 66 | ● | ● | ●
30361 | L2 total kWh | 4 | Float | kWh | 01 | 68 | ● | ● | -
30363 | L3 total kwh | 4 | Float | kWh | 01 | 6A | ● | ● | -
30365 | L1 import kvarh | 4 | Float | kVArh | 01 | 6C | ● | ● | ●
30367 | L2 import kvarh | 4 | Float | kVArh | 01 | 6E | ● | ● | -
30369 | L3 import kvarh | 4 | Float | kVArh | 01 | 70 | ● | ● | -
30371 | L1 e-port kvarh | 4 | Float | kVArh | 01 | 72 | ● | ● | ●
30373 | L2 e-port kvarh | 4 | Float | kVArh | 01 | 74 | ● | ● | -
30375 | L3 e-port kvarh | 4 | Float | kVArh | 01 | 76 | ● | ● | -
30377 | L1 total kvarh | 4 | Float | kVArh | 01 | 78 | ● | ● | ●
30379 | L2 total kvarh | 4 | Float | kVArh | 01 | 7A | ● | ● | -
30381 | L3 total kvarh | 4 | Float | kVArh | 01 | 7C | ● | ● | -
Notes:
1. The power factor has its sign adjusted to indicate the direction of the current. Positive refers to forward current, negative refers to reverse current.
2. The power sum demand calculation is for import – export.
3.Total kWh / kVarh equals to Import + export.