## Tabelle1
Modbus address list
Energy Logger D550
Parameter
Adress | Format | RD/WR | Unit | Note | Adjustment Area | Default
0 | INT |  |  |  | Time in UTC
2 | SHORT | RD/WR | kbps | Baudrate 0=9.6, 1=19.2, 2=38.4, 3=57.6, 4=115.2 kbps | 0...7 | 4
3 | SHORT | RD/WR | - | Master/Slave: 0=Slave, 1=Master | 0, 1 | 0
4 | SHORT | RD/WR | - | Stopbits: 0=1Bit, 1=2Bits | 0, 1 | 0
5 | UINT | RD/WR | - | IP Device address | 0...(232 -1)
7 | UINT | RD/WR | - | IP Gateway address | 0...(232 -1)
9 | UINT | RD/WR | - | Netmask | 0...(232 -1)
11 | SHORT | RD/WR | - | DHCP mode: 0=Fixed IP, 1=BootP, 2=DHCP, 3=Fixed IP with ARP-Probe and Gratuitous-ARP, 4=BootP with ARP-Probe and Gratuitous-ARP, 5=DHCP with ARP-Probe and Gratuitous-ARP | 0...5 | 0
12 | SHORT | RD | - | Boot release | -
13 | SHORT | RD/WR | - | NTP-Modus: 0=off, 1=listen, 2=active | 0...2 | 0
14 | UINT | RD/WR | - | NTP Server adress | 0...(232 - 1)
100 | UINT | RD | - | Serial number | -
116 | SHORT | RD/WR | - | Reset Counter | 0...32767
117 | SHORT | RD/WR | - | Reset Energy | 0...32768
121 | SHORT | RD/WR | - | Digital output 1 inverter, 0=disable, 1=active | 0, 1 | 0
122 | SHORT | RD/WR | - | Digital output 2 inverter, 0=disable, 1=active | 0, 1 | 0
123 | SHORT | RD/WR | - | Digital output 3 inverter, 0=disable, 1=active | 0, 1 | 0
124 | SHORT | RD/WR | - | Digital output 1: Output for temperature control, 0=disable, 1=active | 0, 1 | 0
125 | FLOAT | RD/WR | °C | Temperature offset | -50...50
157 | SHORT | RD |  | Software release | -
200 | STRING | RD/WR | - | Digital input 1 value name | GridVis
216 | STRING | RD/WR | - | Digital input 2 value name | GridVis
232 | STRING | RD/WR | - | Digital input 3 value name | GridVis
248 | STRING | RD/WR | - | Digital input 4 value name | GridVis
264 | STRING | RD/WR | - | Digital input 5 value name | GridVis
280 | STRING | RD/WR | - | Digital input 6 value name | GridVis
296 | STRING | RD/WR | - | Digital input 7 value name | GridVis
312 | STRING | RD/WR | - | Digital input 8 value name | GridVis
328 | STRING | RD/WR | - | Digital input 9 value name | GridVis
344 | STRING | RD/WR | - | Digital input 10 value name | GridVis
360 | STRING | RD/WR | - | Digital input 11 value name | GridVis
376 | STRING | RD/WR | - | Digital input 12 value name | GridVis
392 | STRING | RD/WR | - | Digital input 13 value name | GridVis
408 | STRING | RD/WR | - | Digital input 14 value name | GridVis
424 | STRING | RD/WR | - | Digital input 15 value name | GridVis
440 | STRING | RD/WR | - | Digital input 1 value unit | GridVis
456 | STRING | RD/WR | - | Digital input 2 value unit | GridVis
472 | STRING | RD/WR | - | Digital input 3 value unit | GridVis
488 | STRING | RD/WR | - | Digital input 4 value unit | GridVis
504 | STRING | RD/WR | - | Digital input 5 value unit | GridVis
520 | STRING | RD/WR | - | Digital input 6 value unit | GridVis
536 | STRING | RD/WR | - | Digital input 7 value unit | GridVis
552 | STRING | RD/WR | - | Digital input 8 value unit | GridVis
568 | STRING | RD/WR | - | Digital input 9 value unit | GridVis
584 | STRING | RD/WR | - | Digital input 10 value unit | GridVis
600 | STRING | RD/WR | - | Digital input 11 value unit | GridVis
616 | STRING | RD/WR | - | Digital input 12 value unit | GridVis
632 | STRING | RD/WR | - | Digital input 13 value unit | GridVis
648 | STRING | RD/WR | - | Digital input 14 value unit | GridVis
664 | STRING | RD/WR | - | Digital input 15 value unit | GridVis
700 | STRING | RD/WR | - | Digital input 1 value description | GridVis
732 | STRING | RD/WR | - | Digital input 2 value description | GridVis
764 | STRING | RD/WR | - | Digital input 3 value description | GridVis
796 | STRING | RD/WR | - | Digital input 4 value description | GridVis
828 | STRING | RD/WR | - | Digital input 5 value description | GridVis
860 | STRING | RD/WR | - | Digital input 6 value description | GridVis
892 | STRING | RD/WR | - | Digital input 7 value description | GridVis
924 | STRING | RD/WR | - | Digital input 8 value description | GridVis
956 | STRING | RD/WR | - | Digital input 9 value description | GridVis
988 | STRING | RD/WR | - | Digital input 10 value description | GridVis
1020 | STRING | RD/WR | - | Digital input 11 value description | GridVis
1052 | STRING | RD/WR | - | Digital input 12 value description | GridVis
1084 | STRING | RD/WR | - | Digital input 13 value description | GridVis
1116 | STRING | RD/WR | - | Digital input 14 value description | GridVis
1148 | STRING | RD/WR | - | Digital input 15 value description | GridVis
1700 | SHORT | RD/WR | - | Tariff 1 for digital input, 0=disable, 1=active | 0, 1 | 0
1701 | SHORT | RD/WR | - | Tariff 2 for digital input, 0=disable, 1=active | 0, 1 | 0
1702 | SHORT | RD/WR | - | Tariff 3 for digital input, 0=disable, 1=active | 0, 1 | 0
1703 | SHORT | RD/WR | - | Tariff 4 for digital input, 0=disable, 1=active | 0, 1 | 0
1704 | SHORT | RD/WR | - | Tariff 5 for digital input, 0=disable, 1=active | 0, 1 | 0
1705 | SHORT | RD/WR | - | Tariff 6 for digital input, 0=disable, 1=active | 0, 1 | 0
1706 | SHORT | RD/WR | - | Tariff 7 for digital input, 0=disable, 1=active | 0, 1 | 0
1707 | SHORT | RD/WR | - | Tariff 8 for digital input, 0=disable, 1=active | 0, 1 | 0
1708 | SHORT | RD/WR | - | Digital output 1: Polarity, 0=current flow if active (NOC), 1=current flow if not active (NCC) | 0, 1 | 0
1709 | SHORT | RD/WR | - | Digital output 2: Polarity, 0=current flow if active (NOC), 1=current flow if not active (NCC) | 0, 1 | 0
1710 | SHORT | RD/WR | - | Digital output 3: Polarity, 0=current flow if active (NOC), 1=current flow if not active (NCC) | 0, 1 | 0
1712 | STRING | RD/WR | 64 | Device name (factory settings: Typ + serial number)
1744 | STRING | RD/WR | 256 | Device description
1872 | FLOAT | RD/WR | - | Digital input 1: Scale factor | 0...1000000000.0
1874 | FLOAT | RD/WR | - | Digital input 2: Scale factor | 0...1000000000.0
1876 | FLOAT | RD/WR | - | Digital input 3: Scale factor | 0...1000000000.0
1878 | FLOAT | RD/WR | - | Digital input 4: Scale factor | 0...1000000000.0
1880 | FLOAT | RD/WR | - | Digital input 5: Scale factor | 0...1000000000.0
1882 | FLOAT | RD/WR | - | Digital input 6: Scale factor | 0...1000000000.0
1884 | FLOAT | RD/WR | - | Digital input 7: Scale factor | 0...1000000000.0
1886 | FLOAT | RD/WR | - | Digital input 8: Scale factor | 0...1000000000.0
1888 | FLOAT | RD/WR | - | Digital input 9: Scale factor | 0...1000000000.0
1890 | FLOAT | RD/WR | - | Digital input 10: Scale factor | 0...1000000000.0
1892 | FLOAT | RD/WR | - | Digital input 11: Scale factor | 0...1000000000.0
1894 | FLOAT | RD/WR | - | Digital input 12: Scale factor | 0...1000000000.0
1896 | FLOAT | RD/WR | - | Digital input 13: Scale factor | 0...1000000000.0
1898 | FLOAT | RD/WR | - | Digital input 14: Scale factor | 0...1000000000.0
1900 | FLOAT | RD/WR | - | Digital input 15: Scale factor | 0...1000000000.0
1902 | FLOAT | RD/WR | °C | Temperature input: Threshold temperature | -1...500.0
1904 | FLOAT | RD/WR | °C | Temperature input: Hysteresis | 0...500.0
1906 | INT | RD/WR | - | Temperature sensor: 0=PT100, 1=PT1000, 2=KTY83, 3=KTY84 | 0...3
1908 | SHORT | RD/WR | sec | Temperature input: Minimum exceeding time | 0...3600.0
1909 | SHORT | RD/WR | sec | Temperature input: Minimum run time | 0...3600.0
1910 | SHORT | RD/WR | sec | Averaging interval for digital input 1: Time interval for calculate digital inputs count frequency | 60...3600.0
1911 | SHORT | RD/WR | sec | Averaging interval for digital input 2: Time interval for calculate digital inputs count frequency | 60...3600.0
1912 | SHORT | RD/WR | sec | Averaging interval for digital input 3: Time interval for calculate digital inputs count frequency | 60...3600.0
1913 | SHORT | RD/WR | sec | Averaging interval for digital input 4: Time interval for calculate digital inputs count frequency | 60...3600.0
1914 | SHORT | RD/WR | sec | Averaging interval for digital input 5: Time interval for calculate digital inputs count frequency | 60...3600.0
1915 | SHORT | RD/WR | sec | Averaging interval for digital input 6: Time interval for calculate digital inputs count frequency | 60...3600.0
1916 | SHORT | RD/WR | sec | Averaging interval for digital input 7: Time interval for calculate digital inputs count frequency | 60...3600.0
1917 | SHORT | RD/WR | sec | Averaging interval for digital input 8: Time interval for calculate digital inputs count frequency | 60...3600.0
1918 | SHORT | RD/WR | sec | Averaging interval for digital input 9: Time interval for calculate digital inputs count frequency | 60...3600.0
1919 | SHORT | RD/WR | sec | Averaging interval for digital input 10: Time interval for calculate digital inputs count frequency | 60...3600.0
1920 | SHORT | RD/WR | sec | Averaging interval for digital input 11: Time interval for calculate digital inputs count frequency | 60...3600.0
1921 | SHORT | RD/WR | sec | Averaging interval for digital input 12: Time interval for calculate digital inputs count frequency | 60...3600.0
1922 | SHORT | RD/WR | sec | Averaging interval for digital input 13: Time interval for calculate digital inputs count frequency | 60...3600.0
1923 | SHORT | RD/WR | sec | Averaging interval for digital input 14: Time interval for calculate digital inputs count frequency | 60...3600.0
1924 | SHORT | RD/WR | sec | Averaging interval for digital input 15: Time interval for calculate digital inputs count frequency | 60...3600.0
1925 | SHORT | RD/WR | - | Start daylight saving time: Day | 0...30
1926 | SHORT | RD/WR | - | Start daylight saving time: Hour | 0...23
1927 | SHORT | RD/WR | - | Start daylight saving time: Month | 0...12
1928 | SHORT | RD/WR | - | Start daylight saving time: Minute | 0...59
1929 | SHORT | RD/WR | - | Start daylight saving time: Day of week (0=Su...6=Sa) | 0...6
1930 | SHORT | RD/WR | - | End daylight saving time: Day | 0...30
1931 | SHORT | RD/WR | - | End daylight saving time: Hour | 0...23
1932 | SHORT | RD/WR | - | End daylight saving time: Month | 0...11
1933 | SHORT | RD/WR | - | End daylight saving time: Minute | 0...59
1934 | SHORT | RD/WR | - | End daylight saving time: Day of week (0=Su...6=Sa) | 0...6
1935 | INT | RD/WR | sec | Standard Time offset | 0...3600
1937 | INT | RD/WR | sec | Daylight saving time offset | 0...86400
1940 | SHORT | RD/WR |  | Digital input 1: Tariff selection | 0...255
1941 | SHORT | RD/WR |  | Digital input 2: Tariff selection | 0...255
1942 | SHORT | RD/WR |  | Digital input 3: Tariff selection | 0...255
1943 | SHORT | RD/WR |  | Digital input 4: Tariff selection | 0...255
1944 | SHORT | RD/WR |  | Digital input 5: Tariff selection | 0...255
1945 | SHORT | RD/WR |  | Digital input 6: Tariff selection | 0...255
1946 | SHORT | RD/WR |  | Digital input 7: Tariff selection | 0...255
1947 | SHORT | RD/WR |  | Digital input 8: Tariff selection | 0...255
1948 | SHORT | RD/WR |  | Digital input 9: Tariff selection | 0...255
1949 | SHORT | RD/WR |  | Digital input 10: Tariff selection | 0...255
1950 | SHORT | RD/WR |  | Digital input 11: Tariff selection | 0...255
1951 | SHORT | RD/WR |  | Digital input 12: Tariff selection | 0...255
1952 | SHORT | RD/WR |  | Digital input 13: Tariff selection | 0...255
1953 | SHORT | RD/WR |  | Digital input 14: Tariff selection | 0...255
1954 | SHORT | RD/WR |  | Digital input 15: Tariff selection | 0...255
1955 | USHORT | RD/WR |  | Digital Input 1: Input number | 0...65535
1956 | USHORT | RD/WR |  | Digital Input 2: Input number | 0...65535
1957 | USHORT | RD/WR |  | Digital Input 3: Input number | 0...65535
1958 | USHORT | RD/WR |  | Digital Input 4: Input number | 0...65535
1959 | USHORT | RD/WR |  | Digital Input 5: Input number | 0...65535
1960 | USHORT | RD/WR |  | Digital Input 6: Input number | 0...65535
1961 | USHORT | RD/WR |  | Digital Input 7: Input number | 0...65535
1962 | USHORT | RD/WR |  | Digital Input 8: Input number | 0...65535
1963 | USHORT | RD/WR |  | Digital Input 9: Input number | 0...65535
1964 | USHORT | RD/WR |  | Digital Input 10: Input number | 0...65535
1965 | USHORT | RD/WR |  | Digital Input 11: Input number | 0...65535
1966 | USHORT | RD/WR |  | Digital Input 12: Input number | 0...65535
1967 | USHORT | RD/WR |  | Digital Input 13: Input number | 0...65535
1968 | USHORT | RD/WR |  | Digital Input 14: Input number | 0...65535
1969 | USHORT | RD/WR |  | Digital Input 15: Input number | 0...65535
1970 | SHORT | RD/WR |  | Function digital input 1: 0=disable, 1=tariff | 0, 1 | 0
1971 | SHORT | RD/WR |  | Function digital input 2: 0=disable, 1=tariff | 0, 1 | 0
1972 | SHORT | RD/WR |  | Function digital input 3: 0=disable, 1=tariff | 0, 1 | 0
1973 | SHORT | RD/WR |  | Function digital input 4: 0=disable, 1=tariff | 0, 1 | 0
1974 | SHORT | RD/WR |  | Function digital input 5: 0=disable, 1=tariff | 0, 1 | 0
1975 | SHORT | RD/WR |  | Function digital input 6: 0=disable, 1=tariff | 0, 1 | 0
1976 | SHORT | RD/WR |  | Function digital input 7: 0=disable, 1=tariff | 0, 1 | 0
1977 | SHORT | RD/WR |  | Function digital input 8: 0=disable, 1=tariff | 0, 1 | 0
1978 | SHORT | RD/WR |  | Function digital input 9: 0=disable, 2=time sync (minute), 3=time sync (hour) | 0, 2, 3 | 0
1979 | SHORT | RD/WR |  | Function digital input 10: 0=disable, 4=reset sync values | 0, 4 | 0
9000 | INT64 | RD/WR |  | Clock timer, channel 1 byte1=minute_on byte2=hour_on byte3=minute_off byte4=hour_off byte5=Day (Bit0=Sun, Bit1=Mon... ) byte6=tariff (0=disable, 1...8 Tariff) byte7=digital output (0=disable, 1...3 set digital output) byte 8=reserved | 0...59 0...23 0...59 0...24 0...6 0...8 0...3 -
9004 | INT64 | RD/WR |  | Clock timer, channel 2 | see channel 1
9008 | INT64 | RD/WR |  | Clock timer, channel 3 | see channel 1
9012 | INT64 | RD/WR |  | Clock timer, channel 4 | see channel 1
9016 | INT64 | RD/WR |  | Clock timer, channel 5 | see channel 1
9020 | INT64 | RD/WR |  | Clock timer, channel 6 | see channel 1
9024 | INT64 | RD/WR |  | Clock timer, channel 7 | see channel 1
9028 | INT64 | RD/WR |  | Clock timer, channel 8 | see channel 1
9032 | INT64 | RD/WR |  | Clock timer, channel 9 | see channel 1
9036 | INT64 | RD/WR |  | Clock timer, channel 10 | see channel 1
9040 | INT64 | RD/WR |  | Clock timer, channel 11 | see channel 1
9044 | INT64 | RD/WR |  | Clock timer, channel 12 | see channel 1
9048 | INT64 | RD/WR |  | Clock timer, channel 13 | see channel 1
9052 | INT64 | RD/WR |  | Clock timer, channel 14 | see channel 1
9056 | INT64 | RD/WR |  | Clock timer, channel 15 | see channel 1
9060 | INT64 | RD/WR |  | Clock timer, channel 16 | see channel 1
9064 | INT64 | RD/WR |  | Clock timer, channel 17 | see channel 1
9068 | INT64 | RD/WR |  | Clock timer, channel 18 | see channel 1
9072 | INT64 | RD/WR |  | Clock timer, channel 19 | see channel 1
9076 | INT64 | RD/WR |  | Clock timer, channel 20 | see channel 1
9080 | INT64 | RD/WR |  | Clock timer, channel 21 | see channel 1
9084 | INT64 | RD/WR |  | Clock timer, channel 22 | see channel 1
9088 | INT64 | RD/WR |  | Clock timer, channel 23 | see channel 1
9092 | INT64 | RD/WR |  | Clock timer, channel 24 | see channel 1
9096 | INT64 | RD/WR |  | Clock timer, channel 25 | see channel 1
9100 | INT64 | RD/WR |  | Clock timer, channel 26 | see channel 1
9104 | INT64 | RD/WR |  | Clock timer, channel 27 | see channel 1
9108 | INT64 | RD/WR |  | Clock timer, channel 28 | see channel 1
9112 | INT64 | RD/WR |  | Clock timer, channel 29 | see channel 1
9116 | INT64 | RD/WR |  | Clock timer, channel 30 | see channel 1
9120 | INT64 | RD/WR |  | Clock timer, channel 31 | see channel 1
9124 | INT64 | RD/WR |  | Clock timer, channel 32 | see channel 1
9128 | INT64 | RD/WR |  | Clock timer, channel 33 | see channel 1
9132 | INT64 | RD/WR |  | Clock timer, channel 34 | see channel 1
9136 | INT64 | RD/WR |  | Clock timer, channel 35 | see channel 1
9140 | INT64 | RD/WR |  | Clock timer, channel 36 | see channel 1
9144 | INT64 | RD/WR |  | Clock timer, channel 37 | see channel 1
9148 | INT64 | RD/WR |  | Clock timer, channel 38 | see channel 1
9152 | INT64 | RD/WR |  | Clock timer, channel 39 | see channel 1
9156 | INT64 | RD/WR |  | Clock timer, channel 40 | see channel 1
9160 | INT64 | RD/WR |  | Clock timer, channel 41 | see channel 1
9164 | INT64 | RD/WR |  | Clock timer, channel 42 | see channel 1
9168 | INT64 | RD/WR |  | Clock timer, channel 43 | see channel 1
9172 | INT64 | RD/WR |  | Clock timer, channel 44 | see channel 1
9176 | INT64 | RD/WR |  | Clock timer, channel 45 | see channel 1
9180 | INT64 | RD/WR |  | Clock timer, channel 46 | see channel 1
9184 | INT64 | RD/WR |  | Clock timer, channel 47 | see channel 1
9188 | INT64 | RD/WR |  | Clock timer, channel 48 | see channel 1
9192 | INT64 | RD/WR |  | Clock timer, channel 49 | see channel 1
9196 | INT64 | RD/WR |  | Clock timer, channel 50 | see channel 1
9200 | INT64 | RD/WR |  | Clock timer, channel 51 | see channel 1
9204 | INT64 | RD/WR |  | Clock timer, channel 52 | see channel 1
9208 | INT64 | RD/WR |  | Clock timer, channel 53 | see channel 1
9212 | INT64 | RD/WR |  | Clock timer, channel 54 | see channel 1
9216 | INT64 | RD/WR |  | Clock timer, channel 55 | see channel 1
9220 | INT64 | RD/WR |  | Clock timer, channel 56 | see channel 1
9224 | INT64 | RD/WR |  | Clock timer, channel 57 | see channel 1
9228 | INT64 | RD/WR |  | Clock timer, channel 58 | see channel 1
9232 | INT64 | RD/WR |  | Clock timer, channel 59 | see channel 1
9236 | INT64 | RD/WR |  | Clock timer, channel 60 | see channel 1
9240 | INT64 | RD/WR |  | Clock timer, channel 61 | see channel 1
9244 | INT64 | RD/WR |  | Clock timer, channel 62 | see channel 1
9248 | INT64 | RD/WR |  | Clock timer, channel 63 | see channel 1
9252 | INT64 | RD/WR |  | Clock timer, channel 64 | see channel 1
Adress list
Digital Inputs: Pulses & Scaling
Adress | Format | RD/WR | Unit | Note
2000 | LONG64 | RD/WR | n | pulse count, input 1
2004 | LONG64 | RD/WR | n | pulse count, input 2
2008 | LONG64 | RD/WR | n | pulse count, input 3
2012 | LONG64 | RD/WR | n | pulse count, input 4
2016 | LONG64 | RD/WR | n | pulse count, input 5
2020 | LONG64 | RD/WR | n | pulse count, input 6
2024 | LONG64 | RD/WR | n | pulse count, input 7
2028 | LONG64 | RD/WR | n | pulse count, input 8
2032 | LONG64 | RD/WR | n | pulse count, input 9
2036 | LONG64 | RD/WR | n | pulse count, input 10
2040 | LONG64 | RD/WR | n | pulse count, input 11
2044 | LONG64 | RD/WR | n | pulse count, input 12
2048 | LONG64 | RD/WR | n | pulse count, input 13
2052 | LONG64 | RD/WR | n | pulse count, input 14
2056 | LONG64 | RD/WR | n | pulse count, input 15
2060 | INT | RD/WR | n | pulse count, input 1
2062 | INT | RD/WR | n | pulse count, input 2
2064 | INT | RD/WR | n | pulse count, input 3
2066 | INT | RD/WR | n | pulse count, input 4
2068 | INT | RD/WR | n | pulse count, input 5
2070 | INT | RD/WR | n | pulse count, input 6
2072 | INT | RD/WR | n | pulse count, input 7
2074 | INT | RD/WR | n | pulse count, input 8
2076 | INT | RD/WR | n | pulse count, input 9
2078 | INT | RD/WR | n | pulse count, input 10
2080 | INT | RD/WR | n | pulse count, input 11
2082 | INT | RD/WR | n | pulse count, input 12
2084 | INT | RD/WR | n | pulse count, input 13
2086 | INT | RD/WR | n | pulse count, input 14
2088 | INT | RD/WR | n | pulse count, input 15
2090 | DOUBLE | RD |  | pulse count x scaling, input 1
2094 | DOUBLE | RD |  | pulse count x scaling, input 2
2098 | DOUBLE | RD |  | pulse count x scaling, input 3
2102 | DOUBLE | RD |  | pulse count x scaling, input 4
2106 | DOUBLE | RD |  | pulse count x scaling, input 5
2110 | DOUBLE | RD |  | pulse count x scaling, input 6
2114 | DOUBLE | RD |  | pulse count x scaling, input 7
2118 | DOUBLE | RD |  | pulse count x scaling, input 8
2122 | DOUBLE | RD |  | pulse count x scaling, input 9
2126 | DOUBLE | RD |  | pulse count x scaling, input 10
2130 | DOUBLE | RD |  | pulse count x scaling, input 11
2134 | DOUBLE | RD |  | pulse count x scaling, input 12
2138 | DOUBLE | RD |  | pulse count x scaling, input 13
2142 | DOUBLE | RD |  | pulse count x scaling, input 14
2146 | DOUBLE | RD |  | pulse count x scaling, input 15
2150 | FLOAT | RD |  | pulse count x scaling, input 1
2152 | FLOAT | RD |  | pulse count x scaling, input 2
2154 | FLOAT | RD |  | pulse count x scaling, input 3
2156 | FLOAT | RD |  | pulse count x scaling, input 4
2158 | FLOAT | RD |  | pulse count x scaling, input 5
2160 | FLOAT | RD |  | pulse count x scaling, input 6
2162 | FLOAT | RD |  | pulse count x scaling, input 7
2164 | FLOAT | RD |  | pulse count x scaling, input 8
2166 | FLOAT | RD |  | pulse count x scaling, input 9
2168 | FLOAT | RD |  | pulse count x scaling, input 10
2170 | FLOAT | RD |  | pulse count x scaling, input 11
2172 | FLOAT | RD |  | pulse count x scaling, input 12
2174 | FLOAT | RD |  | pulse count x scaling, input 13
2176 | FLOAT | RD |  | pulse count x scaling, input 14
2178 | FLOAT | RD |  | pulse count x scaling, input 15
2240 | LONG64 | RD/WR | n | pulse count, input 1, tariff 1
2244 | LONG64 | RD/WR | n | pulse count, input 2, tariff 1
2248 | LONG64 | RD/WR | n | pulse count, input 3, tariff 1
2252 | LONG64 | RD/WR | n | pulse count, input 4, tariff 1
2256 | LONG64 | RD/WR | n | pulse count, input 5, tariff 1
2260 | LONG64 | RD/WR | n | pulse count, input 6, tariff 1
2264 | LONG64 | RD/WR | n | pulse count, input 7, tariff 1
2268 | LONG64 | RD/WR | n | pulse count, input 8, tariff 1
2272 | LONG64 | RD/WR | n | pulse count, input 9, tariff 1
2276 | LONG64 | RD/WR | n | pulse count, input 10, tariff 1
2280 | LONG64 | RD/WR | n | pulse count, input 11, tariff 1
2284 | LONG64 | RD/WR | n | pulse count, input 12, tariff 1
2288 | LONG64 | RD/WR | n | pulse count, input 13, tariff 1
2292 | LONG64 | RD/WR | n | pulse count, input 14, tariff 1
2296 | LONG64 | RD/WR | n | pulse count, input 15, tariff 1
2300 | LONG64 | RD/WR | n | pulse count, input 1, tariff 2
2304 | LONG64 | RD/WR | n | pulse count, input 2, tariff 2
2308 | LONG64 | RD/WR | n | pulse count, input 3, tariff 2
2312 | LONG64 | RD/WR | n | pulse count, input 4, tariff 2
2316 | LONG64 | RD/WR | n | pulse count, input 5, tariff 2
2320 | LONG64 | RD/WR | n | pulse count, input 6, tariff 2
2324 | LONG64 | RD/WR | n | pulse count, input 7, tariff 2
2328 | LONG64 | RD/WR | n | pulse count, input 8, tariff 2
2332 | LONG64 | RD/WR | n | pulse count, input 9, tariff 2
2336 | LONG64 | RD/WR | n | pulse count, input 10, tariff 2
2340 | LONG64 | RD/WR | n | pulse count, input 11, tariff 2
2344 | LONG64 | RD/WR | n | pulse count, input 12, tariff 2
2348 | LONG64 | RD/WR | n | pulse count, input 13, tariff 2
2352 | LONG64 | RD/WR | n | pulse count, input 14, tariff 2
2356 | LONG64 | RD/WR | n | pulse count, input 15, tariff 2
2360 | LONG64 | RD/WR | n | pulse count, input 1, tariff 3
2364 | LONG64 | RD/WR | n | pulse count, input 2, tariff 3
2368 | LONG64 | RD/WR | n | pulse count, input 3, tariff 3
2372 | LONG64 | RD/WR | n | pulse count, input 4, tariff 3
2376 | LONG64 | RD/WR | n | pulse count, input 5, tariff 3
2380 | LONG64 | RD/WR | n | pulse count, input 6, tariff 3
2384 | LONG64 | RD/WR | n | pulse count, input 7, tariff 3
2388 | LONG64 | RD/WR | n | pulse count, input 8, tariff 3
2392 | LONG64 | RD/WR | n | pulse count, input 9, tariff 3
2396 | LONG64 | RD/WR | n | pulse count, input 10, tariff 3
2400 | LONG64 | RD/WR | n | pulse count, input 11, tariff 3
2404 | LONG64 | RD/WR | n | pulse count, input 12, tariff 3
2408 | LONG64 | RD/WR | n | pulse count, input 13, tariff 3
2412 | LONG64 | RD/WR | n | pulse count, input 14, tariff 3
2416 | LONG64 | RD/WR | n | pulse count, input 15, tariff 3
2420 | LONG64 | RD/WR | n | pulse count, input 1, tariff 4
2424 | LONG64 | RD/WR | n | pulse count, input 2, tariff 4
2428 | LONG64 | RD/WR | n | pulse count, input 3, tariff 4
2432 | LONG64 | RD/WR | n | pulse count, input 4, tariff 4
2436 | LONG64 | RD/WR | n | pulse count, input 5, tariff 4
2440 | LONG64 | RD/WR | n | pulse count, input 6, tariff 4
2444 | LONG64 | RD/WR | n | pulse count, input 7, tariff 4
2448 | LONG64 | RD/WR | n | pulse count, input 8, tariff 4
2452 | LONG64 | RD/WR | n | pulse count, input 9, tariff 4
2456 | LONG64 | RD/WR | n | pulse count, input 10, tariff 4
2460 | LONG64 | RD/WR | n | pulse count, input 11, tariff 4
2464 | LONG64 | RD/WR | n | pulse count, input 12, tariff 4
2468 | LONG64 | RD/WR | n | pulse count, input 13, tariff 4
2472 | LONG64 | RD/WR | n | pulse count, input 14, tariff 4
2476 | LONG64 | RD/WR | n | pulse count, input 15, tariff 4
2480 | LONG64 | RD/WR | n | pulse count, input 1, tariff 5
2484 | LONG64 | RD/WR | n | pulse count, input 2, tariff 5
2488 | LONG64 | RD/WR | n | pulse count, input 3, tariff 5
2492 | LONG64 | RD/WR | n | pulse count, input 4, tariff 5
2496 | LONG64 | RD/WR | n | pulse count, input 5, tariff 5
2500 | LONG64 | RD/WR | n | pulse count, input 6, tariff 5
2504 | LONG64 | RD/WR | n | pulse count, input 7, tariff 5
2508 | LONG64 | RD/WR | n | pulse count, input 8, tariff 5
2512 | LONG64 | RD/WR | n | pulse count, input 9, tariff 5
2516 | LONG64 | RD/WR | n | pulse count, input 10, tariff 5
2520 | LONG64 | RD/WR | n | pulse count, input 11, tariff 5
2524 | LONG64 | RD/WR | n | pulse count, input 12, tariff 5
2528 | LONG64 | RD/WR | n | pulse count, input 13, tariff 5
2532 | LONG64 | RD/WR | n | pulse count, input 14, tariff 5
2536 | LONG64 | RD/WR | n | pulse count, input 15, tariff 5
2540 | LONG64 | RD/WR | n | pulse count, input 1, tariff 6
2544 | LONG64 | RD/WR | n | pulse count, input 2, tariff 6
2548 | LONG64 | RD/WR | n | pulse count, input 3, tariff 6
2552 | LONG64 | RD/WR | n | pulse count, input 4, tariff 6
2556 | LONG64 | RD/WR | n | pulse count, input 5, tariff 6
2560 | LONG64 | RD/WR | n | pulse count, input 6, tariff 6
2564 | LONG64 | RD/WR | n | pulse count, input 7, tariff 6
2568 | LONG64 | RD/WR | n | pulse count, input 8, tariff 6
2572 | LONG64 | RD/WR | n | pulse count, input 9, tariff 6
2576 | LONG64 | RD/WR | n | pulse count, input 10, tariff 6
2580 | LONG64 | RD/WR | n | pulse count, input 11, tariff 6
2584 | LONG64 | RD/WR | n | pulse count, input 12, tariff 6
2588 | LONG64 | RD/WR | n | pulse count, input 13, tariff 6
2592 | LONG64 | RD/WR | n | pulse count, input 14, tariff 6
2596 | LONG64 | RD/WR | n | pulse count, input 15, tariff 6
2600 | LONG64 | RD/WR | n | pulse count, input 1, tariff 7
2604 | LONG64 | RD/WR | n | pulse count, input 2, tariff 7
2608 | LONG64 | RD/WR | n | pulse count, input 3, tariff 7
2612 | LONG64 | RD/WR | n | pulse count, input 4, tariff 7
2616 | LONG64 | RD/WR | n | pulse count, input 5, tariff 7
2620 | LONG64 | RD/WR | n | pulse count, input 6, tariff 7
2624 | LONG64 | RD/WR | n | pulse count, input 7, tariff 7
2628 | LONG64 | RD/WR | n | pulse count, input 8, tariff 7
2632 | LONG64 | RD/WR | n | pulse count, input 9, tariff 7
2636 | LONG64 | RD/WR | n | pulse count, input 10, tariff 7
2640 | LONG64 | RD/WR | n | pulse count, input 11, tariff 7
2644 | LONG64 | RD/WR | n | pulse count, input 12, tariff 7
2648 | LONG64 | RD/WR | n | pulse count, input 13, tariff 7
2652 | LONG64 | RD/WR | n | pulse count, input 14, tariff 7
2656 | LONG64 | RD/WR | n | pulse count, input 15, tariff 7
2660 | LONG64 | RD/WR | n | pulse count, input 1, tariff 8
2664 | LONG64 | RD/WR | n | pulse count, input 2, tariff 8
2668 | LONG64 | RD/WR | n | pulse count, input 3, tariff 8
2672 | LONG64 | RD/WR | n | pulse count, input 4, tariff 8
2676 | LONG64 | RD/WR | n | pulse count, input 5, tariff 8
2680 | LONG64 | RD/WR | n | pulse count, input 6, tariff 8
2684 | LONG64 | RD/WR | n | pulse count, input 7, tariff 8
2688 | LONG64 | RD/WR | n | pulse count, input 8, tariff 8
2692 | LONG64 | RD/WR | n | pulse count, input 9, tariff 8
2696 | LONG64 | RD/WR | n | pulse count, input 10, tariff 8
2700 | LONG64 | RD/WR | n | pulse count, input 11, tariff 8
2704 | LONG64 | RD/WR | n | pulse count, input 12, tariff 8
2708 | LONG64 | RD/WR | n | pulse count, input 13, tariff 8
2712 | LONG64 | RD/WR | n | pulse count, input 14, tariff 8
2716 | LONG64 | RD/WR | n | pulse count, input 15, tariff 8
2720 | INT | RD/WR | n | pulse count, input 1, tariff 1
2722 | INT | RD/WR | n | pulse count, input 2, tariff 1
2724 | INT | RD/WR | n | pulse count, input 3, tariff 1
2726 | INT | RD/WR | n | pulse count, input 4, tariff 1
2728 | INT | RD/WR | n | pulse count, input 5, tariff 1
2730 | INT | RD/WR | n | pulse count, input 6, tariff 1
2732 | INT | RD/WR | n | pulse count, input 7, tariff 1
2734 | INT | RD/WR | n | pulse count, input 8, tariff 1
2736 | INT | RD/WR | n | pulse count, input 9, tariff 1
2738 | INT | RD/WR | n | pulse count, input 10, tariff 1
2740 | INT | RD/WR | n | pulse count, input 11, tariff 1
2742 | INT | RD/WR | n | pulse count, input 12, tariff 1
2744 | INT | RD/WR | n | pulse count, input 13, tariff 1
2746 | INT | RD/WR | n | pulse count, input 14, tariff 1
2748 | INT | RD/WR | n | pulse count, input 15, tariff 1
2750 | INT | RD/WR | n | pulse count, input 1, tariff 2
2752 | INT | RD/WR | n | pulse count, input 2, tariff 2
2754 | INT | RD/WR | n | pulse count, input 3, tariff 2
2756 | INT | RD/WR | n | pulse count, input 4, tariff 2
2758 | INT | RD/WR | n | pulse count, input 5, tariff 2
2760 | INT | RD/WR | n | pulse count, input 6, tariff 2
2762 | INT | RD/WR | n | pulse count, input 7, tariff 2
2764 | INT | RD/WR | n | pulse count, input 8, tariff 2
2766 | INT | RD/WR | n | pulse count, input 9, tariff 2
2768 | INT | RD/WR | n | pulse count, input 10, tariff 2
2770 | INT | RD/WR | n | pulse count, input 11, tariff 2
2772 | INT | RD/WR | n | pulse count, input 12, tariff 2
2774 | INT | RD/WR | n | pulse count, input 13, tariff 2
2776 | INT | RD/WR | n | pulse count, input 14, tariff 2
2778 | INT | RD/WR | n | pulse count, input 15, tariff 2
2780 | INT | RD/WR | n | pulse count, input 1, tariff 3
2782 | INT | RD/WR | n | pulse count, input 2, tariff 3
2784 | INT | RD/WR | n | pulse count, input 3, tariff 3
2786 | INT | RD/WR | n | pulse count, input 4, tariff 3
2788 | INT | RD/WR | n | pulse count, input 5, tariff 3
2790 | INT | RD/WR | n | pulse count, input 6, tariff 3
2792 | INT | RD/WR | n | pulse count, input 7, tariff 3
2794 | INT | RD/WR | n | pulse count, input 8, tariff 3
2796 | INT | RD/WR | n | pulse count, input 9, tariff 3
2798 | INT | RD/WR | n | pulse count, input 10, tariff 3
2800 | INT | RD/WR | n | pulse count, input 11, tariff 3
2802 | INT | RD/WR | n | pulse count, input 12, tariff 3
2804 | INT | RD/WR | n | pulse count, input 13, tariff 3
2806 | INT | RD/WR | n | pulse count, input 14, tariff 3
2808 | INT | RD/WR | n | pulse count, input 15, tariff 3
2810 | INT | RD/WR | n | pulse count, input 1, tariff 4
2812 | INT | RD/WR | n | pulse count, input 2, tariff 4
2814 | INT | RD/WR | n | pulse count, input 3, tariff 4
2816 | INT | RD/WR | n | pulse count, input 4, tariff 4
2818 | INT | RD/WR | n | pulse count, input 5, tariff 4
2820 | INT | RD/WR | n | pulse count, input 6, tariff 4
2822 | INT | RD/WR | n | pulse count, input 7, tariff 4
2824 | INT | RD/WR | n | pulse count, input 8, tariff 4
2826 | INT | RD/WR | n | pulse count, input 9, tariff 4
2828 | INT | RD/WR | n | pulse count, input 10, tariff 4
2830 | INT | RD/WR | n | pulse count, input 11, tariff 4
2832 | INT | RD/WR | n | pulse count, input 12, tariff 4
2834 | INT | RD/WR | n | pulse count, input 13, tariff 4
2836 | INT | RD/WR | n | pulse count, input 14, tariff 4
2838 | INT | RD/WR | n | pulse count, input 15, tariff 4
2840 | INT | RD/WR | n | pulse count, input 1, tariff 5
2842 | INT | RD/WR | n | pulse count, input 2, tariff 5
2844 | INT | RD/WR | n | pulse count, input 3, tariff 5
2846 | INT | RD/WR | n | pulse count, input 4, tariff 5
2848 | INT | RD/WR | n | pulse count, input 5, tariff 5
2850 | INT | RD/WR | n | pulse count, input 6, tariff 5
2852 | INT | RD/WR | n | pulse count, input 7, tariff 5
2854 | INT | RD/WR | n | pulse count, input 8, tariff 5
2856 | INT | RD/WR | n | pulse count, input 9, tariff 5
2858 | INT | RD/WR | n | pulse count, input 10, tariff 5
2860 | INT | RD/WR | n | pulse count, input 11, tariff 5
2862 | INT | RD/WR | n | pulse count, input 12, tariff 5
2864 | INT | RD/WR | n | pulse count, input 13, tariff 5
2866 | INT | RD/WR | n | pulse count, input 14, tariff 5
2868 | INT | RD/WR | n | pulse count, input 15, tariff 5
2870 | INT | RD/WR | n | pulse count, input 1, tariff 6
2872 | INT | RD/WR | n | pulse count, input 2, tariff 6
2874 | INT | RD/WR | n | pulse count, input 3, tariff 6
2876 | INT | RD/WR | n | pulse count, input 4, tariff 6
2878 | INT | RD/WR | n | pulse count, input 5, tariff 6
2880 | INT | RD/WR | n | pulse count, input 6, tariff 6
2882 | INT | RD/WR | n | pulse count, input 7, tariff 6
2884 | INT | RD/WR | n | pulse count, input 8, tariff 6
2886 | INT | RD/WR | n | pulse count, input 9, tariff 6
2888 | INT | RD/WR | n | pulse count, input 10, tariff 6
2890 | INT | RD/WR | n | pulse count, input 11, tariff 6
2892 | INT | RD/WR | n | pulse count, input 12, tariff 6
2894 | INT | RD/WR | n | pulse count, input 13, tariff 6
2896 | INT | RD/WR | n | pulse count, input 14, tariff 6
2898 | INT | RD/WR | n | pulse count, input 15, tariff 6
2900 | INT | RD/WR | n | pulse count, input 1, tariff 7
2902 | INT | RD/WR | n | pulse count, input 2, tariff 7
2904 | INT | RD/WR | n | pulse count, input 3, tariff 7
2906 | INT | RD/WR | n | pulse count, input 4, tariff 7
2908 | INT | RD/WR | n | pulse count, input 5, tariff 7
2910 | INT | RD/WR | n | pulse count, input 6, tariff 7
2912 | INT | RD/WR | n | pulse count, input 7, tariff 7
2914 | INT | RD/WR | n | pulse count, input 8, tariff 7
2916 | INT | RD/WR | n | pulse count, input 9, tariff 7
2918 | INT | RD/WR | n | pulse count, input 10, tariff 7
2920 | INT | RD/WR | n | pulse count, input 11, tariff 7
2922 | INT | RD/WR | n | pulse count, input 12, tariff 7
2924 | INT | RD/WR | n | pulse count, input 13, tariff 7
2926 | INT | RD/WR | n | pulse count, input 14, tariff 7
2928 | INT | RD/WR | n | pulse count, input 15, tariff 7
2930 | INT | RD/WR | n | pulse count, input 1, tariff 8
2932 | INT | RD/WR | n | pulse count, input 2, tariff 8
2934 | INT | RD/WR | n | pulse count, input 3, tariff 8
2936 | INT | RD/WR | n | pulse count, input 4, tariff 8
2938 | INT | RD/WR | n | pulse count, input 5, tariff 8
2940 | INT | RD/WR | n | pulse count, input 6, tariff 8
2942 | INT | RD/WR | n | pulse count, input 7, tariff 8
2944 | INT | RD/WR | n | pulse count, input 8, tariff 8
2946 | INT | RD/WR | n | pulse count, input 9, tariff 8
2948 | INT | RD/WR | n | pulse count, input 10, tariff 8
2950 | INT | RD/WR | n | pulse count, input 11, tariff 8
2952 | INT | RD/WR | n | pulse count, input 12, tariff 8
2954 | INT | RD/WR | n | pulse count, input 13, tariff 8
2956 | INT | RD/WR | n | pulse count, input 14, tariff 8
2958 | INT | RD/WR | n | pulse count, input 15, tariff 8
2960 | DOUBLE | RD/WR |  | pulse count x scaling, input 1, tariff 1
2964 | DOUBLE | RD/WR |  | pulse count x scaling, input 2, tariff 1
2968 | DOUBLE | RD/WR |  | pulse count x scaling, input 3, tariff 1
2972 | DOUBLE | RD/WR |  | pulse count x scaling, input 4, tariff 1
2976 | DOUBLE | RD/WR |  | pulse count x scaling, input 5, tariff 1
2980 | DOUBLE | RD/WR |  | pulse count x scaling, input 6, tariff 1
2984 | DOUBLE | RD/WR |  | pulse count x scaling, input 7, tariff 1
2988 | DOUBLE | RD/WR |  | pulse count x scaling, input 8, tariff 1
2992 | DOUBLE | RD/WR |  | pulse count x scaling, input 9, tariff 1
2996 | DOUBLE | RD/WR |  | pulse count x scaling, input 10, tariff 1
3000 | DOUBLE | RD/WR |  | pulse count x scaling, input 11, tariff 1
3004 | DOUBLE | RD/WR |  | pulse count x scaling, input 12, tariff 1
3008 | DOUBLE | RD/WR |  | pulse count x scaling, input 13, tariff 1
3012 | DOUBLE | RD/WR |  | pulse count x scaling, input 14, tariff 1
3016 | DOUBLE | RD/WR |  | pulse count x scaling, input 15, tariff 1
3020 | DOUBLE | RD/WR |  | pulse count x scaling, input 1, tariff 2
3024 | DOUBLE | RD/WR |  | pulse count x scaling, input 2, tariff 2
3028 | DOUBLE | RD/WR |  | pulse count x scaling, input 3, tariff 2
3032 | DOUBLE | RD/WR |  | pulse count x scaling, input 4, tariff 2
3036 | DOUBLE | RD/WR |  | pulse count x scaling, input 5, tariff 2
3040 | DOUBLE | RD/WR |  | pulse count x scaling, input 6, tariff 2
3044 | DOUBLE | RD/WR |  | pulse count x scaling, input 7, tariff 2
3048 | DOUBLE | RD/WR |  | pulse count x scaling, input 8, tariff 2
3052 | DOUBLE | RD/WR |  | pulse count x scaling, input 9, tariff 2
3056 | DOUBLE | RD/WR |  | pulse count x scaling, input 10, tariff 2
3060 | DOUBLE | RD/WR |  | pulse count x scaling, input 11, tariff 2
3064 | DOUBLE | RD/WR |  | pulse count x scaling, input 12, tariff 2
3068 | DOUBLE | RD/WR |  | pulse count x scaling, input 13, tariff 2
3072 | DOUBLE | RD/WR |  | pulse count x scaling, input 14, tariff 2
3076 | DOUBLE | RD/WR |  | pulse count x scaling, input 15, tariff 2
3080 | DOUBLE | RD/WR |  | pulse count x scaling, input 1, tariff 3
3084 | DOUBLE | RD/WR |  | pulse count x scaling, input 2, tariff 3
3088 | DOUBLE | RD/WR |  | pulse count x scaling, input 3, tariff 3
3092 | DOUBLE | RD/WR |  | pulse count x scaling, input 4, tariff 3
3096 | DOUBLE | RD/WR |  | pulse count x scaling, input 5, tariff 3
3100 | DOUBLE | RD/WR |  | pulse count x scaling, input 6, tariff 3
3104 | DOUBLE | RD/WR |  | pulse count x scaling, input 7, tariff 3
3108 | DOUBLE | RD/WR |  | pulse count x scaling, input 8, tariff 3
3112 | DOUBLE | RD/WR |  | pulse count x scaling, input 9, tariff 3
3116 | DOUBLE | RD/WR |  | pulse count x scaling, input 10, tariff 3
3120 | DOUBLE | RD/WR |  | pulse count x scaling, input 11, tariff 3
3124 | DOUBLE | RD/WR |  | pulse count x scaling, input 12, tariff 3
3128 | DOUBLE | RD/WR |  | pulse count x scaling, input 13, tariff 3
3132 | DOUBLE | RD/WR |  | pulse count x scaling, input 14, tariff 3
3136 | DOUBLE | RD/WR |  | pulse count x scaling, input 15, tariff 3
3140 | DOUBLE | RD/WR |  | pulse count x scaling, input 1, tariff 4
3144 | DOUBLE | RD/WR |  | pulse count x scaling, input 2, tariff 4
3148 | DOUBLE | RD/WR |  | pulse count x scaling, input 3, tariff 4
3152 | DOUBLE | RD/WR |  | pulse count x scaling, input 4, tariff 4
3156 | DOUBLE | RD/WR |  | pulse count x scaling, input 5, tariff 4
3160 | DOUBLE | RD/WR |  | pulse count x scaling, input 6, tariff 4
3164 | DOUBLE | RD/WR |  | pulse count x scaling, input 7, tariff 4
3168 | DOUBLE | RD/WR |  | pulse count x scaling, input 8, tariff 4
3172 | DOUBLE | RD/WR |  | pulse count x scaling, input 9, tariff 4
3176 | DOUBLE | RD/WR |  | pulse count x scaling, input 10, tariff 4
3180 | DOUBLE | RD/WR |  | pulse count x scaling, input 11, tariff 4
3184 | DOUBLE | RD/WR |  | pulse count x scaling, input 12, tariff 4
3188 | DOUBLE | RD/WR |  | pulse count x scaling, input 13, tariff 4
3192 | DOUBLE | RD/WR |  | pulse count x scaling, input 14, tariff 4
3196 | DOUBLE | RD/WR |  | pulse count x scaling, input 15, tariff 4
3200 | DOUBLE | RD/WR |  | pulse count x scaling, input 1, tariff 5
3204 | DOUBLE | RD/WR |  | pulse count x scaling, input 2, tariff 5
3208 | DOUBLE | RD/WR |  | pulse count x scaling, input 3, tariff 5
3212 | DOUBLE | RD/WR |  | pulse count x scaling, input 4, tariff 5
3216 | DOUBLE | RD/WR |  | pulse count x scaling, input 5, tariff 5
3220 | DOUBLE | RD/WR |  | pulse count x scaling, input 6, tariff 5
3224 | DOUBLE | RD/WR |  | pulse count x scaling, input 7, tariff 5
3228 | DOUBLE | RD/WR |  | pulse count x scaling, input 8, tariff 5
3232 | DOUBLE | RD/WR |  | pulse count x scaling, input 9, tariff 5
3236 | DOUBLE | RD/WR |  | pulse count x scaling, input 10, tariff 5
3240 | DOUBLE | RD/WR |  | pulse count x scaling, input 11, tariff 5
3244 | DOUBLE | RD/WR |  | pulse count x scaling, input 12, tariff 5
3248 | DOUBLE | RD/WR |  | pulse count x scaling, input 13, tariff 5
3252 | DOUBLE | RD/WR |  | pulse count x scaling, input 14, tariff 5
3256 | DOUBLE | RD/WR |  | pulse count x scaling, input 15, tariff 5
3260 | DOUBLE | RD/WR |  | pulse count x scaling, input 1, tariff 6
3264 | DOUBLE | RD/WR |  | pulse count x scaling, input 2, tariff 6
3268 | DOUBLE | RD/WR |  | pulse count x scaling, input 3, tariff 6
3272 | DOUBLE | RD/WR |  | pulse count x scaling, input 4, tariff 6
3276 | DOUBLE | RD/WR |  | pulse count x scaling, input 5, tariff 6
3280 | DOUBLE | RD/WR |  | pulse count x scaling, input 6, tariff 6
3284 | DOUBLE | RD/WR |  | pulse count x scaling, input 7, tariff 6
3288 | DOUBLE | RD/WR |  | pulse count x scaling, input 8, tariff 6
3292 | DOUBLE | RD/WR |  | pulse count x scaling, input 9, tariff 6
3296 | DOUBLE | RD/WR |  | pulse count x scaling, input 10, tariff 6
3300 | DOUBLE | RD/WR |  | pulse count x scaling, input 11, tariff 6
3304 | DOUBLE | RD/WR |  | pulse count x scaling, input 12, tariff 6
3308 | DOUBLE | RD/WR |  | pulse count x scaling, input 13, tariff 6
3312 | DOUBLE | RD/WR |  | pulse count x scaling, input 14, tariff 6
3316 | DOUBLE | RD/WR |  | pulse count x scaling, input 15, tariff 6
3320 | DOUBLE | RD/WR |  | pulse count x scaling, input 1, tariff 7
3324 | DOUBLE | RD/WR |  | pulse count x scaling, input 2, tariff 7
3328 | DOUBLE | RD/WR |  | pulse count x scaling, input 3, tariff 7
3332 | DOUBLE | RD/WR |  | pulse count x scaling, input 4, tariff 7
3336 | DOUBLE | RD/WR |  | pulse count x scaling, input 5, tariff 7
3340 | DOUBLE | RD/WR |  | pulse count x scaling, input 6, tariff 7
3344 | DOUBLE | RD/WR |  | pulse count x scaling, input 7, tariff 7
3348 | DOUBLE | RD/WR |  | pulse count x scaling, input 8, tariff 7
3352 | DOUBLE | RD/WR |  | pulse count x scaling, input 9, tariff 7
3356 | DOUBLE | RD/WR |  | pulse count x scaling, input 10, tariff 7
3360 | DOUBLE | RD/WR |  | pulse count x scaling, input 11, tariff 7
3364 | DOUBLE | RD/WR |  | pulse count x scaling, input 12, tariff 7
3368 | DOUBLE | RD/WR |  | pulse count x scaling, input 13, tariff 7
3372 | DOUBLE | RD/WR |  | pulse count x scaling, input 14, tariff 7
3376 | DOUBLE | RD/WR |  | pulse count x scaling, input 15, tariff 7
3380 | DOUBLE | RD/WR |  | pulse count x scaling, input 1, tariff 8
3384 | DOUBLE | RD/WR |  | pulse count x scaling, input 2, tariff 8
3388 | DOUBLE | RD/WR |  | pulse count x scaling, input 3, tariff 8
3392 | DOUBLE | RD/WR |  | pulse count x scaling, input 4, tariff 8
3396 | DOUBLE | RD/WR |  | pulse count x scaling, input 5, tariff 8
3400 | DOUBLE | RD/WR |  | pulse count x scaling, input 6, tariff 8
3404 | DOUBLE | RD/WR |  | pulse count x scaling, input 7, tariff 8
3408 | DOUBLE | RD/WR |  | pulse count x scaling, input 8, tariff 8
3412 | DOUBLE | RD/WR |  | pulse count x scaling, input 9, tariff 8
3416 | DOUBLE | RD/WR |  | pulse count x scaling, input 10, tariff 8
3420 | DOUBLE | RD/WR |  | pulse count x scaling, input 11, tariff 8
3424 | DOUBLE | RD/WR |  | pulse count x scaling, input 12, tariff 8
3428 | DOUBLE | RD/WR |  | pulse count x scaling, input 13, tariff 8
3432 | DOUBLE | RD/WR |  | pulse count x scaling, input 14, tariff 8
3436 | DOUBLE | RD/WR |  | pulse count x scaling, input 15, tariff 8
3440 | FLOAT | RD/WR |  | pulse count x scaling, input 1, tariff 1
3442 | FLOAT | RD/WR |  | pulse count x scaling, input 2, tariff 1
3444 | FLOAT | RD/WR |  | pulse count x scaling, input 3, tariff 1
3446 | FLOAT | RD/WR |  | pulse count x scaling, input 4, tariff 1
3448 | FLOAT | RD/WR |  | pulse count x scaling, input 5, tariff 1
3450 | FLOAT | RD/WR |  | pulse count x scaling, input 6, tariff 1
3452 | FLOAT | RD/WR |  | pulse count x scaling, input 7, tariff 1
3454 | FLOAT | RD/WR |  | pulse count x scaling, input 8, tariff 1
3456 | FLOAT | RD/WR |  | pulse count x scaling, input 9, tariff 1
3458 | FLOAT | RD/WR |  | pulse count x scaling, input 10, tariff 1
3460 | FLOAT | RD/WR |  | pulse count x scaling, input 11, tariff 1
3462 | FLOAT | RD/WR |  | pulse count x scaling, input 12, tariff 1
3464 | FLOAT | RD/WR |  | pulse count x scaling, input 13, tariff 1
3466 | FLOAT | RD/WR |  | pulse count x scaling, input 14, tariff 1
3468 | FLOAT | RD/WR |  | pulse count x scaling, input 15, tariff 1
3470 | FLOAT | RD/WR |  | pulse count x scaling, input 1, tariff 2
3472 | FLOAT | RD/WR |  | pulse count x scaling, input 2, tariff 2
3474 | FLOAT | RD/WR |  | pulse count x scaling, input 3, tariff 2
3476 | FLOAT | RD/WR |  | pulse count x scaling, input 4, tariff 2
3478 | FLOAT | RD/WR |  | pulse count x scaling, input 5, tariff 2
3480 | FLOAT | RD/WR |  | pulse count x scaling, input 6, tariff 2
3482 | FLOAT | RD/WR |  | pulse count x scaling, input 7, tariff 2
3484 | FLOAT | RD/WR |  | pulse count x scaling, input 8, tariff 2
3486 | FLOAT | RD/WR |  | pulse count x scaling, input 9, tariff 2
3488 | FLOAT | RD/WR |  | pulse count x scaling, input 10, tariff 2
3490 | FLOAT | RD/WR |  | pulse count x scaling, input 11, tariff 2
3492 | FLOAT | RD/WR |  | pulse count x scaling, input 12, tariff 2
3494 | FLOAT | RD/WR |  | pulse count x scaling, input 13, tariff 2
3496 | FLOAT | RD/WR |  | pulse count x scaling, input 14, tariff 2
3498 | FLOAT | RD/WR |  | pulse count x scaling, input 15, tariff 2
3500 | FLOAT | RD/WR |  | pulse count x scaling, input 1, tariff 3
3502 | FLOAT | RD/WR |  | pulse count x scaling, input 2, tariff 3
3504 | FLOAT | RD/WR |  | pulse count x scaling, input 3, tariff 3
3506 | FLOAT | RD/WR |  | pulse count x scaling, input 4, tariff 3
3508 | FLOAT | RD/WR |  | pulse count x scaling, input 5, tariff 3
3510 | FLOAT | RD/WR |  | pulse count x scaling, input 6, tariff 3
3512 | FLOAT | RD/WR |  | pulse count x scaling, input 7, tariff 3
3514 | FLOAT | RD/WR |  | pulse count x scaling, input 8, tariff 3
3516 | FLOAT | RD/WR |  | pulse count x scaling, input 9, tariff 3
3518 | FLOAT | RD/WR |  | pulse count x scaling, input 10, tariff 3
3520 | FLOAT | RD/WR |  | pulse count x scaling, input 11, tariff 3
3522 | FLOAT | RD/WR |  | pulse count x scaling, input 12, tariff 3
3524 | FLOAT | RD/WR |  | pulse count x scaling, input 13, tariff 3
3526 | FLOAT | RD/WR |  | pulse count x scaling, input 14, tariff 3
3528 | FLOAT | RD/WR |  | pulse count x scaling, input 15, tariff 3
3530 | FLOAT | RD/WR |  | pulse count x scaling, input 1, tariff 4
3532 | FLOAT | RD/WR |  | pulse count x scaling, input 2, tariff 4
3534 | FLOAT | RD/WR |  | pulse count x scaling, input 3, tariff 4
3536 | FLOAT | RD/WR |  | pulse count x scaling, input 4, tariff 4
3538 | FLOAT | RD/WR |  | pulse count x scaling, input 5, tariff 4
3540 | FLOAT | RD/WR |  | pulse count x scaling, input 6, tariff 4
3542 | FLOAT | RD/WR |  | pulse count x scaling, input 7, tariff 4
3544 | FLOAT | RD/WR |  | pulse count x scaling, input 8, tariff 4
3546 | FLOAT | RD/WR |  | pulse count x scaling, input 9, tariff 4
3548 | FLOAT | RD/WR |  | pulse count x scaling, input 10, tariff 4
3550 | FLOAT | RD/WR |  | pulse count x scaling, input 11, tariff 4
3552 | FLOAT | RD/WR |  | pulse count x scaling, input 12, tariff 4
3554 | FLOAT | RD/WR |  | pulse count x scaling, input 13, tariff 4
3556 | FLOAT | RD/WR |  | pulse count x scaling, input 14, tariff 4
3558 | FLOAT | RD/WR |  | pulse count x scaling, input 15, tariff 4
3560 | FLOAT | RD/WR |  | pulse count x scaling, input 1, tariff 5
3562 | FLOAT | RD/WR |  | pulse count x scaling, input 2, tariff 5
3564 | FLOAT | RD/WR |  | pulse count x scaling, input 3, tariff 5
3566 | FLOAT | RD/WR |  | pulse count x scaling, input 4, tariff 5
3568 | FLOAT | RD/WR |  | pulse count x scaling, input 5, tariff 5
3570 | FLOAT | RD/WR |  | pulse count x scaling, input 6, tariff 5
3572 | FLOAT | RD/WR |  | pulse count x scaling, input 7, tariff 5
3574 | FLOAT | RD/WR |  | pulse count x scaling, input 8, tariff 5
3576 | FLOAT | RD/WR |  | pulse count x scaling, input 9, tariff 5
3578 | FLOAT | RD/WR |  | pulse count x scaling, input 10, tariff 5
3580 | FLOAT | RD/WR |  | pulse count x scaling, input 11, tariff 5
3582 | FLOAT | RD/WR |  | pulse count x scaling, input 12, tariff 5
3584 | FLOAT | RD/WR |  | pulse count x scaling, input 13, tariff 5
3586 | FLOAT | RD/WR |  | pulse count x scaling, input 14, tariff 5
3588 | FLOAT | RD/WR |  | pulse count x scaling, input 15, tariff 5
3590 | FLOAT | RD/WR |  | pulse count x scaling, input 1, tariff 6
3592 | FLOAT | RD/WR |  | pulse count x scaling, input 2, tariff 6
3594 | FLOAT | RD/WR |  | pulse count x scaling, input 3, tariff 6
3596 | FLOAT | RD/WR |  | pulse count x scaling, input 4, tariff 6
3598 | FLOAT | RD/WR |  | pulse count x scaling, input 5, tariff 6
3600 | FLOAT | RD/WR |  | pulse count x scaling, input 6, tariff 6
3602 | FLOAT | RD/WR |  | pulse count x scaling, input 7, tariff 6
3604 | FLOAT | RD/WR |  | pulse count x scaling, input 8, tariff 6
3606 | FLOAT | RD/WR |  | pulse count x scaling, input 9, tariff 6
3608 | FLOAT | RD/WR |  | pulse count x scaling, input 10, tariff 6
3610 | FLOAT | RD/WR |  | pulse count x scaling, input 11, tariff 6
3612 | FLOAT | RD/WR |  | pulse count x scaling, input 12, tariff 6
3614 | FLOAT | RD/WR |  | pulse count x scaling, input 13, tariff 6
3616 | FLOAT | RD/WR |  | pulse count x scaling, input 14, tariff 6
3618 | FLOAT | RD/WR |  | pulse count x scaling, input 15, tariff 6
3620 | FLOAT | RD/WR |  | pulse count x scaling, input 1, tariff 7
3622 | FLOAT | RD/WR |  | pulse count x scaling, input 2, tariff 7
3624 | FLOAT | RD/WR |  | pulse count x scaling, input 3, tariff 7
3626 | FLOAT | RD/WR |  | pulse count x scaling, input 4, tariff 7
3628 | FLOAT | RD/WR |  | pulse count x scaling, input 5, tariff 7
3630 | FLOAT | RD/WR |  | pulse count x scaling, input 6, tariff 7
3632 | FLOAT | RD/WR |  | pulse count x scaling, input 7, tariff 7
3634 | FLOAT | RD/WR |  | pulse count x scaling, input 8, tariff 7
3636 | FLOAT | RD/WR |  | pulse count x scaling, input 9, tariff 7
3638 | FLOAT | RD/WR |  | pulse count x scaling, input 10, tariff 7
3640 | FLOAT | RD/WR |  | pulse count x scaling, input 11, tariff 7
3642 | FLOAT | RD/WR |  | pulse count x scaling, input 12, tariff 7
3644 | FLOAT | RD/WR |  | pulse count x scaling, input 13, tariff 7
3646 | FLOAT | RD/WR |  | pulse count x scaling, input 14, tariff 7
3648 | FLOAT | RD/WR |  | pulse count x scaling, input 15, tariff 7
3650 | FLOAT | RD/WR |  | pulse count x scaling, input 1, tariff 8
3652 | FLOAT | RD/WR |  | pulse count x scaling, input 2, tariff 8
3654 | FLOAT | RD/WR |  | pulse count x scaling, input 3, tariff 8
3656 | FLOAT | RD/WR |  | pulse count x scaling, input 4, tariff 8
3658 | FLOAT | RD/WR |  | pulse count x scaling, input 5, tariff 8
3660 | FLOAT | RD/WR |  | pulse count x scaling, input 6, tariff 8
3662 | FLOAT | RD/WR |  | pulse count x scaling, input 7, tariff 8
3664 | FLOAT | RD/WR |  | pulse count x scaling, input 8, tariff 8
3666 | FLOAT | RD/WR |  | pulse count x scaling, input 9, tariff 8
3668 | FLOAT | RD/WR |  | pulse count x scaling, input 10, tariff 8
3670 | FLOAT | RD/WR |  | pulse count x scaling, input 11, tariff 8
3672 | FLOAT | RD/WR |  | pulse count x scaling, input 12, tariff 8
3674 | FLOAT | RD/WR |  | pulse count x scaling, input 13, tariff 8
3676 | FLOAT | RD/WR |  | pulse count x scaling, input 14, tariff 8
3678 | FLOAT | RD/WR |  | pulse count x scaling, input 15, tariff 8
4883 | FLOAT | RD |  | input 1 (pulse count x scaling)/interval[sec]
4885 | FLOAT | RD |  | input 2 (pulse count x scaling)/interval[sec]
4887 | FLOAT | RD |  | input 3 (pulse count x scaling)/interval[sec]
4889 | FLOAT | RD |  | input 4 (pulse count x scaling)/interval[sec]
4891 | FLOAT | RD |  | input 5 (pulse count x scaling)/interval[sec]
4893 | FLOAT | RD |  | input 6 (pulse count x scaling)/interval[sec]
4895 | FLOAT | RD |  | input 7 (pulse count x scaling)/interval[sec]
4897 | FLOAT | RD |  | input 8 (pulse count x scaling)/interval[sec]
4899 | FLOAT | RD |  | input 9 (pulse count x scaling)/interval[sec]
4901 | FLOAT | RD |  | input 10 (pulse count x scaling)/interval[sec]
4903 | FLOAT | RD |  | input 11 (pulse count x scaling)/interval[sec]
4905 | FLOAT | RD |  | input 12 (pulse count x scaling)/interval[sec]
4907 | FLOAT | RD |  | input 13 (pulse count x scaling)/interval[sec]
4909 | FLOAT | RD |  | input 14 (pulse count x scaling)/interval[sec]
4911 | FLOAT | RD |  | input 15 (pulse count x scaling)/interval[sec]
Digital Outputs: Events
Adress | Format | RD/WR | Einheit | Bemerkung
3680 | LONG64 | RD | ms | timestamp [UTC], event 1 input 1
3684 | LONG64 | RD | ms | timestamp [UTC], event 1 input 2
3688 | LONG64 | RD | ms | timestamp [UTC], event 1 input 3
3692 | LONG64 | RD | ms | timestamp [UTC], event 1 input 4
3696 | LONG64 | RD | ms | timestamp [UTC], event 1 input 5
3700 | LONG64 | RD | ms | timestamp [UTC], event 1 input 6
3704 | LONG64 | RD | ms | timestamp [UTC], event 1 input 7
3708 | LONG64 | RD | ms | timestamp [UTC], event 1 input 8
3712 | LONG64 | RD | ms | timestamp [UTC], event 1 input 9
3716 | LONG64 | RD | ms | timestamp [UTC], event 1 input 10
3720 | LONG64 | RD | ms | timestamp [UTC], event 1 input 11
3724 | LONG64 | RD | ms | timestamp [UTC], event 1 input 12
3728 | LONG64 | RD | ms | timestamp [UTC], event 1 input 13
3732 | LONG64 | RD | ms | timestamp [UTC], event 1 input 14
3736 | LONG64 | RD | ms | timestamp [UTC], event 1 input 15
3740 | SHORT | RD |  | status, event 1 input 1 (0=off, 1=on)
3741 | SHORT | RD |  | status, event 1 input 2 (0=off, 1=on)
3742 | SHORT | RD |  | status, event 1 input 3 (0=off, 1=on)
3743 | SHORT | RD |  | status, event 1 input 4 (0=off, 1=on)
3744 | SHORT | RD |  | status, event 1 input 5 (0=off, 1=on)
3745 | SHORT | RD |  | status, event 1 input 6 (0=off, 1=on)
3746 | SHORT | RD |  | status, event 1 input 7 (0=off, 1=on)
3747 | SHORT | RD |  | status, event 1 input 8 (0=off, 1=on)
3748 | SHORT | RD |  | status, event 1 input 9 (0=off, 1=on)
3749 | SHORT | RD |  | status, event 1 input 10 (0=off, 1=on)
3750 | SHORT | RD |  | status, event 1 input 11 (0=off, 1=on)
3751 | SHORT | RD |  | status, event 1 input 12 (0=off, 1=on)
3752 | SHORT | RD |  | status, event 1 input 13 (0=off, 1=on)
3753 | SHORT | RD |  | status, event 1 input 14 (0=off, 1=on)
3754 | SHORT | RD |  | status, event 1 input 15 (0=off, 1=on)
3755 | LONG64 | RD | ms | timestamp [UTC], event 2 input 1
3759 | LONG64 | RD | ms | timestamp [UTC], event 2 input 2
3763 | LONG64 | RD | ms | timestamp [UTC], event 2 input 3
3767 | LONG64 | RD | ms | timestamp [UTC], event 2 input 4
3771 | LONG64 | RD | ms | timestamp [UTC], event 2 input 5
3775 | LONG64 | RD | ms | timestamp [UTC], event 2 input 6
3779 | LONG64 | RD | ms | timestamp [UTC], event 2 input 7
3783 | LONG64 | RD | ms | timestamp [UTC], event 2 input 8
3787 | LONG64 | RD | ms | timestamp [UTC], event 2 input 9
3791 | LONG64 | RD | ms | timestamp [UTC], event 2 input 10
3795 | LONG64 | RD | ms | timestamp [UTC], event 2 input 11
3799 | LONG64 | RD | ms | timestamp [UTC], event 2 input 12
3803 | LONG64 | RD | ms | timestamp [UTC], event 2 input 13
3807 | LONG64 | RD | ms | timestamp [UTC], event 2 input 14
3811 | LONG64 | RD | ms | timestamp [UTC], event 2 input 15
3815 | SHORT | RD |  | status, event 2 input 1 (0=off, 1=on)
3816 | SHORT | RD |  | status, event 2 input 2 (0=off, 1=on)
3817 | SHORT | RD |  | status, event 2 input 3 (0=off, 1=on)
3818 | SHORT | RD |  | status, event 2 input 4 (0=off, 1=on)
3819 | SHORT | RD |  | status, event 2 input 5 (0=off, 1=on)
3820 | SHORT | RD |  | status, event 2 input 6 (0=off, 1=on)
3821 | SHORT | RD |  | status, event 2 input 7 (0=off, 1=on)
3822 | SHORT | RD |  | status, event 2 input 8 (0=off, 1=on)
3823 | SHORT | RD |  | status, event 2 input 9 (0=off, 1=on)
3824 | SHORT | RD |  | status, event 2 input 10 (0=off, 1=on)
3825 | SHORT | RD |  | status, event 2 input 11 (0=off, 1=on)
3826 | SHORT | RD |  | status, event 2 input 12 (0=off, 1=on)
3827 | SHORT | RD |  | status, event 2 input 13 (0=off, 1=on)
3828 | SHORT | RD |  | status, event 2 input 14 (0=off, 1=on)
3829 | SHORT | RD |  | status, event 2 input 15 (0=off, 1=on)
3830 | LONG64 | RD | ms | timestamp [UTC], event 3 input 1
3834 | LONG64 | RD | ms | timestamp [UTC], event 3 input 2
3838 | LONG64 | RD | ms | timestamp [UTC], event 3 input 3
3842 | LONG64 | RD | ms | timestamp [UTC], event 3 input 4
3846 | LONG64 | RD | ms | timestamp [UTC], event 3 input 5
3850 | LONG64 | RD | ms | timestamp [UTC], event 3 input 6
3854 | LONG64 | RD | ms | timestamp [UTC], event 3 input 7
3858 | LONG64 | RD | ms | timestamp [UTC], event 3 input 8
3862 | LONG64 | RD | ms | timestamp [UTC], event 3 input 9
3866 | LONG64 | RD | ms | timestamp [UTC], event 3 input 10
3870 | LONG64 | RD | ms | timestamp [UTC], event 3 input 11
3874 | LONG64 | RD | ms | timestamp [UTC], event 3 input 12
3878 | LONG64 | RD | ms | timestamp [UTC], event 3 input 13
3882 | LONG64 | RD | ms | timestamp [UTC], event 3 input 14
3886 | LONG64 | RD | ms | timestamp [UTC], event 3 input 15
3890 | SHORT | RD |  | status, event 3 input 1 (0=off, 1=on)
3891 | SHORT | RD |  | status, event 3 input 2 (0=off, 1=on)
3892 | SHORT | RD |  | status, event 3 input 3 (0=off, 1=on)
3893 | SHORT | RD |  | status, event 3 input 4 (0=off, 1=on)
3894 | SHORT | RD |  | status, event 3 input 5 (0=off, 1=on)
3895 | SHORT | RD |  | status, event 3 input 6 (0=off, 1=on)
3896 | SHORT | RD |  | status, event 3 input 7 (0=off, 1=on)
3897 | SHORT | RD |  | status, event 3 input 8 (0=off, 1=on)
3898 | SHORT | RD |  | status, event 3 input 9 (0=off, 1=on)
3899 | SHORT | RD |  | status, event 3 input 10 (0=off, 1=on)
3900 | SHORT | RD |  | status, event 3 input 11 (0=off, 1=on)
3901 | SHORT | RD |  | status, event 3 input 12 (0=off, 1=on)
3902 | SHORT | RD |  | status, event 3 input 13 (0=off, 1=on)
3903 | SHORT | RD |  | status, event 3 input 14 (0=off, 1=on)
3904 | SHORT | RD |  | status, event 3 input 15 (0=off, 1=on)
3905 | LONG64 | RD | ms | timestamp [UTC], event 4 input 1
3909 | LONG64 | RD | ms | timestamp [UTC], event 4 input 2
3913 | LONG64 | RD | ms | timestamp [UTC], event 4 input 3
3917 | LONG64 | RD | ms | timestamp [UTC], event 4 input 4
3921 | LONG64 | RD | ms | timestamp [UTC], event 4 input 5
3925 | LONG64 | RD | ms | timestamp [UTC], event 4 input 6
3929 | LONG64 | RD | ms | timestamp [UTC], event 4 input 7
3933 | LONG64 | RD | ms | timestamp [UTC], event 4 input 8
3937 | LONG64 | RD | ms | timestamp [UTC], event 4 input 9
3941 | LONG64 | RD | ms | timestamp [UTC], event 4 input 10
3945 | LONG64 | RD | ms | timestamp [UTC], event 4 input 11
3949 | LONG64 | RD | ms | timestamp [UTC], event 4 input 12
3953 | LONG64 | RD | ms | timestamp [UTC], event 4 input 13
3957 | LONG64 | RD | ms | timestamp [UTC], event 4 input 14
3961 | LONG64 | RD | ms | timestamp [UTC], event 4 input 15
3965 | SHORT | RD |  | status, event 4 input 1 (0=off, 1=on)
3966 | SHORT | RD |  | status, event 4 input 2 (0=off, 1=on)
3967 | SHORT | RD |  | status, event 4 input 3 (0=off, 1=on)
3968 | SHORT | RD |  | status, event 4 input 4 (0=off, 1=on)
3969 | SHORT | RD |  | status, event 4 input 5 (0=off, 1=on)
3970 | SHORT | RD |  | status, event 4 input 6 (0=off, 1=on)
3971 | SHORT | RD |  | status, event 4 input 7 (0=off, 1=on)
3972 | SHORT | RD |  | status, event 4 input 8 (0=off, 1=on)
3973 | SHORT | RD |  | status, event 4 input 9 (0=off, 1=on)
3974 | SHORT | RD |  | status, event 4 input 10 (0=off, 1=on)
3975 | SHORT | RD |  | status, event 4 input 11 (0=off, 1=on)
3976 | SHORT | RD |  | status, event 4 input 12 (0=off, 1=on)
3977 | SHORT | RD |  | status, event 4 input 13 (0=off, 1=on)
3978 | SHORT | RD |  | status, event 4 input 14 (0=off, 1=on)
3979 | SHORT | RD |  | status, event 4 input 15 (0=off, 1=on)
3980 | LONG64 | RD | ms | timestamp [UTC], event 5 input 1
3984 | LONG64 | RD | ms | timestamp [UTC], event 5 input 2
3988 | LONG64 | RD | ms | timestamp [UTC], event 5 input 3
3992 | LONG64 | RD | ms | timestamp [UTC], event 5 input 4
3996 | LONG64 | RD | ms | timestamp [UTC], event 5 input 5
4000 | LONG64 | RD | ms | timestamp [UTC], event 5 input 6
4004 | LONG64 | RD | ms | timestamp [UTC], event 5 input 7
4008 | LONG64 | RD | ms | timestamp [UTC], event 5 input 8
4012 | LONG64 | RD | ms | timestamp [UTC], event 5 input 9
4016 | LONG64 | RD | ms | timestamp [UTC], event 5 input 10
4020 | LONG64 | RD | ms | timestamp [UTC], event 5 input 11
4024 | LONG64 | RD | ms | timestamp [UTC], event 5 input 12
4028 | LONG64 | RD | ms | timestamp [UTC], event 5 input 13
4032 | LONG64 | RD | ms | timestamp [UTC], event 5 input 14
4036 | LONG64 | RD | ms | timestamp [UTC], event 5 input 15
4040 | SHORT | RD |  | status, event 5 input 1 (0=off, 1=on)
4041 | SHORT | RD |  | status, event 5 input 2 (0=off, 1=on)
4042 | SHORT | RD |  | status, event 5 input 3 (0=off, 1=on)
4043 | SHORT | RD |  | status, event 5 input 4 (0=off, 1=on)
4044 | SHORT | RD |  | status, event 5 input 5 (0=off, 1=on)
4045 | SHORT | RD |  | status, event 5 input 6 (0=off, 1=on)
4046 | SHORT | RD |  | status, event 5 input 7 (0=off, 1=on)
4047 | SHORT | RD |  | status, event 5 input 8 (0=off, 1=on)
4048 | SHORT | RD |  | status, event 5 input 9 (0=off, 1=on)
4049 | SHORT | RD |  | status, event 5 input 10 (0=off, 1=on)
4050 | SHORT | RD |  | status, event 5 input 11 (0=off, 1=on)
4051 | SHORT | RD |  | status, event 5 input 12 (0=off, 1=on)
4052 | SHORT | RD |  | status, event 5 input 13 (0=off, 1=on)
4053 | SHORT | RD |  | status, event 5 input 14 (0=off, 1=on)
4054 | SHORT | RD |  | status, event 5 input 15 (0=off, 1=on)
4055 | LONG64 | RD | ms | timestamp [UTC], event 6 input 1
4059 | LONG64 | RD | ms | timestamp [UTC], event 6 input 2
4063 | LONG64 | RD | ms | timestamp [UTC], event 6 input 3
4067 | LONG64 | RD | ms | timestamp [UTC], event 6 input 4
4071 | LONG64 | RD | ms | timestamp [UTC], event 6 input 5
4075 | LONG64 | RD | ms | timestamp [UTC], event 6 input 6
4079 | LONG64 | RD | ms | timestamp [UTC], event 6 input 7
4083 | LONG64 | RD | ms | timestamp [UTC], event 6 input 8
4087 | LONG64 | RD | ms | timestamp [UTC], event 6 input 9
4091 | LONG64 | RD | ms | timestamp [UTC], event 6 input 10
4095 | LONG64 | RD | ms | timestamp [UTC], event 6 input 11
4099 | LONG64 | RD | ms | timestamp [UTC], event 6 input 12
4103 | LONG64 | RD | ms | timestamp [UTC], event 6 input 13
4107 | LONG64 | RD | ms | timestamp [UTC], event 6 input 14
4111 | LONG64 | RD | ms | timestamp [UTC], event 6 input 15
4115 | SHORT | RD |  | status, event 6 input 1 (0=off, 1=on)
4116 | SHORT | RD |  | status, event 6 input 2 (0=off, 1=on)
4117 | SHORT | RD |  | status, event 6 input 3 (0=off, 1=on)
4118 | SHORT | RD |  | status, event 6 input 4 (0=off, 1=on)
4119 | SHORT | RD |  | status, event 6 input 5 (0=off, 1=on)
4120 | SHORT | RD |  | status, event 6 input 6 (0=off, 1=on)
4121 | SHORT | RD |  | status, event 6 input 7 (0=off, 1=on)
4122 | SHORT | RD |  | status, event 6 input 8 (0=off, 1=on)
4123 | SHORT | RD |  | status, event 6 input 9 (0=off, 1=on)
4124 | SHORT | RD |  | status, event 6 input 10 (0=off, 1=on)
4125 | SHORT | RD |  | status, event 6 input 11 (0=off, 1=on)
4126 | SHORT | RD |  | status, event 6 input 12 (0=off, 1=on)
4127 | SHORT | RD |  | status, event 6 input 13 (0=off, 1=on)
4128 | SHORT | RD |  | status, event 6 input 14 (0=off, 1=on)
4129 | SHORT | RD |  | status, event 6 input 15 (0=off, 1=on)
4130 | LONG64 | RD | ms | timestamp [UTC], event 7 input 1
4134 | LONG64 | RD | ms | timestamp [UTC], event 7 input 2
4138 | LONG64 | RD | ms | timestamp [UTC], event 7 input 3
4142 | LONG64 | RD | ms | timestamp [UTC], event 7 input 4
4146 | LONG64 | RD | ms | timestamp [UTC], event 7 input 5
4150 | LONG64 | RD | ms | timestamp [UTC], event 7 input 6
4154 | LONG64 | RD | ms | timestamp [UTC], event 7 input 7
4158 | LONG64 | RD | ms | timestamp [UTC], event 7 input 8
4162 | LONG64 | RD | ms | timestamp [UTC], event 7 input 9
4166 | LONG64 | RD | ms | timestamp [UTC], event 7 input 10
4170 | LONG64 | RD | ms | timestamp [UTC], event 7 input 11
4174 | LONG64 | RD | ms | timestamp [UTC], event 7 input 12
4178 | LONG64 | RD | ms | timestamp [UTC], event 7 input 13
4182 | LONG64 | RD | ms | timestamp [UTC], event 7 input 14
4186 | LONG64 | RD | ms | timestamp [UTC], event 7 input 15
4190 | SHORT | RD |  | status, event 7 input 1 (0=off, 1=on)
4191 | SHORT | RD |  | status, event 7 input 2 (0=off, 1=on)
4192 | SHORT | RD |  | status, event 7 input 3 (0=off, 1=on)
4193 | SHORT | RD |  | status, event 7 input 4 (0=off, 1=on)
4194 | SHORT | RD |  | status, event 7 input 5 (0=off, 1=on)
4195 | SHORT | RD |  | status, event 7 input 6 (0=off, 1=on)
4196 | SHORT | RD |  | status, event 7 input 7 (0=off, 1=on)
4197 | SHORT | RD |  | status, event 7 input 8 (0=off, 1=on)
4198 | SHORT | RD |  | status, event 7 input 9 (0=off, 1=on)
4199 | SHORT | RD |  | status, event 7 input 10 (0=off, 1=on)
4200 | SHORT | RD |  | status, event 7 input 11 (0=off, 1=on)
4201 | SHORT | RD |  | status, event 7 input 12 (0=off, 1=on)
4202 | SHORT | RD |  | status, event 7 input 13 (0=off, 1=on)
4203 | SHORT | RD |  | status, event 7 input 14 (0=off, 1=on)
4204 | SHORT | RD |  | status, event 7 input 15 (0=off, 1=on)
4205 | LONG64 | RD | ms | timestamp [UTC], event 8 input 1
4209 | LONG64 | RD | ms | timestamp [UTC], event 8 input 2
4213 | LONG64 | RD | ms | timestamp [UTC], event 8 input 3
4217 | LONG64 | RD | ms | timestamp [UTC], event 8 input 4
4221 | LONG64 | RD | ms | timestamp [UTC], event 8 input 5
4225 | LONG64 | RD | ms | timestamp [UTC], event 8 input 6
4229 | LONG64 | RD | ms | timestamp [UTC], event 8 input 7
4233 | LONG64 | RD | ms | timestamp [UTC], event 8 input 8
4237 | LONG64 | RD | ms | timestamp [UTC], event 8 input 9
4241 | LONG64 | RD | ms | timestamp [UTC], event 8 input 10
4245 | LONG64 | RD | ms | timestamp [UTC], event 8 input 11
4249 | LONG64 | RD | ms | timestamp [UTC], event 8 input 12
4253 | LONG64 | RD | ms | timestamp [UTC], event 8 input 13
4257 | LONG64 | RD | ms | timestamp [UTC], event 8 input 14
4261 | LONG64 | RD | ms | timestamp [UTC], event 8 input 15
4265 | SHORT | RD |  | status, event 8 input 1 (0=off, 1=on)
4266 | SHORT | RD |  | status, event 8 input 2 (0=off, 1=on)
4267 | SHORT | RD |  | status, event 8 input 3 (0=off, 1=on)
4268 | SHORT | RD |  | status, event 8 input 4 (0=off, 1=on)
4269 | SHORT | RD |  | status, event 8 input 5 (0=off, 1=on)
4270 | SHORT | RD |  | status, event 8 input 6 (0=off, 1=on)
4271 | SHORT | RD |  | status, event 8 input 7 (0=off, 1=on)
4272 | SHORT | RD |  | status, event 8 input 8 (0=off, 1=on)
4273 | SHORT | RD |  | status, event 8 input 9 (0=off, 1=on)
4274 | SHORT | RD |  | status, event 8 input 10 (0=off, 1=on)
4275 | SHORT | RD |  | status, event 8 input 11 (0=off, 1=on)
4276 | SHORT | RD |  | status, event 8 input 12 (0=off, 1=on)
4277 | SHORT | RD |  | status, event 8 input 13 (0=off, 1=on)
4278 | SHORT | RD |  | status, event 8 input 14 (0=off, 1=on)
4279 | SHORT | RD |  | status, event 8 input 15 (0=off, 1=on)
4280 | LONG64 | RD | ms | timestamp [UTC], event 9 input 1
4284 | LONG64 | RD | ms | timestamp [UTC], event 9 input 2
4288 | LONG64 | RD | ms | timestamp [UTC], event 9 input 3
4292 | LONG64 | RD | ms | timestamp [UTC], event 9 input 4
4296 | LONG64 | RD | ms | timestamp [UTC], event 9 input 5
4300 | LONG64 | RD | ms | timestamp [UTC], event 9 input 6
4304 | LONG64 | RD | ms | timestamp [UTC], event 9 input 7
4308 | LONG64 | RD | ms | timestamp [UTC], event 9 input 8
4312 | LONG64 | RD | ms | timestamp [UTC], event 9 input 9
4316 | LONG64 | RD | ms | timestamp [UTC], event 9 input 10
4320 | LONG64 | RD | ms | timestamp [UTC], event 9 input 11
4324 | LONG64 | RD | ms | timestamp [UTC], event 9 input 12
4328 | LONG64 | RD | ms | timestamp [UTC], event 9 input 13
4332 | LONG64 | RD | ms | timestamp [UTC], event 9 input 14
4336 | LONG64 | RD | ms | timestamp [UTC], event 9 input 15
4340 | SHORT | RD |  | status, event 9 input 1 (0=off, 1=on)
4341 | SHORT | RD |  | status, event 9 input 2 (0=off, 1=on)
4342 | SHORT | RD |  | status, event 9 input 3 (0=off, 1=on)
4343 | SHORT | RD |  | status, event 9 input 4 (0=off, 1=on)
4344 | SHORT | RD |  | status, event 9 input 5 (0=off, 1=on)
4345 | SHORT | RD |  | status, event 9 input 6 (0=off, 1=on)
4346 | SHORT | RD |  | status, event 9 input 7 (0=off, 1=on)
4347 | SHORT | RD |  | status, event 9 input 8 (0=off, 1=on)
4348 | SHORT | RD |  | status, event 9 input 9 (0=off, 1=on)
4349 | SHORT | RD |  | status, event 9 input 10 (0=off, 1=on)
4350 | SHORT | RD |  | status, event 9 input 11 (0=off, 1=on)
4351 | SHORT | RD |  | status, event 9 input 12 (0=off, 1=on)
4352 | SHORT | RD |  | status, event 9 input 13 (0=off, 1=on)
4353 | SHORT | RD |  | status, event 9 input 14 (0=off, 1=on)
4354 | SHORT | RD |  | status, event 9 input 15 (0=off, 1=on)
4355 | LONG64 | RD | ms | timestamp [UTC], event 10 input 1
4359 | LONG64 | RD | ms | timestamp [UTC], event 10 input 2
4363 | LONG64 | RD | ms | timestamp [UTC], event 10 input 3
4367 | LONG64 | RD | ms | timestamp [UTC], event 10 input 4
4371 | LONG64 | RD | ms | timestamp [UTC], event 10 input 5
4375 | LONG64 | RD | ms | timestamp [UTC], event 10 input 6
4379 | LONG64 | RD | ms | timestamp [UTC], event 10 input 7
4383 | LONG64 | RD | ms | timestamp [UTC], event 10 input 8
4387 | LONG64 | RD | ms | timestamp [UTC], event 10 input 9
4391 | LONG64 | RD | ms | timestamp [UTC], event 10 input 10
4395 | LONG64 | RD | ms | timestamp [UTC], event 10 input 11
4399 | LONG64 | RD | ms | timestamp [UTC], event 10 input 12
4403 | LONG64 | RD | ms | timestamp [UTC], event 10 input 13
4407 | LONG64 | RD | ms | timestamp [UTC], event 10 input 14
4411 | LONG64 | RD | ms | timestamp [UTC], event 10 input 15
4415 | SHORT | RD |  | status, event 10 input 1 (0=off, 1=on)
4416 | SHORT | RD |  | status, event 10 input 2 (0=off, 1=on)
4417 | SHORT | RD |  | status, event 10 input 3 (0=off, 1=on)
4418 | SHORT | RD |  | status, event 10 input 4 (0=off, 1=on)
4419 | SHORT | RD |  | status, event 10 input 5 (0=off, 1=on)
4420 | SHORT | RD |  | status, event 10 input 6 (0=off, 1=on)
4421 | SHORT | RD |  | status, event 10 input 7 (0=off, 1=on)
4422 | SHORT | RD |  | status, event 10 input 8 (0=off, 1=on)
4423 | SHORT | RD |  | status, event 10 input 9 (0=off, 1=on)
4424 | SHORT | RD |  | status, event 10 input 10 (0=off, 1=on)
4425 | SHORT | RD |  | status, event 10 input 11 (0=off, 1=on)
4426 | SHORT | RD |  | status, event 10 input 12 (0=off, 1=on)
4427 | SHORT | RD |  | status, event 10 input 13 (0=off, 1=on)
4428 | SHORT | RD |  | status, event 10 input 14 (0=off, 1=on)
4429 | SHORT | RD |  | status, event 10 input 15 (0=off, 1=on)
4430 | LONG64 | RD | ms | timestamp [UTC], event 11 input 1
4434 | LONG64 | RD | ms | timestamp [UTC], event 11 input 2
4438 | LONG64 | RD | ms | timestamp [UTC], event 11 input 3
4442 | LONG64 | RD | ms | timestamp [UTC], event 11 input 4
4446 | LONG64 | RD | ms | timestamp [UTC], event 11 input 5
4450 | LONG64 | RD | ms | timestamp [UTC], event 11 input 6
4454 | LONG64 | RD | ms | timestamp [UTC], event 11 input 7
4458 | LONG64 | RD | ms | timestamp [UTC], event 11 input 8
4462 | LONG64 | RD | ms | timestamp [UTC], event 11 input 9
4466 | LONG64 | RD | ms | timestamp [UTC], event 11 input 10
4470 | LONG64 | RD | ms | timestamp [UTC], event 11 input 11
4474 | LONG64 | RD | ms | timestamp [UTC], event 11 input 12
4478 | LONG64 | RD | ms | timestamp [UTC], event 11 input 13
4482 | LONG64 | RD | ms | timestamp [UTC], event 11 input 14
4486 | LONG64 | RD | ms | timestamp [UTC], event 11 input 15
4490 | SHORT | RD |  | status, event 11 input 1 (0=off, 1=on)
4491 | SHORT | RD |  | status, event 11 input 2 (0=off, 1=on)
4492 | SHORT | RD |  | status, event 11 input 3 (0=off, 1=on)
4493 | SHORT | RD |  | status, event 11 input 4 (0=off, 1=on)
4494 | SHORT | RD |  | status, event 11 input 5 (0=off, 1=on)
4495 | SHORT | RD |  | status, event 11 input 6 (0=off, 1=on)
4496 | SHORT | RD |  | status, event 11 input 7 (0=off, 1=on)
4497 | SHORT | RD |  | status, event 11 input 8 (0=off, 1=on)
4498 | SHORT | RD |  | status, event 11 input 9 (0=off, 1=on)
4499 | SHORT | RD |  | status, event 11 input 10 (0=off, 1=on)
4500 | SHORT | RD |  | status, event 11 input 11 (0=off, 1=on)
4501 | SHORT | RD |  | status, event 11 input 12 (0=off, 1=on)
4502 | SHORT | RD |  | status, event 11 input 13 (0=off, 1=on)
4503 | SHORT | RD |  | status, event 11 input 14 (0=off, 1=on)
4504 | SHORT | RD |  | status, event 11 input 15 (0=off, 1=on)
4505 | LONG64 | RD | ms | timestamp [UTC], event 12 input 1
4509 | LONG64 | RD | ms | timestamp [UTC], event 12 input 2
4513 | LONG64 | RD | ms | timestamp [UTC], event 12 input 3
4517 | LONG64 | RD | ms | timestamp [UTC], event 12 input 4
4521 | LONG64 | RD | ms | timestamp [UTC], event 12 input 5
4525 | LONG64 | RD | ms | timestamp [UTC], event 12 input 6
4529 | LONG64 | RD | ms | timestamp [UTC], event 12 input 7
4533 | LONG64 | RD | ms | timestamp [UTC], event 12 input 8
4537 | LONG64 | RD | ms | timestamp [UTC], event 12 input 9
4541 | LONG64 | RD | ms | timestamp [UTC], event 12 input 10
4545 | LONG64 | RD | ms | timestamp [UTC], event 12 input 11
4549 | LONG64 | RD | ms | timestamp [UTC], event 12 input 12
4553 | LONG64 | RD | ms | timestamp [UTC], event 12 input 13
4557 | LONG64 | RD | ms | timestamp [UTC], event 12 input 14
4561 | LONG64 | RD | ms | timestamp [UTC], event 12 input 15
4565 | SHORT | RD |  | status, event 12 input 1 (0=off, 1=on)
4566 | SHORT | RD |  | status, event 12 input 2 (0=off, 1=on)
4567 | SHORT | RD |  | status, event 12 input 3 (0=off, 1=on)
4568 | SHORT | RD |  | status, event 12 input 4 (0=off, 1=on)
4569 | SHORT | RD |  | status, event 12 input 5 (0=off, 1=on)
4570 | SHORT | RD |  | status, event 12 input 6 (0=off, 1=on)
4571 | SHORT | RD |  | status, event 12 input 7 (0=off, 1=on)
4572 | SHORT | RD |  | status, event 12 input 8 (0=off, 1=on)
4573 | SHORT | RD |  | status, event 12 input 9 (0=off, 1=on)
4574 | SHORT | RD |  | status, event 12 input 10 (0=off, 1=on)
4575 | SHORT | RD |  | status, event 12 input 11 (0=off, 1=on)
4576 | SHORT | RD |  | status, event 12 input 12 (0=off, 1=on)
4577 | SHORT | RD |  | status, event 12 input 13 (0=off, 1=on)
4578 | SHORT | RD |  | status, event 12 input 14 (0=off, 1=on)
4579 | SHORT | RD |  | status, event 12 input 15 (0=off, 1=on)
4580 | LONG64 | RD | ms | timestamp [UTC], event 13 input 1
4584 | LONG64 | RD | ms | timestamp [UTC], event 13 input 2
4588 | LONG64 | RD | ms | timestamp [UTC], event 13 input 3
4592 | LONG64 | RD | ms | timestamp [UTC], event 13 input 4
4596 | LONG64 | RD | ms | timestamp [UTC], event 13 input 5
4600 | LONG64 | RD | ms | timestamp [UTC], event 13 input 6
4604 | LONG64 | RD | ms | timestamp [UTC], event 13 input 7
4608 | LONG64 | RD | ms | timestamp [UTC], event 13 input 8
4612 | LONG64 | RD | ms | timestamp [UTC], event 13 input 9
4616 | LONG64 | RD | ms | timestamp [UTC], event 13 input 10
4620 | LONG64 | RD | ms | timestamp [UTC], event 13 input 11
4624 | LONG64 | RD | ms | timestamp [UTC], event 13 input 12
4628 | LONG64 | RD | ms | timestamp [UTC], event 13 input 13
4632 | LONG64 | RD | ms | timestamp [UTC], event 13 input 14
4636 | LONG64 | RD | ms | timestamp [UTC], event 13 input 15
4640 | SHORT | RD |  | status, event 13 input 1 (0=off, 1=on)
4641 | SHORT | RD |  | status, event 13 input 2 (0=off, 1=on)
4642 | SHORT | RD |  | status, event 13 input 3 (0=off, 1=on)
4643 | SHORT | RD |  | status, event 13 input 4 (0=off, 1=on)
4644 | SHORT | RD |  | status, event 13 input 5 (0=off, 1=on)
4645 | SHORT | RD |  | status, event 13 input 6 (0=off, 1=on)
4646 | SHORT | RD |  | status, event 13 input 7 (0=off, 1=on)
4647 | SHORT | RD |  | status, event 13 input 8 (0=off, 1=on)
4648 | SHORT | RD |  | status, event 13 input 9 (0=off, 1=on)
4649 | SHORT | RD |  | status, event 13 input 10 (0=off, 1=on)
4650 | SHORT | RD |  | status, event 13 input 11 (0=off, 1=on)
4651 | SHORT | RD |  | status, event 13 input 12 (0=off, 1=on)
4652 | SHORT | RD |  | status, event 13 input 13 (0=off, 1=on)
4653 | SHORT | RD |  | status, event 13 input 14 (0=off, 1=on)
4654 | SHORT | RD |  | status, event 13 input 15 (0=off, 1=on)
4655 | LONG64 | RD | ms | timestamp [UTC], event 14 input 1
4659 | LONG64 | RD | ms | timestamp [UTC], event 14 input 2
4663 | LONG64 | RD | ms | timestamp [UTC], event 14 input 3
4667 | LONG64 | RD | ms | timestamp [UTC], event 14 input 4
4671 | LONG64 | RD | ms | timestamp [UTC], event 14 input 5
4675 | LONG64 | RD | ms | timestamp [UTC], event 14 input 6
4679 | LONG64 | RD | ms | timestamp [UTC], event 14 input 7
4683 | LONG64 | RD | ms | timestamp [UTC], event 14 input 8
4687 | LONG64 | RD | ms | timestamp [UTC], event 14 input 9
4691 | LONG64 | RD | ms | timestamp [UTC], event 14 input 10
4695 | LONG64 | RD | ms | timestamp [UTC], event 14 input 11
4699 | LONG64 | RD | ms | timestamp [UTC], event 14 input 12
4703 | LONG64 | RD | ms | timestamp [UTC], event 14 input 13
4707 | LONG64 | RD | ms | timestamp [UTC], event 14 input 14
4711 | LONG64 | RD | ms | timestamp [UTC], event 14 input 15
4715 | SHORT | RD |  | status, event 14 input 1 (0=off, 1=on)
4716 | SHORT | RD |  | status, event 14 input 2 (0=off, 1=on)
4717 | SHORT | RD |  | status, event 14 input 3 (0=off, 1=on)
4718 | SHORT | RD |  | status, event 14 input 4 (0=off, 1=on)
4719 | SHORT | RD |  | status, event 14 input 5 (0=off, 1=on)
4720 | SHORT | RD |  | status, event 14 input 6 (0=off, 1=on)
4721 | SHORT | RD |  | status, event 14 input 7 (0=off, 1=on)
4722 | SHORT | RD |  | status, event 14 input 8 (0=off, 1=on)
4723 | SHORT | RD |  | status, event 14 input 9 (0=off, 1=on)
4724 | SHORT | RD |  | status, event 14 input 10 (0=off, 1=on)
4725 | SHORT | RD |  | status, event 14 input 11 (0=off, 1=on)
4726 | SHORT | RD |  | status, event 14 input 12 (0=off, 1=on)
4727 | SHORT | RD |  | status, event 14 input 13 (0=off, 1=on)
4728 | SHORT | RD |  | status, event 14 input 14 (0=off, 1=on)
4729 | SHORT | RD |  | status, event 14 input 15 (0=off, 1=on)
4730 | LONG64 | RD | ms | timestamp [UTC], event 15 input 1
4734 | LONG64 | RD | ms | timestamp [UTC], event 15 input 2
4738 | LONG64 | RD | ms | timestamp [UTC], event 15 input 3
4742 | LONG64 | RD | ms | timestamp [UTC], event 15 input 4
4746 | LONG64 | RD | ms | timestamp [UTC], event 15 input 5
4750 | LONG64 | RD | ms | timestamp [UTC], event 15 input 6
4754 | LONG64 | RD | ms | timestamp [UTC], event 15 input 7
4758 | LONG64 | RD | ms | timestamp [UTC], event 15 input 8
4762 | LONG64 | RD | ms | timestamp [UTC], event 15 input 9
4766 | LONG64 | RD | ms | timestamp [UTC], event 15 input 10
4770 | LONG64 | RD | ms | timestamp [UTC], event 15 input 11
4774 | LONG64 | RD | ms | timestamp [UTC], event 15 input 12
4778 | LONG64 | RD | ms | timestamp [UTC], event 15 input 13
4782 | LONG64 | RD | ms | timestamp [UTC], event 15 input 14
4786 | LONG64 | RD | ms | timestamp [UTC], event 15 input 15
4790 | SHORT | RD |  | status, event 15 input 1 (0=off, 1=on)
4791 | SHORT | RD |  | status, event 15 input 2 (0=off, 1=on)
4792 | SHORT | RD |  | status, event 15 input 3 (0=off, 1=on)
4793 | SHORT | RD |  | status, event 15 input 4 (0=off, 1=on)
4794 | SHORT | RD |  | status, event 15 input 5 (0=off, 1=on)
4795 | SHORT | RD |  | status, event 15 input 6 (0=off, 1=on)
4796 | SHORT | RD |  | status, event 15 input 7 (0=off, 1=on)
4797 | SHORT | RD |  | status, event 15 input 8 (0=off, 1=on)
4798 | SHORT | RD |  | status, event 15 input 9 (0=off, 1=on)
4799 | SHORT | RD |  | status, event 15 input 10 (0=off, 1=on)
4800 | SHORT | RD |  | status, event 15 input 11 (0=off, 1=on)
4801 | SHORT | RD |  | status, event 15 input 12 (0=off, 1=on)
4802 | SHORT | RD |  | status, event 15 input 13 (0=off, 1=on)
4803 | SHORT | RD |  | status, event 15 input 14 (0=off, 1=on)
4804 | SHORT | RD |  | status, event 15 input 15 (0=off, 1=on)
4805 | LONG64 | RD | ms | timestamp [UTC], event 16 input 1
4809 | LONG64 | RD | ms | timestamp [UTC], event 16 input 2
4813 | LONG64 | RD | ms | timestamp [UTC], event 16 input 3
4817 | LONG64 | RD | ms | timestamp [UTC], event 16 input 4
4821 | LONG64 | RD | ms | timestamp [UTC], event 16 input 5
4825 | LONG64 | RD | ms | timestamp [UTC], event 16 input 6
4829 | LONG64 | RD | ms | timestamp [UTC], event 16 input 7
4833 | LONG64 | RD | ms | timestamp [UTC], event 16 input 8
4837 | LONG64 | RD | ms | timestamp [UTC], event 16 input 9
4841 | LONG64 | RD | ms | timestamp [UTC], event 16 input 10
4845 | LONG64 | RD | ms | timestamp [UTC], event 16 input 11
4849 | LONG64 | RD | ms | timestamp [UTC], event 16 input 12
4853 | LONG64 | RD | ms | timestamp [UTC], event 16 input 13
4857 | LONG64 | RD | ms | timestamp [UTC], event 16 input 14
4861 | LONG64 | RD | ms | timestamp [UTC], event 16 input 15
4865 | SHORT | RD |  | status, event 16 input 1 (0=off, 1=on)
4866 | SHORT | RD |  | status, event 16 input 2 (0=off, 1=on)
4867 | SHORT | RD |  | status, event 16 input 3 (0=off, 1=on)
4868 | SHORT | RD |  | status, event 16 input 4 (0=off, 1=on)
4869 | SHORT | RD |  | status, event 16 input 5 (0=off, 1=on)
4870 | SHORT | RD |  | status, event 16 input 6 (0=off, 1=on)
4871 | SHORT | RD |  | status, event 16 input 7 (0=off, 1=on)
4872 | SHORT | RD |  | status, event 16 input 8 (0=off, 1=on)
4873 | SHORT | RD |  | status, event 16 input 9 (0=off, 1=on)
4874 | SHORT | RD |  | status, event 16 input 10 (0=off, 1=on)
4875 | SHORT | RD |  | status, event 16 input 11 (0=off, 1=on)
4876 | SHORT | RD |  | status, event 16 input 12 (0=off, 1=on)
4877 | SHORT | RD |  | status, event 16 input 13 (0=off, 1=on)
4878 | SHORT | RD |  | status, event 16 input 14 (0=off, 1=on)
4879 | SHORT | RD |  | status, event 16 input 15 (0=off, 1=on)
4880 | SHORT | RD |  | status, digital output 1 (0=off, 1=on)
4881 | SHORT | RD |  | status, digital output 2 (0=off, 1=on)
4882 | SHORT | RD |  | status, digital output 3 (0=off, 1=on)
Miscellaneous
Adress | Format | RD/WR | Unit | Note
4913 | SHORT | RD |  | overtemperature (0=no, 1=yes)
4914 | FLOAT | RD | °C | temperature input
4916 | FLOAT | RD | Ohm | temperature input
4918 | SHORT | RD |  | status tariff 1 (0=not active)
4919 | SHORT | RD |  | status tariff 2 (0=not active)
4920 | SHORT | RD |  | status tariff 3 (0=not active)
4921 | SHORT | RD |  | status tariff 4 (0=not active)
4922 | SHORT | RD |  | status tariff 5 (0=not active)
4923 | SHORT | RD |  | status tariff 6 (0=not active)
4924 | SHORT | RD |  | status tariff 7 (0=not active)
4925 | SHORT | RD |  | status tariff 8 (0=not active)
4926 | SHORT | RD |  | status input 1 (0=off, 1=on)
4927 | SHORT | RD |  | status input 2 (0=off, 1=on)
4928 | SHORT | RD |  | status input 3 (0=off, 1=on)
4929 | SHORT | RD |  | status input 4 (0=off, 1=on)
4930 | SHORT | RD |  | status input 5 (0=off, 1=on)
4931 | SHORT | RD |  | status input 6 (0=off, 1=on)
4932 | SHORT | RD |  | status input 7 (0=off, 1=on)
4933 | SHORT | RD |  | status input 8 (0=off, 1=on)
4934 | SHORT | RD |  | status input 9 (0=off, 1=on)
4935 | SHORT | RD |  | status input 10 (0=off, 1=on)
4936 | SHORT | RD |  | status input 11 (0=off, 1=on)
4937 | SHORT | RD |  | status input 12 (0=off, 1=on)
4938 | SHORT | RD |  | status input 13 (0=off, 1=on)
4939 | SHORT | RD |  | status input 14 (0=off, 1=on)
4940 | SHORT | RD |  | status input 15 (0=off, 1=on)
4941 | USHORT | RD |  | status tariff, binary (X000 0000)
4942 | SHORT | RD |  | Bit0 = 1: Battery capacity exhausted. Clock has stopped. Bit1 = 1: Battery capacity nearly exhausted. Replace battery. Bit2 = 1: Battery capacity low. Battery should be replaced.