## Tabelle1
Address List
Frequently required readings
Address | Type | RD/WR | Designation | Unit | Remark
19000 | float | RD | _ULN[0] | V | Voltage L1-N
19002 | float | RD | _ULN[1] | V | Voltage L2-N
19004 | float | RD | _ULN[2] | V | Voltage L3-N
19006 | float | RD | _ULL[0] | V | Voltage L1-L2
19008 | float | RD | _ULL[1] | V | Voltage L2-L3
19010 | float | RD | _ULL[2] | V | Voltage L3-L1
19012 | float | RD | _ILN[0] | A | Apparent current, L1
19014 | float | RD | _ILN[1] | A | Apparent current, L2
19016 | float | RD | _ILN[2] | A | Apparent current, L3
19018 | float | RD | _I_SUM3 | A | Vector sum; IN=I1+I2+I3
19020 | float | RD | _PLN[0] | W | Real power L1
19022 | float | RD | _PLN[1] | W | Real power L2
19024 | float | RD | _PLN[2] | W | Real power L3
19026 | float | RD | _P_SUM3 | W | Sum; Psum3=P1+P2+P3
19028 | float | RD | _SLN[0] | VA | Apparent power L1
19030 | float | RD | _SLN[1] | VA | Apparent power L2
19032 | float | RD | _SLN[2] | VA | Apparent power L3
19034 | float | RD | _S_SUM3 | VA | Sum; Ssum3=S1+S2+S3
19036 | float | RD | _QLN[0] | var | Reactive power (mains frequ.) L1
19038 | float | RD | _QLN[1] | var | Reactive power (mains frequ.) L2
19040 | float | RD | _QLN[2] | var | Reactive power (mains frequ.) L3
19042 | float | RD | _Q_SUM3 | var | Sum; Qsum3=Q1+Q2+Q3
19044 | float | RD | _COS_PHI[0] |  | Fund.power factor, CosPhi; UL1 IL1
19046 | float | RD | _COS_PHI[1] |  | Fund.power factor, CosPhi; UL2 IL2
19048 | float | RD | _COS_PHI[2] |  | Fund.power factor, CosPhi; UL3 IL3
19050 | float | RD | _FREQ | Hz | Measured frequency
19052 | float | RD | _PHASE_SEQ |  | Rotation field; 1=right, 0=none, -1=left
19054* | float | RD | _WH_V[0] | Wh | Real energy L1, consumed
19056* | float | RD | _WH_V[1] | Wh | Real energy L2, consumed
19058* | float | RD | _WH_V[2] | Wh | Real energy L3, consumed
19060 | float | RD | _WH_V_HT_SUML13 | Wh | Real energy L1..L3
19062 | float | RD | _WH_V[0] | Wh | Real energy L1, consumed
19064 | float | RD | _WH_V[1] | Wh | Real energy L2, consumed
19066 | float | RD | _WH_V[2] | Wh | Real energy L3, consumed
19068 | float | RD | _WH_V_HT_SUML13 | Wh | Real energy L1..L3, consumed, rate 1
19070 | float | RD | _WH_Z[0] | Wh | Real energy L1, delivered
19072 | float | RD | _WH_Z[1] | Wh | Real energy L2, delivered
19074 | float | RD | _WH_Z[2] | Wh | Real energy L3, delivered
19076 | float | RD | _WH_Z_SUML13 | Wh | Real energy L1..L3, delivered
19078 | float | RD | _WH_S[0] | VAh | Apparent energy L1
19080 | float | RD | _WH_S[1] | VAh | Apparent energy L2
19082 | float | RD | _WH_S[2] | VAh | Apparent energy L3
19084 | float | RD | _WH_S_SUML13 | VAh | Apparent energy L1..L3
19086* | float | RD | _IQH[0] | varh | Reactive energy, inductive, L1
19088* | float | RD | _IQH[1] | varh | Reactive energy, inductive, L2
19090* | float | RD | _IQH[2] | varh | Reactive energy, inductive, L3
19092 | float | RD | _IQH_SUML13 | varh | Reactive energy L1..L3
19094 | float | RD | _IQH[0] | varh | Reactive energy, inductive, L1
19096 | float | RD | _IQH[1] | varh | Reactive energy, inductive, L2
19098 | float | RD | _IQH[2] | varh | Reactive energy, inductive, L3
19100 | float | RD | _IQH_SUML13 | varh | Reactive energy L1..L3, ind.
19102 | float | RD | _CQH[0] | varh | Reactive energy, capacitive, L1
19104 | float | RD | _CQH[1] | varh | Reactive energy, capacitive, L2
19106 | float | RD | _CQH[2] | varh | Reactive energy, capacitive, L3
19108 | float | RD | _CQH_SUML13 | varh | Reactive energy L1..L3, cap.
19110 | float | RD | _THD_ULN[0] | % | Harmonic, THD,U L1-N
19112 | float | RD | _THD_ULN[1] | % | Harmonic, THD,U L2-N
19114 | float | RD | _THD_ULN[2] | % | Harmonic, THD,U L3-N
19116 | float | RD | _THD_ILN[0] | % | Harmonic, THD,I L1
19118 | float | RD | _THD_ILN[1] | % | Harmonic, THD,I L2
19120 | float | RD | _THD_ILN[2] | % | Harmonic, THD,I L3
Address | Designation | Configuration Range |  | Type | Default Setting
8 | Delete MinMax-Value | 0 | 1 | CHAR | 0
9 | Delete_Work | 0 | 1 | CHAR | 0
13 | Comparator 1A, Threshold Val. | -999999999 | 999999999 | LONG | 0
15 | Comparator 1A, Measured Val. | 0 | 999 | SHORT
16 | Comparator 1A, Min. Duration | 1 | 900 | SHORT | 1 Sec.
17 | Comparator 1A, Operator | 0 | 1 | CHAR | 0
18 | Comparator 1B, Threshold Val. | -999999999 | 999999999 | LONG | 0
20 | Comparator 1B, Measured Val. | 0 | 999 | SHORT
21 | Comparator 1B, Min. Duration | 1 | 900 | SHORT | 1 Sec.
22 | Comparator 1B, Operator | 0 | 1 | CHAR | 0
23 | Comparator 1C, Threshold Val. | -999999999 | 999999999 | LONG | 0
25 | Comparator 1C, Measured Val. | 0 | 999 | SHORT
26 | Comparator 1C, Min. Duration | 1 | 900 | SHORT | 1 Sec.
27 | Comparator 1C, Operator | 0 | 1 | CHAR | 0
28 | Comparator 2A, Threshold Val. | -999999999 | 999999999 | LONG | 0
30 | Comparator 2A, Measured Val. | 0 | 999 | SHORT
31 | Comparator 2A, Min. Duration | 1 | 900 | SHORT | 1 Sec.
32 | Comparator 2A, Operator | 0 | 1 | CHAR | 0
33 | Comparator 2B, Threshold Val. | -999999999 | 999999999 | LONG | 0
35 | Comparator 2B, Measured Val. | 0 | 999 | SHORT
36 | Comparator 2B, Min. Duration | 1 | 900 | SHORT | 1 Sec.
37 | Comparator 2B, Operator | 0 | 1 | CHAR | 0
38 | Comparator 2C, Threshold Val. | -999999999 | 999999999 | LONG | 0
40 | Comparator 2C, Measured Val. | 0 | 999 | SHORT
41 | Comparator 2C, Min. Duration | 1 | 900 | SHORT | 1 Sec.
42 | Comparator 2C, Operator | 0 | 1 | CHAR | 0
43 | Output[0] link | 0 | 1 | CHAR | 0
44 | Output[0] invert | 0 | 1 | CHAR | 0
45 | Output[1] link | 0 | 1 | CHAR | 0
46 | Output[1] invert | 0 | 1 | CHAR | 0
57 | Averaging Time for all I | 0 | 8 | CHAR
58 | Averaging Time for all P | 0 | 8 | CHAR | 0 = 5 Sec. 1 = 10 Sec. 2 = 30 Sec. 3 = 60 Sec. 4 = 300 Sec. 5 = 480 Sec. 6 = 900 Sec. (default) 7 = 30 Min. 8 = 60 Min.
63 | Frequency | 0 | 2 | CHAR | 0=Automatic (default) 1=50Hz 2=60Hz
64 | Comparator 1A Lead Time | 1 | 900 | SHORT | 0 Sec.
65 | Comparator 1B Lead Time | 1 | 900 | SHORT | 0 Sec.
66 | Comparator 1C Lead Time | 1 | 900 | SHORT | 0 Sec.
67 | Comparator 2A Lead Time | 1 | 900 | SHORT | 0 Sec.
68 | Comparator 2B Lead Time | 1 | 900 | SHORT | 0 Sec.
69 | Comparator 2C Lead Time | 1 | 900 | SHORT | 0 Sec.
71 | HT/ switch real energy | 0 | 1 | CHAR | 0
72 | HT/NT switch reactive energy | 0 | 1 | CHAR | 0
73 | Averaging time for all U | 0 | 8 | CHAR | 0 = 5 Sec. 1 = 10 Sec. 2 = 30 Sec. 3 = 60 Sec. 4 = 300 Sec. 5 = 480 Sec. 6 = 900 Sec. (default) 7 = 30 Min. 8 = 60 Min.
600 | ct_prim | 0 | 10000 | SHORT | Primary Current Converter (in A)
601 | ct_sec | 1 | 5 | SHORT | Secondary Current Converter (in A)
602 | vt_prim | 100 | 60000 | USHORT | Primary Voltage Converter (in V)
603 | vt_sec | 100 | 400 | SHORT | Secondary Voltage Converter (in V)
800 | Write Operations in EEPROM Bit 1 = 1, write calibration data Bit 2 = 1, Write programming data Bit 4 = 1, Write counter Bit 8 = 1, Min-max values |  | 1 | SHORT
860 | Calibration Password |  |  | SHORT
911 | Serial number | only read |  | LONG
913 | Firmware-Release | only read |  | SHORT
914 | Hardware-Expansion | only read |  | SHORT
Address | Designation | Scaling Factor | Type | Unit | Remark
200 | Voltage Uln L1 | 10 | SHORT | V | VT
201 | Voltage Uln L2 | 10 | SHORT | V | VT
202 | Voltage Uln L3 | 10 | SHORT | V | VT
203 | Voltage Ull L1-L2 | 10 | SHORT | V | VT
204 | Voltage Ull L2-L3 | 10 | SHORT | V | VT
205 | Voltage Ull L3-L1 | 10 | SHORT | V | VT
206 | Current I L1 | 1000 | SHORT | mA | CT
207 | Current I L2 | 1000 | SHORT | mA | CT
208 | Current I L3 | 1000 | SHORT | mA | CT
209 | Real power L1 | 10 | SHORT | W | CT VT
210 | Real power L2 | 10 | SHORT | W | CT VT
211 | Real power L3 | 10 | SHORT | W | CT VT
212 | Reactive power L1 | 10 | SHORT | var | CT VT
213 | Reactive power L2 | 10 | SHORT | var | CT VT
214 | Reactive power L3 | 10 | SHORT | var | CT VT
215 | Apparent power L1 | 10 | SHORT | VA | CT VT
216 | Apparent power L2 | 10 | SHORT | VA | CT VT
217 | Apparent power L3 | 10 | SHORT | VA | CT VT
218 | CosPhi L1 | 100 | SHORT | -
219 | CosPhi L2 | 100 | SHORT | -
220 | CosPhi L3 | 100 | SHORT | -
221 | 1. Harmonic U L1 | 10 | SHORT | V | VT
222 | 3. Harmonic U L1 | 10 | SHORT | V | VT
223 | 5. Harmonic U L1 | 10 | SHORT | V | VT
224 | 7. Harmonic U L1 | 10 | SHORT | V | VT
225 | 9. Harmonic U L1 | 10 | SHORT | V | VT
226 | 11. Harmonic U L1 | 10 | SHORT | V | VT
227 | 13. Harmonic U L1 | 10 | SHORT | V | VT
228 | 15. Harmonic U L1 | 10 | SHORT | V | VT
229 | 1. Harmonic U L2 | 10 | SHORT | V | VT
230 | 3. Harmonic U L2 | 10 | SHORT | V | VT
231 | 5. Harmonic U L2 | 10 | SHORT | V | VT
232 | 7. Harmonic U L2 | 10 | SHORT | V | VT
233 | 9. Harmonic U L2 | 10 | SHORT | V | VT
234 | 11. Harmonic U L2 | 10 | SHORT | V | VT
235 | 13. Harmonic U L2 | 10 | SHORT | V | VT
236 | 15. Harmonic U L2 | 10 | SHORT | V | VT
237 | 1. Harmonic U L3 | 10 | SHORT | V | VT
238 | 3. Harmonic U L3 | 10 | SHORT | V | VT
239 | 5. Harmonic U L3 | 10 | SHORT | V | VT
240 | 7. Harmonic U L3 | 10 | SHORT | V | VT
241 | 9. Harmonic U L3 | 10 | SHORT | V | VT
242 | 11. Harmonic U L3 | 10 | SHORT | V | VT
243 | 13. Harmonic U L3 | 10 | SHORT | V | VT
244 | 15. Harmonic U L3 | 10 | SHORT | V | VT
245 | 1. Harmonic I L1 | 1000 | SHORT | mA | CT
246 | 3. Harmonic I L1 | 1000 | SHORT | mA | CT
247 | 5. Harmonic I L1 | 1000 | SHORT | mA | CT
248 | 7. Harmonic I L1 | 1000 | SHORT | mA | CT
249 | 9. Harmonic I L1 | 1000 | SHORT | mA | CT
250 | 11. Harmonic I L1 | 1000 | SHORT | mA | CT
251 | 13. Harmonic I L1 | 1000 | SHORT | mA | CT
252 | 15. Harmonic I L1 | 1000 | SHORT | mA | CT
253 | 1. Harmonic I L2 | 1000 | SHORT | mA | CT
254 | 3. Harmonic I L2 | 1000 | SHORT | mA | CT
255 | 5. Harmonic I L2 | 1000 | SHORT | mA | CT
256 | 7. Harmonic I L2 | 1000 | SHORT | mA | CT
257 | 9. Harmonic I L2 | 1000 | SHORT | mA | CT
258 | 11. Harmonic I L2 | 1000 | SHORT | mA | CT
259 | 13. Harmonic I L2 | 1000 | SHORT | mA | CT
260 | 15. Harmonic I L2 | 1000 | SHORT | mA | CT
261 | 1. Harmonic I L3 | 1000 | SHORT | mA | CT
262 | 3. Harmonic I L3 | 1000 | SHORT | mA | CT
263 | 5. Harmonic I L3 | 1000 | SHORT | mA | CT
264 | 7. Harmonic I L3 | 1000 | SHORT | mA | CT
265 | 9. Harmonic I L3 | 1000 | SHORT | mA | CT
266 | 11. Harmonic I L3 | 1000 | SHORT | mA | CT
267 | 13. Harmonic I L3 | 1000 | SHORT | mA | CT
268 | 15. Harmonic I L3 | 1000 | SHORT | mA | CT
269 | THD U L1 | 1000 | SHORT | %
270 | THD U L2 | 1000 | SHORT | %
271 | THD U L3 | 1000 | SHORT | %
272 | THD I L1 | 1000 | SHORT | %
273 | THD I L2 | 1000 | SHORT | %
274 | THD I L3 | 1000 | SHORT | %
275 | Frequency | 100 | USHORT | Hz
276 | CosPhi sum | 100 | SHORT | -
277 | Rotation field | 1 | SHORT | - | +1= right rotary field 0= no rotary field -1= left rotary field
278 | I Sum (converted current in N) | 1000 | SHORT | mA | CT
279 | P Sum | 1 | SHORT | W | CT VT
280 | Q Sum | 1 | SHORT | var | CT VT
281 | S Sum | 1 | SHORT | VA | CT VT
282 | Mean value I L1 | 1000 | SHORT | mA | CT
283 | Mean value I L2 | 1000 | SHORT | mA | CT
284 | Mean value I L3 | 1000 | SHORT | mA | CT
285 | Mean value P L1 | 10 | SHORT | W | CT VT
286 | Mean value P L2 | 10 | SHORT | W | CT VT
287 | Mean value P L3 | 10 | SHORT | W | CT VT
288 | Mean value Q L1 | 10 | SHORT | var | CT VT
289 | Mean value Q L2 | 10 | SHORT | var | CT VT
290 | Mean value Q L3 | 10 | SHORT | var | CT VT
291 | Mean value S L1 | 10 | SHORT | VA | CT VT
292 | Mean value S L2 | 10 | SHORT | VA | CT VT
293 | Mean value S L3 | 10 | SHORT | VA | CT VT
294 | Mean value I Sum | 1000 | SHORT | mA | CT
295 | Mean value P Sum | 1 | SHORT | W | CT VT
296 | Mean value Q Sum | 1 | SHORT | var | CT VT
297 | Mean value S Sum | 1 | SHORT | VA | CT VT
298 | Max. Mean value I Sum | 1000 | SHORT | mA | CT
299 | Max. Mean value P Sum | 1 | SHORT | W | CT VT
300 | Max. value I Sum | 1000 | SHORT | mA | CT
301 | Max. value P Sum | 1 | SHORT | W | CT VT
302 | Max. value Q Sum | 1 | SHORT | var | CT VT
303 | Max. value S Sum | 1 | SHORT | VA | CT VT
304 | Max. value CosPhi Sum | 100 | SHORT | -
305 | Min. value Uln L1 | 10 | SHORT | V | VT
306 | Min. value Uln L2 | 10 | SHORT | V | VT
307 | Min. value Uln L3 | 10 | SHORT | V | VT
308 | Max. value Uln L1 | 10 | SHORT | V | VT
309 | Max. value Uln L2 | 10 | SHORT | V | VT
310 | Max. value Uln L3 | 10 | SHORT | V | VT
311 | Min. value Ull L1-L2 | 10 | SHORT | V | VT
312 | Min. value Ull L2-L3 | 10 | SHORT | V | VT
313 | Min. value Ull L3-L1 | 10 | SHORT | V | VT
314 | Max. value Ull L1-L2 | 10 | SHORT | V | VT
315 | Max. value Ull L2-L3 | 10 | SHORT | V | VT
316 | Max. value Ull L3-L1 | 10 | SHORT | V | VT
317 | Max. value I L1 | 1000 | SHORT | mA | CT
318 | Max. value I L2 | 1000 | SHORT | mA | CT
319 | Max. value I L3 | 1000 | SHORT | mA | CT
320 | Max_Mean value I L1 | 1000 | SHORT | mA | CT
321 | Max_Mean value I L2 | 1000 | SHORT | mA | CT
322 | Max_Mean value I L3 | 1000 | SHORT | mA | CT
323 | Max. value P L1 | 10 | SHORT | W | CT VT
324 | Max. value P L2 | 10 | SHORT | W | CT VT
325 | Max. value P L3 | 10 | SHORT | W | CT VT
326 | Max. value Q L1 | 10 | SHORT | var | CT VT
327 | Max. value Q L2 | 10 | SHORT | var | CT VT
328 | Max. value Q L3 | 10 | SHORT | var | CT VT
329 | Max. value S L1 | 10 | SHORT | VA | CT VT
330 | Max. value S L2 | 10 | SHORT | VA | CT VT
331 | Max. value S L3 | 10 | SHORT | VA | CT VT
332 | Max. value 1. Harmonic U L1 | 10 | SHORT | V | VT
333 | Max. value 3. Harmonic U L1 | 10 | SHORT | V | VT
334 | Max. value 5. Harmonic U L1 | 10 | SHORT | V | VT
335 | Max. value 7. Harmonic U L1 | 10 | SHORT | V | VT
336 | Max. value 9. Harmonic U L1 | 10 | SHORT | V | VT
337 | Max. value 11. Harmonic U L1 | 10 | SHORT | V | VT
338 | Max. value 13. Harmonic U L1 | 10 | SHORT | V | VT
339 | Max. value 15. Harmonic U L1 | 10 | SHORT | V | VT
340 | Max. value 1. Harmonic U L2 | 10 | SHORT | V | VT
341 | Max. value 3. Harmonic U L2 | 10 | SHORT | V | VT
342 | Max. value 5. Harmonic U L2 | 10 | SHORT | V | VT
343 | Max. value 7. Harmonic U L2 | 10 | SHORT | V | VT
344 | Max. value 9. Harmonic U L2 | 10 | SHORT | V | VT
345 | Max. value 11. Harmonic U L2 | 10 | SHORT | V | VT
346 | Max. value 13. Harmonic U L2 | 10 | SHORT | V | VT
347 | Max. value 15. Harmonic U L2 | 10 | SHORT | V | VT
348 | Max. value 1. Harmonic U L3 | 10 | SHORT | V | VT
349 | Max. value 3. Harmonic U L3 | 10 | SHORT | V | VT
350 | Max. value 5. Harmonic U L3 | 10 | SHORT | V | VT
351 | Max. value 7. Harmonic U L3 | 10 | SHORT | V | VT
352 | Max. value 9. Harmonic U L3 | 10 | SHORT | V | VT
353 | Max. value 11. Harmonic U L3 | 10 | SHORT | V | VT
354 | Max. value 13. Harmonic U L3 | 10 | SHORT | V | VT
355 | Max. value 15. Harmonic U L3 | 10 | SHORT | V | VT
356 | Max. value 1. Harmonic I L1 | 1000 | SHORT | mA | CT
357 | Max. value 3. Harmonic I L1 | 1000 | SHORT | mA | CT
358 | Max. value 5. Harmonic I L1 | 1000 | SHORT | mA | CT
359 | Max. value 7. Harmonic I L1 | 1000 | SHORT | mA | CT
360 | Max. value 9. Harmonic I L1 | 1000 | SHORT | mA | CT
361 | Max. value 11. Harmonic I L1 | 1000 | SHORT | mA | CT
362 | Max. value 13. Harmonic I L1 | 1000 | SHORT | mA | CT
363 | Max. value 15. Harmonic I L1 | 1000 | SHORT | mA | CT
364 | Max. value 1. Harmonic I L2 | 1000 | SHORT | mA | CT
365 | Max. value 3. Harmonic I L2 | 1000 | SHORT | mA | CT
366 | Max. value 5. Harmonic I L2 | 1000 | SHORT | mA | CT
367 | Max. value 7. Harmonic I L2 | 1000 | SHORT | mA | CT
368 | Max. value 9. Harmonic I L2 | 1000 | SHORT | mA | CT
369 | Max. value 11. Harmonic I L2 | 1000 | SHORT | mA | CT
370 | Max. value 13. Harmonic I L2 | 1000 | SHORT | mA | CT
371 | Max. value 15. Harmonic I L2 | 1000 | SHORT | mA | CT
372 | Max. value 1. Harmonic I L3 | 1000 | SHORT | mA | CT
373 | Max. value 3. Harmonic I L3 | 1000 | SHORT | mA | CT
374 | Max. value 5. Harmonic I L3 | 1000 | SHORT | mA | CT
375 | Max. value 7. Harmonic I L3 | 1000 | SHORT | mA | CT
376 | Max. value 9. Harmonic I L3 | 1000 | SHORT | mA | CT
377 | Max. value 11. Harmonic I L3 | 1000 | SHORT | mA | CT
378 | Max. value 13. Harmonic I L3 | 1000 | SHORT | mA | CT
379 | Max. value 15. Harmonic I L3 | 1000 | SHORT | mA | CT
380 | Max. value THD U L1 | 1 | SHORT | %
381 | Max. value THD U L2 | 1 | SHORT | %
382 | Max. value THD U L3 | 1 | SHORT | %
383 | Max. value THD I L1 | 1 | SHORT | %
384 | Max. value THD I L2 | 1 | SHORT | %
385 | Max. value THD I L3 | 1 | SHORT | %
386 | Comparator Result 1A | 1 | CHAR | -
387 | Comparator Result 1B | 1 | CHAR | -
388 | Comparator Result 1C | 1 | CHAR | -
389 | Comparator Group 1, total result | 1 | CHAR | -
390 | Comparator Result 2A | 1 | CHAR | -
391 | Comparator Result 2B | 1 | CHAR | -
392 | Comparator Result 2C | 1 | CHAR | -
393 | Comparator Group 2, total result | 1 | CHAR | -
394 | Operating Hour Counter | 1 | LONG | Sec.
396 | Total Run Time Comparator 1A | 1 | LONG | Sec.
398 | Total Run Time Comparator 1B | 1 | LONG | Sec.
400 | Total Run Time Comparator 1C | 1 | LONG | Sec.
402 | Total Run Time Comparator 2A | 1 | LONG | Sec.
404 | Total Run Time Comparator 2B | 1 | LONG | Sec.
406 | Total Run Time Comparator 2C | 1 | LONG | Sec.
410 | Time since the 1.1.1970 | 1 | LONG | Sec.
412 | Mean value CosPhi Sum | 100 | SHORT | -
413 | Measuring range exceeded Bit 1 = I > 6,5A L1 Bit 2 = I > 6,5A L2 Bit 3 = I > 6,5A L3 Bit 4 = free Bit 5 = U > 300V L1-N Bit 6 = U > 300V L2-N Bit 7 = U > 300V L3-N Bit 8 = free | 1 | CHAR | -
416 | Real energy Sum without return travel block | 1 | LONG | Wh | CT VT
418 | Reactive energy, Sum inductive | 1 | LONG | varh | CT VT
422 | Real energy, consumed, Sum | 1 | LONG | Wh | CT VT
424 | Real energy, delivered, Sum | 1 | LONG | Wh | CT VT
426 | Reactive energy, capacitive, Sum | 1 | LONG | varh | CT VT
428 | Reactive energy, Sum | 1 | LONG | varh | CT VT
430 | Apparent energy, Sum | 1 | LONG | VAh | CT VT
432 | Mean value UL1-N | 10 | SHORT | V | VT
433 | Mean value UL2-N | 10 | SHORT | V | VT
434 | Mean value UL3-N | 10 | SHORT | V | VT
435 | Mean value UL1-L2 | 10 | SHORT | V | VT
436 | Mean value UL2-L3 | 10 | SHORT | V | VT
437 | Mean value UL3-L1 | 10 | SHORT | V | VT
438 | Over-range | - | LONG | status
600 | ct_prim | 0 | 10000 | SHORT | A | Current transf., prim.
601 | ct_sec | 1 | 5 | SHORT | A | Current transf., second.
602 | vt_prim | 100 | 60000 | USHORT | V | Voltage transf., prim.
603 | vt_sec | 100 | 400 | SHORT | V | Voltage transf., second.
800 | Write in EEPROM Bit 1 = 1, Write calibration data Bit 2 = 1, Write programming data Bit 4 = 1, Write counter Bit 8 = 1, Write min-max values |  | 1 | SHORT
860 | Calibration Password | 1 | SHORT
911 | Serial number | 1 | LONG
913 | Firmware release | 1 | SHORT
914 | Hardware expansion | 1 | SHORT
920 | Calibration value U L1 | 1 | FLOAT
922 | Calibration value U L2 | 1 | FLOAT
924 | Calibration value U L3 | 1 | FLOAT
926 | Calibration value I L1 | 1 | FLOAT
928 | Calibration value I L2 | 1 | FLOAT
930 | Calibration value I L3 | 1 | FLOAT
932 | Calibration value Phase U L1 | 1 | FLOAT
934 | Calibration value Phase U L2 | 1 | FLOAT
936 | Calibration value Phase U L3 | 1 | FLOAT
938 | Calibration value Phase I L1 | 1 | FLOAT
940 | Calibration value Phase I L2 | 1 | FLOAT
942 | Calibration value Phase I L3 | 1 | FLOAT
1000 | U L1 | 1 | FLOAT
1002 | U L2 | 1 | FLOAT
1004 | U L3 | 1 | FLOAT
1006 | U L1-L2 | 1 | FLOAT
1008 | U L2-L3 | 1 | FLOAT
1010 | U L3-L1 | 1 | FLOAT
1012 | I L1 | 1 | FLOAT
1014 | I L2 | 1 | FLOAT
1016 | I L3 | 1 | FLOAT
1018 | I Sum (converted current in N) | 1 | FLOAT
1020 | P L1 | 1 | FLOAT
1022 | P L2 | 1 | FLOAT
1024 | P L3 | 1 | FLOAT
1026 | P Sum | 1 | FLOAT
1028 | Q L1 | 1 | FLOAT
1030 | Q L2 | 1 | FLOAT
1032 | Q L3 | 1 | FLOAT
1034 | Q Sum | 1 | FLOAT
1036 | S L1 | 1 | FLOAT
1038 | S L2 | 1 | FLOAT
1040 | S L3 | 1 | FLOAT
1042 | S Sum | 1 | FLOAT
1044 | CosPhi L1 | 1 | FLOAT
1046 | CosPhi L2 | 1 | FLOAT
1048 | CosPhi L3 | 1 | FLOAT
1050 | CosPhi Sum | 1 | FLOAT
1052 | Real power, fundamental oscillation L1 | 1 | FLOAT
1054 | Real power, fundamental oscillation L2 | 1 | FLOAT
1056 | Real power, fundamental oscillation L3 | 1 | FLOAT
1058 | 1. Harmonic U L1 | 1 | FLOAT
1060 | 3. Harmonic U L1 | 1 | FLOAT
1062 | 5. Harmonic U L1 | 1 | FLOAT
1064 | 7. Harmonic U L1 | 1 | FLOAT
1066 | 9. Harmonic U L1 | 1 | FLOAT
1068 | 11. Harmonic U L1 | 1 | FLOAT
1070 | 13. Harmonic U L1 | 1 | FLOAT
1072 | 15. Harmonic U L1 | 1 | FLOAT
1074 | 17. Harmonic U L1 | 1 | FLOAT
1076 | 19. Harmonic U L1 | 1 | FLOAT
1078 | 21. Harmonic U L1 | 1 | FLOAT
1080 | 23. Harmonic U L1 | 1 | FLOAT
1082 | 25. Harmonic U L1 | 1 | FLOAT
1084 | 1. Harmonic U L2 | 1 | FLOAT
1086 | 3. Harmonic U L2 | 1 | FLOAT
1088 | 5. Harmonic U L2 | 1 | FLOAT
1090 | 7. Harmonic U L2 | 1 | FLOAT
1092 | 9. Harmonic U L2 | 1 | FLOAT
1094 | 11. Harmonic U L2 | 1 | FLOAT
1096 | 13. Harmonic U L2 | 1 | FLOAT
1098 | 15. Harmonic U L2 | 1 | FLOAT
1100 | 17. Harmonic U L2 | 1 | FLOAT
1102 | 19. Harmonic U L2 | 1 | FLOAT
1104 | 21. Harmonic U L2 | 1 | FLOAT
1106 | 23. Harmonic U L2 | 1 | FLOAT
1108 | 25. Harmonic U L2 | 1 | FLOAT
1110 | 1. Harmonic U L3 | 1 | FLOAT
1112 | 3. Harmonic U L3 | 1 | FLOAT
1114 | 5. Harmonic U L3 | 1 | FLOAT
1116 | 7. Harmonic U L3 | 1 | FLOAT
1118 | 9. Harmonic U L3 | 1 | FLOAT
1120 | 11. Harmonic U L3 | 1 | FLOAT
1122 | 13. Harmonic U L3 | 1 | FLOAT
1124 | 15. Harmonic U L3 | 1 | FLOAT
1126 | 17. Harmonic U L3 | 1 | FLOAT
1128 | 19. Harmonic U L3 | 1 | FLOAT
1130 | 21. Harmonic U L3 | 1 | FLOAT
1132 | 23. Harmonic U L3 | 1 | FLOAT
1134 | 25. Harmonic U L3 | 1 | FLOAT
1136 | 1. Harmonic I L1 | 1 | FLOAT
1138 | 3. Harmonic I L1 | 1 | FLOAT
1140 | 5. Harmonic I L1 | 1 | FLOAT
1142 | 7. Harmonic I L1 | 1 | FLOAT
1144 | 9. Harmonic I L1 | 1 | FLOAT
1146 | 11. Harmonic I L1 | 1 | FLOAT
1148 | 13. Harmonic I L1 | 1 | FLOAT
1150 | 15. Harmonic I L1 | 1 | FLOAT
1152 | 17. Harmonic I L1 | 1 | FLOAT
1154 | 19. Harmonic I L1 | 1 | FLOAT
1156 | 21. Harmonic I L1 | 1 | FLOAT
1158 | 23. Harmonic I L1 | 1 | FLOAT
1160 | 25. Harmonic I L1 | 1 | FLOAT
1162 | 1. Harmonic I L2 | 1 | FLOAT
1164 | 3. Harmonic I L2 | 1 | FLOAT
1166 | 5. Harmonic I L2 | 1 | FLOAT
1168 | 7. Harmonic I L2 | 1 | FLOAT
1170 | 9. Harmonic I L2 | 1 | FLOAT
1172 | 11. Harmonic I L2 | 1 | FLOAT
1174 | 13. Harmonic I L2 | 1 | FLOAT
1176 | 15. Harmonic I L2 | 1 | FLOAT
1178 | 17. Harmonic I L2 | 1 | FLOAT
1180 | 19. Harmonic I L2 | 1 | FLOAT
1182 | 21. Harmonic I L2 | 1 | FLOAT
1184 | 23. Harmonic I L2 | 1 | FLOAT
1186 | 25. Harmonic I L2 | 1 | FLOAT
1188 | 1. Harmonic I L3 | 1 | FLOAT
1190 | 3. Harmonic I L3 | 1 | FLOAT
1192 | 5. Harmonic I L3 | 1 | FLOAT
1194 | 7. Harmonic I L3 | 1 | FLOAT
1196 | 9. Harmonic I L3 | 1 | FLOAT
1198 | 11. Harmonic I L3 | 1 | FLOAT
1200 | 13. Harmonic I L3 | 1 | FLOAT
1202 | 15. Harmonic I L3 | 1 | FLOAT
1204 | 17. Harmonic I L3 | 1 | FLOAT
1206 | 19. Harmonic I L3 | 1 | FLOAT
1208 | 21. Harmonic I L3 | 1 | FLOAT
1210 | 23. Harmonic I L3 | 1 | FLOAT
1212 | 25. Harmonic I L3 | 1 | FLOAT
1214 | THD U L1 | 1 | FLOAT
1216 | THD U L2 | 1 | FLOAT
1218 | THD U L3 | 1 | FLOAT
1220 | THD I L1 | 1 | FLOAT
1222 | THD I L2 | 1 | FLOAT
1224 | THD I L3 | 1 | FLOAT
1226 | Frequency | 1 | FLOAT
1228 | Zero sequence U | 1 | FLOAT
1230 | Postive sequence U | 1 | FLOAT
1232 | Negative sequence U | 1 | FLOAT
1234 | Zero sequence I | 1 | FLOAT
1236 | Postive sequence I | 1 | FLOAT
1238 | Negative sequence I | 1 | FLOAT
1240 | Distortion power L1 | 1 | FLOAT
1242 | Distortion power L2 | 1 | FLOAT
1244 | Distortion power L3 | 1 | FLOAT
1246 | Distortion power Sum | 1 | FLOAT
1248 | Rotation field | 1 | FLOAT |  | +1= right rotary field 0= no rotary field -1= left rotary field
1250 | Real part of the fundamental oscillation UL1 | 1 | FLOAT
1252 | Imaginary part of the fund. oscillation UL1 | 1 | FLOAT
1254 | Real part of the fund. oscillation UL2 | 1 | FLOAT
1256 | Imaginary part of the fund. oscillation UL2 | 1 | FLOAT
1258 | Real part of the fund. oscillation UL3 | 1 | FLOAT
1260 | Imaginary part of the fund. oscillation UL3 | 1 | FLOAT
1262 | Real part of the fund. oscillation IL1 | 1 | FLOAT
1264 | Imaginary part of the fund. oscillation IL1 | 1 | FLOAT
1266 | Real part of the fund. oscillation IL2 | 1 | FLOAT
1268 | Imaginary part of the fund. oscillation IL2 | 1 | FLOAT
1270 | Real part of the fund. oscillation IL3 | 1 | FLOAT
1272 | Imaginary part of the fund. oscillation IL3 | 1 | FLOAT
2000 | Mean value U L1 | 1 | FLOAT
2002 | Mean value U L2 | 1 | FLOAT
2004 | Mean value U L3 | 1 | FLOAT
2006 | Mean value U L1-L2 | 1 | FLOAT
2008 | Mean value U L2-L3 | 1 | FLOAT
2010 | Mean value U L3-L1 | 1 | FLOAT
2012 | Mean value I L1 | 1 | FLOAT
2014 | Mean value I L2 | 1 | FLOAT
2016 | Mean value I L3 | 1 | FLOAT
2018 | Mean value I Sum | 1 | FLOAT
2020 | Mean value P L1 | 1 | FLOAT
2022 | Mean value P L2 | 1 | FLOAT
2024 | Mean value P L3 | 1 | FLOAT
2026 | Mean value P Sum | 1 | FLOAT
2028 | Mean value Q L1 | 1 | FLOAT
2030 | Mean value Q L2 | 1 | FLOAT
2032 | Mean value Q L3 | 1 | FLOAT
2034 | Mean value Q Sum | 1 | FLOAT
2036 | Mean value S L1 | 1 | FLOAT
2038 | Mean value S L2 | 1 | FLOAT
2040 | Mean value S L3 | 1 | FLOAT
2042 | Mean value S Sum | 1 | FLOAT
2044 | Mean value CosPhi L1 | 1 | FLOAT
2046 | Mean value CosPhi L2 | 1 | FLOAT
2048 | Mean value CosPhi L3 | 1 | FLOAT
2050 | Mean value CosPhi Sum | 1 | FLOAT
2052 | Mean value real power, fundamental osc. L1 | 1 | FLOAT
2054 | Mean value real power, fundamental osc. L2 | 1 | FLOAT
2056 | Mean value real power, fund. osz. L3 | 1 | FLOAT
2058 | Mean value 1. Harmonic U L1 | 1 | FLOAT
2060 | Mean value 3. Harmonic U L1 | 1 | FLOAT
2062 | Mean value 5. Harmonic U L1 | 1 | FLOAT
2064 | Mean value 7. Harmonic U L1 | 1 | FLOAT
2066 | Mean value 9. Harmonic U L1 | 1 | FLOAT
2068 | Mean value 11. Harmonic U L1 | 1 | FLOAT
2070 | Mean value 13. Harmonic U L1 | 1 | FLOAT
2072 | Mean value 15. Harmonic U L1 | 1 | FLOAT
2074 | Mean value 17. Harmonic U L1 | 1 | FLOAT
2076 | Mean value 19. Harmonic U L1 | 1 | FLOAT
2078 | Mean value 21. Harmonic U L1 | 1 | FLOAT
2080 | Mean value 23. Harmonic U L1 | 1 | FLOAT
2082 | Mean value 25. Harmonic U L1 | 1 | FLOAT
2084 | Mean value 1. Harmonic U L2 | 1 | FLOAT
2086 | Mean value 3. Harmonic U L2 | 1 | FLOAT
2088 | Mean value 5. Harmonic U L2 | 1 | FLOAT
2090 | Mean value 7. Harmonic U L2 | 1 | FLOAT
2092 | Mean value 9. Harmonic U L2 | 1 | FLOAT
2094 | Mean value 11. Harmonic U L2 | 1 | FLOAT
2096 | Mean value 13. Harmonic U L2 | 1 | FLOAT
2098 | Mean value 15. Harmonic U L2 | 1 | FLOAT
2100 | Mean value 17. Harmonic U L2 | 1 | FLOAT
2102 | Mean value 19. Harmonic U L2 | 1 | FLOAT
2104 | Mean value 21. Harmonic U L2 | 1 | FLOAT
2106 | Mean value 23. Harmonic U L2 | 1 | FLOAT
2108 | Mean value 25. Harmonic U L2 | 1 | FLOAT
2110 | Mean value 1. Harmonic U L3 | 1 | FLOAT
2112 | Mean value 3. Harmonic U L3 | 1 | FLOAT
2114 | Mean value 5. Harmonic U L3 | 1 | FLOAT
2116 | Mean value 7. Harmonic U L3 | 1 | FLOAT
2118 | Mean value 9. Harmonic U L3 | 1 | FLOAT
2120 | Mean value 11. Harmonic U L3 | 1 | FLOAT
2122 | Mean value 13. Harmonic U L3 | 1 | FLOAT
2124 | Mean value 15. Harmonic U L3 | 1 | FLOAT
2126 | Mean value 17. Harmonic U L3 | 1 | FLOAT
2128 | Mean value 19. Harmonic U L3 | 1 | FLOAT
2130 | Mean value 21. Harmonic U L3 | 1 | FLOAT
2132 | Mean value 23. Harmonic U L3 | 1 | FLOAT
2134 | Mean value 25. Harmonic U L3 | 1 | FLOAT
2136 | Mean value 1. Harmonic I L1 | 1 | FLOAT
2138 | Mean value 3. Harmonic I L1 | 1 | FLOAT
2140 | Mean value 5. Harmonic I L1 | 1 | FLOAT
2142 | Mean value 7. Harmonic I L1 | 1 | FLOAT
2144 | Mean value 9. Harmonic I L1 | 1 | FLOAT
2146 | Mean value 11. Harmonic I L1 | 1 | FLOAT
2148 | Mean value 13. Harmonic I L1 | 1 | FLOAT
2150 | Mean value 15. Harmonic I L1 | 1 | FLOAT
2152 | Mean value 17. Harmonic I L1 | 1 | FLOAT
2154 | Mean value 19. Harmonic I L1 | 1 | FLOAT
2156 | Mean value 21. Harmonic I L1 | 1 | FLOAT
2158 | Mean value 23. Harmonic I L1 | 1 | FLOAT
2160 | Mean value 25. Harmonic I L1 | 1 | FLOAT
2162 | Mean value 1. Harmonic I L2 | 1 | FLOAT
2164 | Mean value 3. Harmonic I L2 | 1 | FLOAT
2166 | Mean value 5. Harmonic I L2 | 1 | FLOAT
2168 | Mean value 7. Harmonic I L2 | 1 | FLOAT
2170 | Mean value 9. Harmonic I L2 | 1 | FLOAT
2172 | Mean value 11. Harmonic I L2 | 1 | FLOAT
2174 | Mean value 13. Harmonic I L2 | 1 | FLOAT
2176 | Mean value 15. Harmonic I L2 | 1 | FLOAT
2178 | Mean value 17. Harmonic I L2 | 1 | FLOAT
2180 | Mean value 19. Harmonic I L2 | 1 | FLOAT
2182 | Mean value 21. Harmonic I L2 | 1 | FLOAT
2184 | Mean value 23. Harmonic I L2 | 1 | FLOAT
2186 | Mean value 25. Harmonic I L2 | 1 | FLOAT
2188 | Mean value 1. Harmonic I L3 | 1 | FLOAT
2190 | Mean value 3. Harmonic I L3 | 1 | FLOAT
2192 | Mean value 5. Harmonic I L3 | 1 | FLOAT
2194 | Mean value 7. Harmonic I L3 | 1 | FLOAT
2196 | Mean value 9. Harmonic I L3 | 1 | FLOAT
2198 | Mean value 11. Harmonic I L3 | 1 | FLOAT
2200 | Mean value 13. Harmonic I L3 | 1 | FLOAT
2202 | Mean value 15. Harmonic I L3 | 1 | FLOAT
2204 | Mean value 17. Harmonic I L3 | 1 | FLOAT
2206 | Mean value 19. Harmonic I L3 | 1 | FLOAT
2208 | Mean value 21. Harmonic I L3 | 1 | FLOAT
2210 | Mean value 23. Harmonic I L3 | 1 | FLOAT
2212 | Mean value 25. Harmonic I L3 | 1 | FLOAT
2214 | Mean value THD U L1 | 1 | FLOAT
2216 | Mean value THD U L2 | 1 | FLOAT
2218 | Mean value THD U L3 | 1 | FLOAT
2220 | Mean value THD I L1 | 1 | FLOAT
2222 | Mean value THD I L2 | 1 | FLOAT
2224 | Mean value THD I L3 | 1 | FLOAT
2226 | Mean value Frequency | 1 | FLOAT
2228 | Mean value Zero sequence U | 1 | FLOAT
2230 | Mean value postive sequence U | 1 | FLOAT
2232 | Mean value negative sequence U | 1 | FLOAT
2234 | Mean value Zero sequence I | 1 | FLOAT
2236 | Mean value postive sequence I | 1 | FLOAT
2238 | Mean value negative sequence I | 1 | FLOAT
2240 | Mean value distortion power L1 | 1 | FLOAT
2242 | Mean value distortion power L2 | 1 | FLOAT
2244 | Mean value distortion power L3 | 1 | FLOAT
2246 | Mean value distortion power Sum | 1 | FLOAT
3000 | Max. value. U L1 | 1 | FLOAT
3002 | Max. value. U L2 | 1 | FLOAT
3004 | Max. value. U L3 | 1 | FLOAT
3006 | Max. value. U L1-L2 | 1 | FLOAT
3008 | Max. value. U L2-L3 | 1 | FLOAT
3010 | Max. value. U L3-L1 | 1 | FLOAT
3012 | Max. value. I L1 | 1 | FLOAT
3014 | Max. value. I L2 | 1 | FLOAT
3016 | Max. value. I L3 | 1 | FLOAT
3018 | Max. value. I Sum (convert. Current in N) | 1 | FLOAT
3020 | Max. value. P L1 | 1 | FLOAT
3022 | Max. value. P L2 | 1 | FLOAT
3024 | Max. value. P L3 | 1 | FLOAT
3026 | Max. value. P Sum | 1 | FLOAT
3028 | Max. value. Q L1 | 1 | FLOAT
3030 | Max. value. Q L2 | 1 | FLOAT
3032 | Max. value. Q L3 | 1 | FLOAT
3034 | Max. value. Q Sum | 1 | FLOAT
3036 | Max. value. S L1 | 1 | FLOAT
3038 | Max. value. S L2 | 1 | FLOAT
3040 | Max. value. S L3 | 1 | FLOAT
3042 | Max. value. S Sum | 1 | FLOAT
3044 | Max. value. CosPhi L1 | 1 | FLOAT
3046 | Max. value. CosPhi L2 | 1 | FLOAT
3048 | Max. value. CosPhi L3 | 1 | FLOAT
3050 | Max. value. CosPhi Sum | 1 | FLOAT
3052 | Max. value. real power, fundamental osc. L1 | 1 | FLOAT
3054 | Max. value. real power, fundamental osc. L2 | 1 | FLOAT
3056 | Max. value. real power, fundamental osc. L3 | 1 | FLOAT
3058 | Max. value. 1. Harmonic U L1 | 1 | FLOAT
3060 | Max. value. 3. Harmonic U L1 | 1 | FLOAT
3062 | Max. value. 5. Harmonic U L1 | 1 | FLOAT
3064 | Max. value. 7. Harmonic U L1 | 1 | FLOAT
3066 | Max. value. 9. Harmonic U L1 | 1 | FLOAT
3068 | Max. value. 11. Harmonic U L1 | 1 | FLOAT
3070 | Max. value. 13. Harmonic U L1 | 1 | FLOAT
3072 | Max. value. 15. Harmonic U L1 | 1 | FLOAT
3074 | Max. value. 17. Harmonic U L1 | 1 | FLOAT
3076 | Max. value. 19. Harmonic U L1 | 1 | FLOAT
3078 | Max. value. 21. Harmonic U L1 | 1 | FLOAT
3080 | Max. value. 23. Harmonic U L1 | 1 | FLOAT
3082 | Max. value. 25. Harmonic U L1 | 1 | FLOAT
3084 | Max. value. 1. Harmonic U L2 | 1 | FLOAT
3086 | Max. value. 3. Harmonic U L2 | 1 | FLOAT
3088 | Max. value. 5. Harmonic U L2 | 1 | FLOAT
3090 | Max. value. 7. Harmonic U L2 | 1 | FLOAT
3092 | Max. value. 9. Harmonic U L2 | 1 | FLOAT
3094 | Max. value. 11. Harmonic U L2 | 1 | FLOAT
3096 | Max. value. 13. Harmonic U L2 | 1 | FLOAT
3098 | Max. value. 15. Harmonic U L2 | 1 | FLOAT
3100 | Max. value. 17. Harmonic U L2 | 1 | FLOAT
3102 | Max. value. 19. Harmonic U L2 | 1 | FLOAT
2104 | Max. value. 21. Harmonic U L2 | 1 | FLOAT
3106 | Max. value. 23. Harmonic U L2 | 1 | FLOAT
3108 | Max. value. 25. Harmonic U L2 | 1 | FLOAT
3110 | Max. value. 1. Harmonic U L3 | 1 | FLOAT
3112 | Max. value. 3. Harmonic U L3 | 1 | FLOAT
3114 | Max. value. 5. Harmonic U L3 | 1 | FLOAT
3116 | Max. value. 7. Harmonic U L3 | 1 | FLOAT
3118 | Max. value. 9. Harmonic U L3 | 1 | FLOAT
3120 | Max. value. 11. Harmonic U L3 | 1 | FLOAT
3122 | Max. value. 13. Harmonic U L3 | 1 | FLOAT
3124 | Max. value. 15. Harmonic U L3 | 1 | FLOAT
3126 | Max. value. 17. Harmonic U L3 | 1 | FLOAT
3128 | Max. value. 19. Harmonic U L3 | 1 | FLOAT
3130 | Max. value. 21. Harmonic U L3 | 1 | FLOAT
3132 | Max. value. 23. Harmonic U L3 | 1 | FLOAT
3134 | Max. value. 25. Harmonic U L3 | 1 | FLOAT
3136 | Max. value. 1. Harmonic I L1 | 1 | FLOAT
3138 | Max. value. 3. Harmonic I L1 | 1 | FLOAT
3140 | Max. value. 5. Harmonic I L1 | 1 | FLOAT
3142 | Max. value. 7. Harmonic I L1 | 1 | FLOAT
3144 | Max. value. 9. Harmonic I L1 | 1 | FLOAT
3146 | Max. value. 11. Harmonic I L1 | 1 | FLOAT
3148 | Max. value. 13. Harmonic I L1 | 1 | FLOAT
3150 | Max. value. 15. Harmonic I L1 | 1 | FLOAT
3152 | Max. value. 17. Harmonic I L1 | 1 | FLOAT
3154 | Max. value. 19. Harmonic I L1 | 1 | FLOAT
3156 | Max. value. 21. Harmonic I L1 | 1 | FLOAT
3158 | Max. value. 23. Harmonic I L1 | 1 | FLOAT
3160 | Max. value. 25. Harmonic I L1 | 1 | FLOAT
3162 | Max. value. 1. Harmonic I L2 | 1 | FLOAT
3164 | Max. value. 3. Harmonic I L2 | 1 | FLOAT
3166 | Max. value. 5. Harmonic I L2 | 1 | FLOAT
3168 | Max. value. 7. Harmonic I L2 | 1 | FLOAT
3170 | Max. value. 9. Harmonic I L2 | 1 | FLOAT
3172 | Max. value. 11. Harmonic I L2 | 1 | FLOAT
3174 | Max. value. 13. Harmonic I L2 | 1 | FLOAT
3176 | Max. value. 15. Harmonic I L2 | 1 | FLOAT
3178 | Max. value. 17. Harmonic I L2 | 1 | FLOAT
3180 | Max. value. 19. Harmonic I L2 | 1 | FLOAT
3182 | Max. value. 21. Harmonic I L2 | 1 | FLOAT
3184 | Max. value. 23. Harmonic I L2 | 1 | FLOAT
3186 | Max. value. 25. Harmonic I L2 | 1 | FLOAT
3188 | Max. value. 1. Harmonic I L3 | 1 | FLOAT
3190 | Max. value. 3. Harmonic I L3 | 1 | FLOAT
3192 | Max. value. 5. Harmonic I L3 | 1 | FLOAT
3194 | Max. value. 7. Harmonic I L3 | 1 | FLOAT
3196 | Max. value. 9. Harmonic I L3 | 1 | FLOAT
3198 | Max. value. 11. Harmonic I L3 | 1 | FLOAT
3200 | Max. value. 13. Harmonic I L3 | 1 | FLOAT
3202 | Max. value. 15. Harmonic I L3 | 1 | FLOAT
3204 | Max. value. 17. Harmonic I L3 | 1 | FLOAT
3206 | Max. value. 19. Harmonic I L3 | 1 | FLOAT
3208 | Max. value. 21. Harmonic I L3 | 1 | FLOAT
3210 | Max. value. 23. Harmonic I L3 | 1 | FLOAT
3212 | Max. value. 25. Harmonic I L3 | 1 | FLOAT
3214 | Max. value. THD U L1 | 1 | FLOAT
3216 | Max. value. THD U L2 | 1 | FLOAT
3218 | Max. value. THD U L3 | 1 | FLOAT
3220 | Max. value. THD I L1 | 1 | FLOAT
3222 | Max. value. THD I L2 | 1 | FLOAT
3224 | Max. value. THD I L3 | 1 | FLOAT
3226 | Max. value. Frequency | 1 | FLOAT
3228 | Max. value U Zero sequence | 1 | FLOAT
3230 | Max. value U postive sequence | 1 | FLOAT
3232 | Max. value U negative sequence | 1 | FLOAT
3234 | Max. value I Zero sequence | 1 | FLOAT
3236 | Max. value I postive sequence | 1 | FLOAT
3238 | Max. value I negative sequence | 1 | FLOAT
3240 | Max. value Distortion power L1 | 1 | FLOAT
3242 | Max. value Distortion power L2 | 1 | FLOAT
3244 | Max. value Distortion power L3 | 1 | FLOAT
3246 | Max. value Distortion power Sum | 1 | FLOAT
3248 | Max. value des Mean value I L1 | 1 | FLOAT
3250 | Max. value des Mean value I L2 | 1 | FLOAT
3252 | Max. value des Mean value I L3 | 1 | FLOAT
3254 | Max. value des Mean value I Sum | 1 | FLOAT
3256 | Max. of Mean value P L1 | 1 | FLOAT
3258 | Max. of Mean value P L2 | 1 | FLOAT
3260 | Max. of Mean value P L3 | 1 | FLOAT
3262 | Max. of Mean value P Sum. | 1 | FLOAT
4000 | Min. value U L1 | 1 | FLOAT
4002 | Min. value U L2 | 1 | FLOAT
4004 | Min. value U L3 | 1 | FLOAT
4006 | Min. value U L1-L2 | 1 | FLOAT
4008 | Min. value U L2-L3 | 1 | FLOAT
4010 | Min. value U L3-L1 | 1 | FLOAT
4012 | Min. value CosPhi L1 | 1 | FLOAT
4014 | Min. value CosPhi L1 | 1 | FLOAT
4016 | Min. value CosPhi L2 | 1 | FLOAT
4018 | Min. value CosPhi L3 | 1 | FLOAT
4020 | Min. value 1. Harmonic U L1 | 1 | FLOAT
4022 | Min. value 3. Harmonic U L1 | 1 | FLOAT
4024 | Min. value 5. Harmonic U L1 | 1 | FLOAT
4026 | Min. value 7. Harmonic U L1 | 1 | FLOAT
4028 | Min. value 9. Harmonic U L1 | 1 | FLOAT
4030 | Min. value 11. Harmonic U L1 | 1 | FLOAT
4032 | Min. value 13. Harmonic U L1 | 1 | FLOAT
4034 | Min. value 15. Harmonic U L1 | 1 | FLOAT
4036 | Min. value 17. Harmonic U L1 | 1 | FLOAT
4038 | Min. value 19. Harmonic U L1 | 1 | FLOAT
4040 | Min. value 21. Harmonic U L1 | 1 | FLOAT
4042 | Min. value 23. Harmonic U L1 | 1 | FLOAT
4044 | Min. value 25. Harmonic U L1 | 1 | FLOAT
4046 | Min. value 1. Harmonic U L2 | 1 | FLOAT
4048 | Min. value 3. Harmonic U L2 | 1 | FLOAT
4050 | Min. value 5. Harmonic U L2 | 1 | FLOAT
4052 | Min. value 7. Harmonic U L2 | 1 | FLOAT
4054 | Min. value 9. Harmonic U L2 | 1 | FLOAT
4056 | Min. value 11. Harmonic U L2 | 1 | FLOAT
4058 | Min. value 13. Harmonic U L2 | 1 | FLOAT
4060 | Min. value 15. Harmonic U L2 | 1 | FLOAT
4062 | Min. value 17. Harmonic U L2 | 1 | FLOAT
4064 | Min. value 19. Harmonic U L2 | 1 | FLOAT
4066 | Min. value 21. Harmonic U L2 | 1 | FLOAT
4068 | Min. value 23. Harmonic U L2 | 1 | FLOAT
4070 | Min. value 25. Harmonic U L2 | 1 | FLOAT
4072 | Min. value 1. Harmonic U L3 | 1 | FLOAT
4074 | Min. value 3. Harmonic U L3 | 1 | FLOAT
4076 | Min. value 5. Harmonic U L3 | 1 | FLOAT
4078 | Min. value 7. Harmonic U L3 | 1 | FLOAT
4080 | Min. value 9. Harmonic U L3 | 1 | FLOAT
4082 | Min. value 11. Harmonic U L3 | 1 | FLOAT
4084 | Min. value 13. Harmonic U L3 | 1 | FLOAT
4086 | Min. value 15. Harmonic U L3 | 1 | FLOAT
4088 | Min. value 17. Harmonic U L3 | 1 | FLOAT
4090 | Min. value 19. Harmonic U L3 | 1 | FLOAT
4092 | Min. value 21. Harmonic U L3 | 1 | FLOAT
4094 | Min. value 23. Harmonic U L3 | 1 | FLOAT
4096 | Min. value 25. Harmonic U L3 | 1 | FLOAT
4098 | Min. value THD U L1 | 1 | FLOAT
4100 | Min. value THD U L2 | 1 | FLOAT
4102 | Min. value THD U L3 | 1 | FLOAT
4104 | Min. value Frequency | 1 | FLOAT
4106 | Min. value U Zero sequence | 1 | FLOAT
4108 | Min. value U postive sequence | 1 | FLOAT
4110 | Min. value U negative sequence | 1 | FLOAT
5000 | Real energy L1, Consumption | 1 | FLOAT
5002 | Real energy L2, Consumption | 1 | FLOAT
5004 | Real energy L3, Consumption | 1 | FLOAT
5006 | Real energy Sum, Consumption | 1 | FLOAT
5008 | Real energy L1, Consumption, HT | 1 | FLOAT
5010 | Real energy L2, Consumption, HT | 1 | FLOAT
5012 | Real energy L3, Consumption, HT | 1 | FLOAT
5014 | Real energy Sum, Consumption, HT | 1 | FLOAT
5016 | Real energy L1, Consumption, NT | 1 | FLOAT
5018 | Real energy L2, Consumption, NT | 1 | FLOAT
5020 | Real energy L3, Consumption, NT | 1 | FLOAT
5022 | Real energy Sum, Consumption, NT | 1 | FLOAT
5024 | Apparent energy L1 | 1 | FLOAT
5026 | Apparent energy L2 | 1 | FLOAT
5028 | Apparent energy L3 | 1 | FLOAT
5030 | Apparent energy Sum | 1 | FLOAT
5032 | Apparent energy L1, HT | 1 | FLOAT
5034 | Apparent energy L2, HT | 1 | FLOAT
5036 | Apparent energy L3, HT | 1 | FLOAT
5038 | Apparent energy Sum, HT | 1 | FLOAT
5040 | Apparent energy L1, NT | 1 | FLOAT
5042 | Apparent energy L2, NT | 1 | FLOAT
5044 | Apparent energy L3, NT | 1 | FLOAT
5046 | Apparent energy Sum, NT | 1 | FLOAT
5048 | Reactive energy L1, ind. | 1 | FLOAT
5050 | Reactive energy L2, ind. | 1 | FLOAT
5052 | Reactive energy L3, ind. | 1 | FLOAT
5054 | Reactive energy Sum, ind. | 1 | FLOAT
5056 | Reactive energy L1, ind. HT | 1 | FLOAT
5058 | Reactive energy L2, ind. HT | 1 | FLOAT
5060 | Reactive energy L3, ind. HT | 1 | FLOAT
5062 | Reactive energy Sum, ind. HT | 1 | FLOAT
5064 | Reactive energy L1, ind. NT | 1 | FLOAT
5066 | Reactive energy L2, ind. NT | 1 | FLOAT
5068 | Reactive energy L3, ind. NT | 1 | FLOAT
5070 | Reactive energy Sum, ind. NT | 1 | FLOAT
5072 | Real energy L1, Supply | 1 | FLOAT
5074 | Real energy L2, Supply | 1 | FLOAT
5076 | Real energy L3, Supply | 1 | FLOAT
5078 | Real energy Sum, Supply | 1 | FLOAT
5080 | Reactive energy L1, capacitive | 1 | FLOAT
5082 | Reactive energy L2, capacitive | 1 | FLOAT
5084 | Reactive energy L3, capacitive | 1 | FLOAT
5086 | Reactive energy Sum, capacitive | 1 | FLOAT
5088 | Real energy Sum, without return travel block | 1 | FLOAT
5090 | Reactive energy Sum, without ret. tra. block | 1 | FLOAT
6000 | Real energy L1, Consumption | 1 | DOUBLE
6004 | Real energy L2, Consumption | 1 | DOUBLE
6008 | Real energy L3, Consumption | 1 | DOUBLE
6012 | Real energy Sum, Consumption | 1 | DOUBLE
6016 | Real energy L1, Consumption, HT | 1 | DOUBLE
6020 | Real energy L2, Consumption, HT | 1 | DOUBLE
6024 | Real energy L3, Consumption, HT | 1 | DOUBLE
6028 | Real energy Sum, Consumption, HT | 1 | DOUBLE
6032 | Real energy L1, Consumption, NT | 1 | DOUBLE
6036 | Real energy L2, Consumption, NT | 1 | DOUBLE
6040 | Real energy L3, Consumption, NT | 1 | DOUBLE
6044 | Real energy Sum, Consumption, NT | 1 | DOUBLE
6048 | Apparent energy L1 | 1 | DOUBLE
6052 | Apparent energy L2 | 1 | DOUBLE
6056 | Apparent energy L3 | 1 | DOUBLE
6060 | Apparent energy Sum | 1 | DOUBLE
6064 | Apparent energy L1, HT | 1 | DOUBLE
6068 | Apparent energy L2, HT | 1 | DOUBLE
6072 | Apparent energy L3, HT | 1 | DOUBLE
6076 | Apparent energy Sum, HT | 1 | DOUBLE
6080 | Apparent energy L1, NT | 1 | DOUBLE
6084 | Apparent energy L2, NT | 1 | DOUBLE
6088 | Apparent energy L3, NT | 1 | DOUBLE
6092 | Apparent energy Sum, NT | 1 | DOUBLE
6096 | Reactive energy L1, ind. | 1 | DOUBLE
6100 | Reactive energy L2, ind. | 1 | DOUBLE
6104 | Reactive energy L3, ind. | 1 | DOUBLE
6108 | Reactive energy Sum, ind. | 1 | DOUBLE
6112 | Reactive energy L1, ind. HT | 1 | DOUBLE
6116 | Reactive energy L2, ind. HT | 1 | DOUBLE
6120 | Reactive energy L3, ind. HT | 1 | DOUBLE
6124 | Reactive energy Sum, ind. HT | 1 | DOUBLE
6128 | Reactive energy L1, ind. NT | 1 | DOUBLE
6132 | Reactive energy L2, ind. NT | 1 | DOUBLE
6136 | Reactive energy L3, ind. NT | 1 | DOUBLE
6140 | Reactive energy Sum, ind. NT | 1 | DOUBLE
6144 | Real energy L1, Supply | 1 | DOUBLE
6148 | Real energy L2, Supply | 1 | DOUBLE
6152 | Real energy L3, Supply | 1 | DOUBLE
6156 | Real energy Sum, Supply | 1 | DOUBLE
6160 | Reactive energy L1, capacitive | 1 | DOUBLE
6164 | Reactive energy L2, capacitive | 1 | DOUBLE
6168 | Reactive energy L3, capacitive | 1 | DOUBLE
6172 | Reactive energy Sum, capacitive | 1 | DOUBLE
6176 | Real energy Sum, without return travel block | 1 | DOUBLE
6180 | Reactive energy Sum, without ret. tra. block | 1 | DOUBLE
11000 | U L1 | 10 | SHORT |  | VT
11001 | U L2 | 10 | SHORT |  | VT
11002 | U L3 | 10 | SHORT |  | VT
11003 | U L1-L2 | 10 | SHORT |  | VT
11004 | U L2-L3 | 10 | SHORT |  | VT
11005 | U L3-L1 | 10 | SHORT |  | VT
11006 | I L1 | 1000 | SHORT |  | CT
11007 | I L2 | 1000 | SHORT |  | CT
11008 | I L3 | 1000 | SHORT |  | CT
11009 | I Sum | 1000 | SHORT |  | CT
11010 | P L1 | 10 | SHORT |  | CT VT
11011 | P L2 | 10 | SHORT |  | CT VT
11012 | P L3 | 10 | SHORT |  | CT VT
11013 | P Sum | 1 | SHORT |  | CT VT
11014 | Q L1 | 10 | SHORT |  | CT VT
11015 | Q L2 | 10 | SHORT |  | CT VT
11016 | Q L3 | 10 | SHORT |  | CT VT
11017 | Q Sum | 1 | SHORT |  | CT VT
11018 | S L1 | 10 | SHORT |  | CT VT
11019 | S L2 | 10 | SHORT |  | CT VT
11020 | S L3 | 10 | SHORT |  | CT VT
11021 | S Sum | 1 | SHORT |  | CT VT
11022 | CosPhi L1 | 1 | SHORT
11023 | CosPhi L2 | 1 | SHORT
11024 | CosPhi L3 | 1 | SHORT
11025 | CosPhi Sum | 1 | SHORT
11026 | Real power, fundamental oscillation, L1 | 10 | SHORT |  | CT VT
11027 | Real power, fundamental oscillation, L2 | 10 | SHORT |  | CT VT
11028 | Real power, fundamental oscillation, L3 | 10 | SHORT |  | CT VT
11029 | 1. Harmonic U L1 | 10 | SHORT |  | VT
11030 | 3. Harmonic U L1 | 10 | SHORT |  | VT
11031 | 5. Harmonic U L1 | 10 | SHORT |  | VT
11032 | 7. Harmonic U L1 | 10 | SHORT |  | VT
11033 | 9. Harmonic U L1 | 10 | SHORT |  | VT
11034 | 11. Harmonic U L1 | 10 | SHORT |  | VT
11035 | 13. Harmonic U L1 | 10 | SHORT |  | VT
11036 | 15. Harmonic U L1 | 10 | SHORT |  | VT
11037 | 17. Harmonic U L1 | 10 | SHORT |  | VT
11038 | 19. Harmonic U L1 | 10 | SHORT |  | VT
11039 | 21. Harmonic U L1 | 10 | SHORT |  | VT
11040 | 23. Harmonic U L1 | 10 | SHORT |  | VT
11041 | 25. Harmonic U L1 | 10 | SHORT |  | VT
11042 | 1. Harmonic U L2 | 10 | SHORT |  | VT
11043 | 3. Harmonic U L2 | 10 | SHORT |  | VT
11044 | 5. Harmonic U L2 | 10 | SHORT |  | VT
11045 | 7. Harmonic U L2 | 10 | SHORT |  | VT
11046 | 9. Harmonic U L2 | 10 | SHORT |  | VT
11047 | 11. Harmonic U L2 | 10 | SHORT |  | VT
11048 | 13. Harmonic U L2 | 10 | SHORT |  | VT
11049 | 15. Harmonic U L2 | 10 | SHORT |  | VT
11050 | 17. Harmonic U L2 | 10 | SHORT |  | VT
11051 | 19. Harmonic U L2 | 10 | SHORT |  | VT
11052 | 21. Harmonic U L2 | 10 | SHORT |  | VT
11053 | 23. Harmonic U L2 | 10 | SHORT |  | VT
11054 | 25. Harmonic U L2 | 10 | SHORT |  | VT
11055 | 1. Harmonic U L3 | 10 | SHORT |  | VT
11056 | 3. Harmonic U L3 | 10 | SHORT |  | VT
11057 | 5. Harmonic U L3 | 10 | SHORT |  | VT
11058 | 7. Harmonic U L3 | 10 | SHORT |  | VT
11059 | 9. Harmonic U L3 | 10 | SHORT |  | VT
11060 | 11. Harmonic U L3 | 10 | SHORT |  | VT
11061 | 13. Harmonic U L3 | 10 | SHORT |  | VT
11062 | 15. Harmonic U L3 | 10 | SHORT |  | VT
11063 | 17. Harmonic U L3 | 10 | SHORT |  | VT
11064 | 19. Harmonic U L3 | 10 | SHORT |  | VT
11065 | 21. Harmonic U L3 | 10 | SHORT |  | VT
11066 | 23. Harmonic U L3 | 10 | SHORT |  | VT
11067 | 25. Harmonic U L3 | 10 | SHORT |  | VT
11068 | 1. Harmonic I L1 | 1000 | SHORT |  | CT
11069 | 3. Harmonic I L1 | 1000 | SHORT |  | CT
11070 | 5. Harmonic I L1 | 1000 | SHORT |  | CT
11071 | 7. Harmonic I L1 | 1000 | SHORT |  | CT
11072 | 9. Harmonic I L1 | 1000 | SHORT |  | CT
11073 | 11. Harmonic I L1 | 1000 | SHORT |  | CT
11074 | 13. Harmonic I L1 | 1000 | SHORT |  | CT
11075 | 15. Harmonic I L1 | 1000 | SHORT |  | CT
11076 | 17. Harmonic I L1 | 1000 | SHORT |  | CT
11077 | 19. Harmonic I L1 | 1000 | SHORT |  | CT
11078 | 21. Harmonic I L1 | 1000 | SHORT |  | CT
11079 | 23. Harmonic I L1 | 1000 | SHORT |  | CT
11080 | 25. Harmonic I L1 | 1000 | SHORT |  | CT
11081 | 1. Harmonic I L2 | 1000 | SHORT |  | CT
11082 | 3. Harmonic I L2 | 1000 | SHORT |  | CT
11083 | 5. Harmonic I L2 | 1000 | SHORT |  | CT
11084 | 7. Harmonic I L2 | 1000 | SHORT |  | CT
11085 | 9. Harmonic I L2 | 1000 | SHORT |  | CT
11086 | 11. Harmonic I L2 | 1000 | SHORT |  | CT
11087 | 13. Harmonic I L2 | 1000 | SHORT |  | CT
11088 | 15. Harmonic I L2 | 1000 | SHORT |  | CT
11089 | 17. Harmonic I L2 | 1000 | SHORT |  | CT
11090 | 19. Harmonic I L2 | 1000 | SHORT |  | CT
11091 | 22. Harmonic I L2 | 1000 | SHORT |  | CT
11092 | 23. Harmonic I L2 | 1000 | SHORT |  | CT
11093 | 25. Harmonic I L2 | 1000 | SHORT |  | CT
11094 | 1. Harmonic I L3 | 1000 | SHORT |  | CT
11095 | 3. Harmonic I L3 | 1000 | SHORT |  | CT
11096 | 5. Harmonic I L3 | 1000 | SHORT |  | CT
11097 | 7. Harmonic I L3 | 1000 | SHORT |  | CT
11098 | 9. Harmonic I L3 | 1000 | SHORT |  | CT
11099 | 11. Harmonic I L3 | 1000 | SHORT |  | CT
11100 | 13. Harmonic I L3 | 1000 | SHORT |  | CT
11101 | 15. Harmonic I L3 | 1000 | SHORT |  | CT
11102 | 17. Harmonic I L3 | 1000 | SHORT |  | CT
11103 | 19. Harmonic I L3 | 1000 | SHORT |  | CT
11108 | 21. Harmonic I L3 | 1000 | SHORT |  | CT
11109 | 23. Harmonic I L3 | 1000 | SHORT |  | CT
11110 | 25. Harmonic I L3 | 1000 | SHORT |  | CT
11111 | THD U L1 | 100 | SHORT
11112 | THD U L2 | 100 | SHORT
11113 | THD U L3 | 100 | SHORT
11114 | THD I L1 | 100 | SHORT
11115 | THD I L2 | 100 | SHORT
11116 | THD I L3 | 100 | SHORT
11117 | Frequency | 100 | SHORT
11118 | Zero sequence U | 10 | SHORT |  | VT
11119 | Postive sequence U | 10 | SHORT |  | VT
11120 | Negative sequence U | 10 | SHORT |  | VT
11121 | Zero sequence I | 1000 | SHORT |  | CT
11122 | Postive sequence I | 1000 | SHORT |  | CT
11123 | Negative sequence I | 1000 | SHORT |  | CT
11124 | Distortion power L1 | 10 | SHORT |  | CT VT
11125 | Distortion power L2 | 10 | SHORT |  | CT VT
11126 | Distortion power L3 | 10 | SHORT |  | CT VT
11127 | Distortion power Sum | 1 | SHORT |  | CT VT
11128 | Rotation field | 1 | SHORT |  | +1= right rotary field 0= no rotary field -1= left rotary field
11130 | Comparator 1A Lead Time | 1 | LONG
11132 | Comparator 1B Lead Time | 1 | LONG
11134 | Comparator 1C Lead Time | 1 | LONG
11136 | Comparator 2A Lead Time | 1 | LONG
11138 | Comparator 2B Lead Time | 1 | LONG
11140 | Comparator 2C Lead Time | 1 | LONG
11142 | Operating hours counter | 1 | LONG
12000 | Mean value U L1 | 10 | SHORT |  | VT
12001 | Mean value U L2 | 10 | SHORT |  | VT
12002 | Mean value U L3 | 10 | SHORT |  | VT
12003 | Mean value U L1-L2 | 10 | SHORT |  | VT
12004 | Mean value U L2-L3 | 10 | SHORT |  | VT
12005 | Mean value U L3-L1 | 10 | SHORT |  | VT
12006 | Mean value I L1 | 1000 | SHORT |  | CT
12007 | Mean value I L2 | 1000 | SHORT |  | CT
12008 | Mean value I L3 | 1000 | SHORT |  | CT
12009 | Mean value I Sum | 1000 | SHORT |  | CT
12010 | Mean value P L1 | 10 | SHORT |  | CT VT
12011 | Mean value P L2 | 10 | SHORT |  | CT VT
12012 | Mean value P L3 | 10 | SHORT |  | CT VT
12013 | Mean value P Sum | 1 | SHORT |  | CT VT
12014 | Mean value Q L1 | 10 | SHORT |  | CT VT
12015 | Mean value Q L2 | 10 | SHORT |  | CT VT
12016 | Mean value Q L3 | 10 | SHORT |  | CT VT
12017 | Mean value Q Sum | 1 | SHORT |  | CT VT
12018 | Mean value S[0] | 10 | SHORT |  | CT VT
12019 | Mean value S[1] | 10 | SHORT |  | CT VT
12020 | Mean value S[2] | 10 | SHORT |  | CT VT
12021 | Mean value S[3] | 1 | SHORT |  | CT VT
12022 | Mean value Cosphi L1 | 1 | SHORT
12023 | Mean value Cosphi L2 | 1 | SHORT
12024 | Mean value Cosphi L3 | 1 | SHORT
12025 | Mean value Cosphi Sum | 1 | SHORT
12026 | Mean value P L1 | 10 | SHORT |  | CT VT
12027 | Mean value P L2 | 10 | SHORT |  | CT VT
12028 | Mean value P L3 | 10 | SHORT |  | CT VT
12029 | Mean value 1. Harmonic U L1 | 10 | SHORT |  | VT
12030 | Mean value 3. Harmonic U L1 | 10 | SHORT |  | VT
12031 | Mean value 5. Harmonic U L1 | 10 | SHORT |  | VT
12032 | Mean value 7. Harmonic U L1 | 10 | SHORT |  | VT
12033 | Mean value 9. Harmonic U L1 | 10 | SHORT |  | VT
12034 | Mean value 11. Harmonic U L1 | 10 | SHORT |  | VT
12035 | Mean value 13. Harmonic U L1 | 10 | SHORT |  | VT
12036 | Mean value 15. Harmonic U L1 | 10 | SHORT |  | VT
12037 | Mean value 17. Harmonic U L1 | 10 | SHORT |  | VT
12038 | Mean value 19. Harmonic U L1 | 10 | SHORT |  | VT
12039 | Mean value 21. Harmonic U L1 | 10 | SHORT |  | VT
12040 | Mean value 23. Harmonic U L1 | 10 | SHORT |  | VT
12041 | Mean value 25. Harmonic U L1 | 10 | SHORT |  | VT
12042 | Mean value 1. Harmonic U L2 | 10 | SHORT |  | VT
12043 | Mean value 3. Harmonic U L2 | 10 | SHORT |  | VT
12044 | Mean value 5. Harmonic U L2 | 10 | SHORT |  | VT
12045 | Mean value 7. Harmonic U L2 | 10 | SHORT |  | VT
12046 | Mean value 9. Harmonic U L2 | 10 | SHORT |  | VT
12047 | Mean value 11. Harmonic U L2 | 10 | SHORT |  | VT
12048 | Mean value 13. Harmonic U L2 | 10 | SHORT |  | VT
12049 | Mean value 15. Harmonic U L2 | 10 | SHORT |  | VT
12050 | Mean value 17. Harmonic U L2 | 10 | SHORT |  | VT
12051 | Mean value 19. Harmonic U L2 | 10 | SHORT |  | VT
12052 | Mean value 21. Harmonic U L2 | 10 | SHORT |  | VT
12053 | Mean value 23. Harmonic U L2 | 10 | SHORT |  | VT
12054 | Mean value 25. Harmonic U L2 | 10 | SHORT |  | VT
12055 | Mean value 1. Harmonic U L3 | 10 | SHORT |  | VT
12056 | Mean value 3. Harmonic U L3 | 10 | SHORT |  | VT
12057 | Mean value 5. Harmonic U L3 | 10 | SHORT |  | VT
12058 | Mean value 7. Harmonic U L3 | 10 | SHORT |  | VT
12059 | Mean value 9. Harmonic U L3 | 10 | SHORT |  | VT
12060 | Mean value 11. Harmonic U L3 | 10 | SHORT |  | VT
12061 | Mean value 13. Harmonic U L3 | 10 | SHORT |  | VT
12062 | Mean value 15. Harmonic U L3 | 10 | SHORT |  | VT
12063 | Mean value 17. Harmonic U L3 | 10 | SHORT |  | VT
12064 | Mean value 19. Harmonic U L3 | 10 | SHORT |  | VT
12065 | Mean value 21. Harmonic U L3 | 10 | SHORT |  | VT
12066 | Mean value 23. Harmonic U L3 | 10 | SHORT |  | VT
12067 | Mean value 25. Harmonic U L3 | 10 | SHORT |  | VT
12068 | Mean value 1. Harmonic I L1 | 1000 | SHORT |  | CT
12069 | Mean value 3. Harmonic I L1 | 1000 | SHORT |  | CT
12070 | Mean value 5. Harmonic I L1 | 1000 | SHORT |  | CT
12071 | Mean value 7. Harmonic I L1 | 1000 | SHORT |  | CT
12072 | Mean value 9. Harmonic I L1 | 1000 | SHORT |  | CT
12073 | Mean value 11. Harmonic I L1 | 1000 | SHORT |  | CT
12074 | Mean value 13. Harmonic I L1 | 1000 | SHORT |  | CT
12075 | Mean value 15. Harmonic I L1 | 1000 | SHORT |  | CT
12076 | Mean value 17. Harmonic I L1 | 1000 | SHORT |  | CT
12077 | Mean value 19. Harmonic I L1 | 1000 | SHORT |  | CT
12078 | Mean value 21. Harmonic I L1 | 1000 | SHORT |  | CT
12079 | Mean value 23. Harmonic I L1 | 1000 | SHORT |  | CT
12080 | Mean value 25. Harmonic I L1 | 1000 | SHORT |  | CT
12081 | Mean value 1. Harmonic I L1 | 1000 | SHORT |  | CT
12082 | Mean value 3. Harmonic I L1 | 1000 | SHORT |  | CT
12083 | Mean value 5. Harmonic I L1 | 1000 | SHORT |  | CT
12084 | Mean value 7. Harmonic I L1 | 1000 | SHORT |  | CT
12085 | Mean value 9. Harmonic I L1 | 1000 | SHORT |  | CT
12086 | Mean value 11. Harmonic I L1 | 1000 | SHORT |  | CT
12087 | Mean value 13. Harmonic I L1 | 1000 | SHORT |  | CT
12088 | Mean value 15. Harmonic I L1 | 1000 | SHORT |  | CT
12089 | Mean value 17. Harmonic I L1 | 1000 | SHORT |  | CT
12090 | Mean value 19. Harmonic I L1 | 1000 | SHORT |  | CT
12091 | Mean value 21. Harmonic I L1 | 1000 | SHORT |  | CT
12092 | Mean value 23. Harmonic I L1 | 1000 | SHORT |  | CT
12093 | Mean value 25. Harmonic I L1 | 1000 | SHORT |  | CT
12094 | Mean value 1. Harmonic I L2 | 1000 | SHORT |  | CT
12095 | Mean value 3. Harmonic I L2 | 1000 | SHORT |  | CT
12096 | Mean value 5. Harmonic I L2 | 1000 | SHORT |  | CT
12097 | Mean value 7. Harmonic I L2 | 1000 | SHORT |  | CT
12098 | Mean value 9. Harmonic I L2 | 1000 | SHORT |  | CT
12099 | Mean value 11. Harmonic I L2 | 1000 | SHORT |  | CT
12100 | Mean value 13. Harmonic I L2 | 1000 | SHORT |  | CT
12101 | Mean value 15. Harmonic I L2 | 1000 | SHORT |  | CT
12102 | Mean value 17. Harmonic I L2 | 1000 | SHORT |  | CT
12103 | Mean value 19. Harmonic I L2 | 1000 | SHORT |  | CT
12104 | Mean value 21. Harmonic I L2 | 1000 | SHORT |  | CT
12105 | Mean value 23. Harmonic I L2 | 1000 | SHORT |  | CT
12106 | Mean value 25. Harmonic I L2 | 1000 | SHORT |  | CT
12107 | Mean value THD U L1 | 100 | SHORT
12108 | Mean value THD U L2 | 100 | SHORT
12109 | Mean value THD U L3 | 100 | SHORT
12110 | Mean value THD I L1 | 100 | SHORT
12111 | Mean value THD I L2 | 100 | SHORT
12112 | Mean value THD I L3 | 100 | SHORT
12113 | Mean value Frequency | 100 | SHORT
12114 | Mean value Zero sequence U | 10 | SHORT |  | VT
12115 | Mean value Postive sequence U | 10 | SHORT |  | VT
12116 | Mean value Negative sequence U | 10 | SHORT |  | VT
12117 | Mean value Zero sequence I | 1000 | SHORT |  | CT
12118 | Mean value Postive sequence I | 1000 | SHORT |  | CT
12119 | Mean value Negative sequence I | 1000 | SHORT |  | CT
12120 | Mean value Distortion power L1 | 10 | SHORT |  | CT VT
12121 | Mean value Distortion power L2 | 10 | SHORT |  | CT VT
12122 | Mean value Distortion power L3 | 10 | SHORT |  | CT VT
12123 | Mean value Distortion power L4 | 1 | SHORT |  | CT VT
13000 | Max. value U L1 | 10 | SHORT |  | VT
13002 | Max. value U L2 | 10 | SHORT |  | VT
13004 | Max. value U L3 | 10 | SHORT |  | VT
13006 | Max. value U L1-L2 | 10 | SHORT |  | VT
13008 | Max. value U L2-L3 | 10 | SHORT |  | VT
13010 | Max. value U L3-L1 | 10 | SHORT |  | VT
13012 | Max. value I L1 | 1000 | SHORT |  | CT
13014 | Max. value I L2 | 1000 | SHORT |  | CT
13016 | Max. value I L3 | 1000 | SHORT |  | CT
13018 | Max. value I Sum | 1000 | SHORT |  | CT
13020 | Max. value P L1 | 10 | SHORT |  | CT VT
13022 | Max. value P L2 | 10 | SHORT |  | CT VT
13024 | Max. value P L3 | 10 | SHORT |  | CT VT
13026 | Max. value P Sum | 1 | SHORT |  | CT VT
13028 | Max. value Q L1 | 10 | SHORT |  | CT VT
13030 | Max. value Q L2 | 10 | SHORT |  | CT VT
13032 | Max. value Q L3 | 10 | SHORT |  | CT VT
13034 | Max. value Q Sum | 1 | SHORT |  | CT VT
13036 | Max. value S L1 | 10 | SHORT |  | CT VT
13038 | Max. value S L2 | 10 | SHORT |  | CT VT
13040 | Max. value S L3 | 10 | SHORT |  | CT VT
13042 | Max. value S Sum | 10 | SHORT |  | CT VT
13044 | Max. value CosPhi L1 | 100 | SHORT
13046 | Max. value CosPhi L2 | 100 | SHORT
13048 | Max. value CosPhi L3 | 100 | SHORT
13050 | Max. value CosPhi Sum | 100 | SHORT
13052 | Max. value real power, fund. oscillation L1 | 10 | SHORT |  | CT VT
13054 | Max. value real power, fund. oscillation L2 | 10 | SHORT |  | CT VT
13056 | Max. value real power, fund. oscillation L3 | 10 | SHORT |  | CT VT
13058 | Max. value 1. Harmonic U L1 | 10 | SHORT |  | VT
13060 | Max. value 3. Harmonic U L1 | 10 | SHORT |  | VT
13062 | Max. value 5. Harmonic U L1 | 10 | SHORT |  | VT
13064 | Max. value 7. Harmonic U L1 | 10 | SHORT |  | VT
13066 | Max. value 9. Harmonic U L1 | 10 | SHORT |  | VT
13068 | Max. value 11. Harmonic U L1 | 10 | SHORT |  | VT
13070 | Max. value 13. Harmonic U L1 | 10 | SHORT |  | VT
13072 | Max. value 15. Harmonic U L1 | 10 | SHORT |  | VT
13074 | Max. value 17. Harmonic U L1 | 10 | SHORT |  | VT
13076 | Max. value 19. Harmonic U L1 | 10 | SHORT |  | VT
13078 | Max. value 21. Harmonic U L1 | 10 | SHORT |  | VT
13080 | Max. value 23. Harmonic U L1 | 10 | SHORT |  | VT
13082 | Max. value 25. Harmonic U L1 | 10 | SHORT |  | VT
13084 | Max. value 1. Harmonic U L2 | 10 | SHORT |  | VT
13086 | Max. value 3. Harmonic U L2 | 10 | SHORT |  | VT
13088 | Max. value 5. Harmonic U L2 | 10 | SHORT |  | VT
13090 | Max. value 7. Harmonic U L2 | 10 | SHORT |  | VT
13092 | Max. value 9. Harmonic U L2 | 10 | SHORT |  | VT
13094 | Max. value 11. Harmonic U L2 | 10 | SHORT |  | VT
13096 | Max. value 13. Harmonic U L2 | 10 | SHORT |  | VT
13098 | Max. value 15. Harmonic U L2 | 10 | SHORT |  | VT
13100 | Max. value 17. Harmonic U L2 | 10 | SHORT |  | VT
13102 | Max. value 19. Harmonic U L2 | 10 | SHORT |  | VT
12104 | Max. value 21. Harmonic U L2 | 10 | SHORT |  | VT
13106 | Max. value 23. Harmonic U L2 | 10 | SHORT |  | VT
13108 | Max. value 25. Harmonic U L2 | 10 | SHORT |  | VT
13110 | Max. value 1. Harmonic U L3 | 10 | SHORT |  | VT
13112 | Max. value 3. Harmonic U L3 | 10 | SHORT |  | VT
13114 | Max. value 5. Harmonic U L3 | 10 | SHORT |  | VT
13116 | Max. value 7. Harmonic U L3 | 10 | SHORT |  | VT
13118 | Max. value 9. Harmonic U L3 | 10 | SHORT |  | VT
13120 | Max. value 11. Harmonic U L3 | 10 | SHORT |  | VT
13122 | Max. value 13. Harmonic U L3 | 10 | SHORT |  | VT
13124 | Max. value 15. Harmonic U L3 | 10 | SHORT |  | VT
13126 | Max. value 17. Harmonic U L3 | 10 | SHORT |  | VT
13128 | Max. value 19. Harmonic U L3 | 10 | SHORT |  | VT
13130 | Max. value 21. Harmonic U L3 | 10 | SHORT |  | VT
13132 | Max. value 23. Harmonic U L3 | 10 | SHORT |  | VT
13134 | Max. value 25. Harmonic U L3 | 10 | SHORT |  | VT
13136 | Max. value 1. Harmonic I L1 | 1000 | SHORT |  | CT
13138 | Max. value 3. Harmonic I L1 | 1000 | SHORT |  | CT
13140 | Max. value 5. Harmonic I L1 | 1000 | SHORT |  | CT
13142 | Max. value 7. Harmonic I L1 | 1000 | SHORT |  | CT
13144 | Max. value 9. Harmonic I L1 | 1000 | SHORT |  | CT
13146 | Max. value 11. Harmonic I L1 | 1000 | SHORT |  | CT
13148 | Max. value 13. Harmonic I L1 | 1000 | SHORT |  | CT
13150 | Max. value 15. Harmonic I L1 | 1000 | SHORT |  | CT
13152 | Max. value 17. Harmonic I L1 | 1000 | SHORT |  | CT
13154 | Max. value 19. Harmonic I L1 | 1000 | SHORT |  | CT
13156 | Max. value 21. Harmonic I L1 | 1000 | SHORT |  | CT
13158 | Max. value 23. Harmonic I L1 | 1000 | SHORT |  | CT
13160 | Max. value 25. Harmonic I L1 | 1000 | SHORT |  | CT
13162 | Max. value 1. Harmonic I L2 | 1000 | SHORT |  | CT
13164 | Max. value 3. Harmonic I L2 | 1000 | SHORT |  | CT
13166 | Max. value 5. Harmonic I L2 | 1000 | SHORT |  | CT
13168 | Max. value 7. Harmonic I L2 | 1000 | SHORT |  | CT
13170 | Max. value 9. Harmonic I L2 | 1000 | SHORT |  | CT
13172 | Max. value 11. Harmonic I L2 | 1000 | SHORT |  | CT
13174 | Max. value 13. Harmonic I L2 | 1000 | SHORT |  | CT
13176 | Max. value 15. Harmonic I L2 | 1000 | SHORT |  | CT
13178 | Max. value 17. Harmonic I L2 | 1000 | SHORT |  | CT
13180 | Max. value 19. Harmonic I L2 | 1000 | SHORT |  | CT
13182 | Max. value 21. Harmonic I L2 | 1000 | SHORT |  | CT
13184 | Max. value 23. Harmonic I L2 | 1000 | SHORT |  | CT
13186 | Max. value 25. Harmonic I L2 | 1000 | SHORT |  | CT
13188 | Max. value 1. Harmonic I L3 | 1000 | SHORT |  | CT
13190 | Max. value 3. Harmonic I L3 | 1000 | SHORT |  | CT
13192 | Max. value 5. Harmonic I L3 | 1000 | SHORT |  | CT
13194 | Max. value 7. Harmonic I L3 | 1000 | SHORT |  | CT
13196 | Max. value 9. Harmonic I L3 | 1000 | SHORT |  | CT
13198 | Max. value 11. Harmonic I L3 | 1000 | SHORT |  | CT
13200 | Max. value 13. Harmonic I L3 | 1000 | SHORT |  | CT
13202 | Max. value 15. Harmonic I L3 | 1000 | SHORT |  | CT
13204 | Max. value 17. Harmonic I L3 | 1000 | SHORT |  | CT
13206 | Max. value 19. Harmonic I L3 | 1000 | SHORT |  | CT
13208 | Max. value 21. Harmonic I L3 | 1000 | SHORT |  | CT
13210 | Max. value 23. Harmonic I L3 | 1000 | SHORT |  | CT
13212 | Max. value 25. Harmonic I L3 | 1000 | SHORT |  | CT
13214 | Max. value THD U L1 | 100 | SHORT
13216 | Max. value THD U L2 | 100 | SHORT
13218 | Max. value THD U L3 | 100 | SHORT
13220 | Max. value THD I L1 | 100 | SHORT
13222 | Max. value THD I L2 | 100 | SHORT
13224 | Max. value THD I L3 | 100 | SHORT
13226 | Max. value Frequency | 100 | SHORT
13228 | Max. value Zero sequence | 10 | SHORT |  | VT
13230 | Max. value Postive sequence | 10 | SHORT |  | VT
13232 | Max. value Negative sequence | 10 | SHORT |  | VT
13234 | Max. value Zero sequence | 1000 | SHORT |  | CT
13236 | Max. value Postive sequence | 1000 | SHORT |  | CT
13238 | Max. value Negative sequence | 1000 | SHORT |  | CT
13240 | Max. value distortion power L1 | 10 | SHORT |  | CT VT
13242 | Max. value Distortion power L2 | 10 | SHORT |  | CT VT
13244 | Max. value Distortion power L3 | 10 | SHORT |  | CT VT
13246 | Max. value Distortion power L4 | 1 | SHORT |  | CT VT
13248 | Max. value Mean value, I L1 | 1000 | SHORT |  | CT
13250 | Max. value Mean value, I L2 | 1000 | SHORT |  | CT
13252 | Max. value Mean value, I L3 | 1000 | SHORT |  | CT
13254 | Max. value Mean value, I Sum (N) | 1 | SHORT |  | CT
13256 | Max. of Mean value P L1 | 10 | SHORT |  | CT VT
13258 | Max. of Mean value P L2 | 10 | SHORT |  | CT VT
13260 | Max. of Mean value P L3 | 10 | SHORT |  | CT VT
13262 | Max. of Mean value P Sum | 1 | SHORT |  | CT VT
14000 | Min. value U L1 | 10 | SHORT |  | VT
14001 | Min. value U L2 | 10 | SHORT |  | VT
14002 | Min. value U L3 | 10 | SHORT |  | VT
14003 | Min. value U L1-L2 | 10 | SHORT |  | VT
14004 | Min. value U L2-L3 | 10 | SHORT |  | VT
14005 | Min. value U L3-L1 | 10 | SHORT |  | VT
14006 | Min. value CosPhi L1 | 1 | SHORT
14007 | Min. value CosPhi L2 | 1 | SHORT
14008 | Min. value CosPhi L3 | 1 | SHORT
14009 | Min. value CosPhi Sum | 1 | SHORT
14010 | Min. value 1. Harmonic U L1 | 10 | SHORT |  | VT
14011 | Min. value 3. Harmonic U L1 | 10 | SHORT |  | VT
14012 | Min. value 5. Harmonic U L1 | 10 | SHORT |  | VT
14013 | Min. value 7. Harmonic U L1 | 10 | SHORT |  | VT
14014 | Min. value 9. Harmonic U L1 | 10 | SHORT |  | VT
14015 | Min. value 11. Harmonic U L1 | 10 | SHORT |  | VT
14016 | Min. value 13. Harmonic U L1 | 10 | SHORT |  | VT
14017 | Min. value 15. Harmonic U L1 | 10 | SHORT |  | VT
14018 | Min. value 17. Harmonic U L1 | 10 | SHORT |  | VT
14019 | Min. value 19. Harmonic U L1 | 10 | SHORT |  | VT
14020 | Min. value 21. Harmonic U L1 | 10 | SHORT |  | VT
14021 | Min. value 23. Harmonic U L1 | 10 | SHORT |  | VT
14022 | Min. value 25. Harmonic U L1 | 10 | SHORT |  | VT
14023 | Min. value 1. Harmonic U L2 | 10 | SHORT |  | VT
14024 | Min. value 3. Harmonic U L2 | 10 | SHORT |  | VT
14025 | Min. value 5. Harmonic U L2 | 10 | SHORT |  | VT
14026 | Min. value 7. Harmonic U L2 | 10 | SHORT |  | VT
14027 | Min. value 9. Harmonic U L2 | 10 | SHORT |  | VT
14028 | Min. value 11. Harmonic U L2 | 10 | SHORT |  | VT
14029 | Min. value 13. Harmonic U L2 | 10 | SHORT |  | VT
14030 | Min. value 15. Harmonic U L2 | 10 | SHORT |  | VT
14031 | Min. value 17. Harmonic U L2 | 10 | SHORT |  | VT
14032 | Min. value 19. Harmonic U L2 | 10 | SHORT |  | VT
14033 | Min. value 23. Harmonic U L2 | 10 | SHORT |  | VT
14034 | Min. value 25. Harmonic U L2 | 10 | SHORT |  | VT
14035 | Min. value 1. Harmonic U L3 | 10 | SHORT |  | VT
14036 | Min. value 3. Harmonic U L3 | 10 | SHORT |  | VT
14037 | Min. value 5. Harmonic U L3 | 10 | SHORT |  | VT
14038 | Min. value 7. Harmonic U L3 | 10 | SHORT |  | VT
14039 | Min. value 9. Harmonic U L3 | 10 | SHORT |  | VT
14040 | Min. value 11. Harmonic U L3 | 10 | SHORT |  | VT
14041 | Min. value 13. Harmonic U L3 | 10 | SHORT |  | VT
14042 | Min. value 15. Harmonic U L3 | 10 | SHORT |  | VT
14043 | Min. value 17. Harmonic U L3 | 10 | SHORT |  | VT
14044 | Min. value 19. Harmonic U L3 | 10 | SHORT |  | VT
14045 | Min. value 21. Harmonic U L3 | 10 | SHORT |  | VT
14046 | Min. value 23. Harmonic U L3 | 10 | SHORT |  | VT
14047 | Min. value 23. Harmonic U L3 | 10 | SHORT |  | VT
14048 | Min. value 25. Harmonic U L3 | 10 | SHORT |  | VT
14049 | Min. value THD U L1 | 100 | SHORT
14050 | Min. value THD U L2 | 100 | SHORT
14051 | Min. value THD U L3 | 100 | SHORT
14052 | Min. value Frequency | 100 | SHORT
14053 | Min. value Zero sequence U | 10 | SHORT |  | VT
14054 | Min. value Postive sequence U | 10 | SHORT |  | VT
14055 | Min. value Negative sequence U | 10 | SHORT |  | VT
15000 | Real energy consumption L1 | 1 | LONG
15002 | Real energy consumption L2 | 1 | LONG
15004 | Real energy consumption L3 | 1 | LONG
15006 | Real energy consumption Sum | 1 | LONG
15008 | Real energy consumption HT L1 | 1 | LONG
15010 | Real energy consumption HT L2 | 1 | LONG
15012 | Real energy consumption HT L3 | 1 | LONG
15014 | Real energy consumption HT Sum | 1 | LONG
15016 | Real energy consumption NT L1 | 1 | LONG
15018 | Real energy consumption NT L1 | 1 | LONG
15020 | Real energy consumption NT L1 | 1 | LONG
15022 | Real energy consumption NT L1 | 1 | LONG
15024 | Apparent energy L1 | 1 | LONG
15026 | Apparent energy L2 | 1 | LONG
15028 | Apparent energy L3 | 1 | LONG
15030 | Apparent energy Sum | 1 | LONG
15032 | Apparent energy HT L1 | 1 | LONG
15034 | Apparent energy HT L2 | 1 | LONG
15036 | Apparent energy HT L3 | 1 | LONG
15038 | Apparent energy HT Sum | 1 | LONG
15040 | Apparent energy NT L1 | 1 | LONG
15042 | Apparent energy NT L2 | 1 | LONG
15044 | Apparent energy NT L3 | 1 | LONG
15046 | Apparent energy NT Sum | 1 | LONG
15048 | Reactive energy induktiv L1 | 1 | LONG
15050 | Reactive energy induktiv L2 | 1 | LONG
15052 | Reactive energy induktiv L3 | 1 | LONG
15054 | Reactive energy induktiv Sum | 1 | LONG
15056 | Reactive energy induktiv HT L1 | 1 | LONG
15058 | Reactive energy induktiv HT L2 | 1 | LONG
15060 | Reactive energy induktiv HT L3 | 1 | LONG
15062 | Reactive energy induktiv HT Sum | 1 | LONG
15064 | Reactive energy induktiv NT L1 | 1 | LONG
15066 | Reactive energy induktiv NT L2 | 1 | LONG
15068 | Reactive energy induktiv NT L3 | 1 | LONG
15070 | Reactive energy induktiv NT Sum | 1 | LONG
15072 | Real energy geliefert L1 | 1 | LONG
15074 | Real energy geliefert L2 | 1 | LONG
15076 | Real energy geliefert L3 | 1 | LONG
15078 | Real energy geliefert Sum | 1 | LONG
15080 | Reactive energy capacitive L1 | 1 | LONG
15082 | Reactive energy capacitive L2 | 1 | LONG
15084 | Reactive energy capacitive L3 | 1 | LONG
15086 | Reactive energy capacitive Sum | 1 | LONG
15088 | Real energy Sum, without return travel block | 1 | LONG
15090 | Reactive energy Sum, without ret. trav. block | 1 | LONG