## Tabelle1
Parameter
These values can be set via the device buttons
Address | Format | RD/WR | Unit | Note | Adjustment Area | Default
0 | SHORT | RD/WR | - | Device adress | 0..255 (*1) | 1
1 | SHORT | RD/WR | kbps | Baudrate | 0=9.6kbps | 4
1=19.2kbps
2=38.4kbps
3=57.6kbps
4=115.2kbps
2 | SHORT | RD/WR | - | Modbus Master
|  |  |  | (Master=1 only for version ethernet) | 0.1 | 0
3 | SHORT | RD/WR | - | Stop bits (0=1 bit, 1=2 bits) | 0.1 | 0
10 | FLOAT | RD/WR | A | Current transformer I1, primary | 0..1000000 (*2) | 5
12 | FLOAT | RD/WR | A | Current transformer I1, sec. | 1..5 | 5
14 | FLOAT | RD/WR | V | Voltage transformer V1, primary | 0..1000000 (*2) | 400
16 | FLOAT | RD/WR | V | Voltage transformer V1, sec. | 100, 400 | 400
18 | FLOAT | RD/WR | A | Current transformer I2, primary | 0..1000000 (*2) | 5
20 | FLOAT | RD/WR | A | Current transformer I2, sec. | 1..5 | 5
22 | FLOAT | RD/WR | V | Voltage transformer V2, primary | 1..1000000 | 400
24 | FLOAT | RD/WR | V | Voltage transformer V2, sec. | 100, 400 | 400
26 | FLOAT | RD/WR | A | Current transformer I3, primary | 1..1000000 | 5
28 | FLOAT | RD/WR | A | Current transformer I3, sec. | 1..5 | 5
30 | FLOAT | RD/WR | V | Voltage transformer V3, primary | 1..1000000 | 400
32 | FLOAT | RD/WR | V | Voltage transformer V3, sec. | 100, 400 | 400
34 | SHORT | RD/WR | Hz | Frequency determination | 0, 45..65 | 0
0=Auto, 45..65=Hz
35 | SHORT | RD/WR | - | Display contrast | 0 .. 9 | 5
0 (low), 9 (high)
36 | SHORT | RD/WR | - | Background lighting | 0 .. 9 | 6
0 (dark), 9 (bright)
37 | SHORT | RD/WR | - | Indication profile | 0 .. 3 | 0
0 .. 2 = Fix indication profiles
3 = Free selectable indication profile
38 | SHORT | RD/WR | - | Indication rotation profile | 0 .. 3 | 0
0 .. 2 = Fix indication rotation profiles
Indication rotation profile
3 = Free selectable indication
rotation profile
39 | SHORT | RD/WR | Sec. | Rotation time | 0 .. 60 | 0
40 | SHORT | RD/WR | - | Averaging time, I | 0 .. 8* | 6
41 | SHORT | RD/WR | - | Averaging time, P | 0 .. 8* | 6
42 | SHORT | RD/WR | - | Averaging time, U | 0 .. 8* | 6
43 | FLOAT | RD/WR | A | Nominal current TDD | 0 .. 1000000 | 150
45 | INT | RD/WR | mA | Threshold, current measurement L1..L3 | 0 .. 200 | 5
50 | SHORT | RD/WR | - | Password | 0 .. 999 | 0 (no password)
100 | SHORT | RD/WR | - | Address of measurement value, | 0 .. 32000 | 874
digital output 1
101 | SHORT | RD/WR | - | Address of measurement value, | 0 .. 32000 | 882
digital output 2
102 | FLOAT | RD/WR | - | Pulse valence, out 1 | -1000000 .. + 1000000 | 1000
104 | FLOAT | RD/WR | - | Pulse valence, out 2 | -1000000 .. + 1000000 | 1000
106 | SHORT | RD/WR | - | Min. pulse duration, | 1..1000 | 5
digital output 1/2
107 | SHORT | RD/WR | - | Results of the Comparator group 1 | 0, 1
combine A, B, C
1 = and, 0 = or
108 | FLOAT | RD/WR | - | Comparator 1A, limit | -1012-1..+1012-1
110 | SHORT | RD/WR | - | Comparator 1A, | 0 .. 32000
Address of measurement value
111 | SHORT | RD/WR | Sec. | Comparator 1A, min. on time | 0 .. 32000
112 | SHORT | RD/WR | Sec. | Comparator 1A, lead time | 0 .. 32000
113 | SHORT | RD/WR | - | Comparator 1A, operator | 0, 1
„>=“ = 0, „<“ = 1
114 | FLOAT | RD/WR | - | Comparator 1B, limit | -1012-1..+1012-1
116 | SHORT | RD/WR | - | Comparator 1B, | 0 .. 32000
Address of measurement value
117 | SHORT | RD/WR | Sec. | Comparator 1B, min. on time | 0 .. 32000
118 | SHORT | RD/WR | Sec. | Comparator 1B, lead time | 0 .. 32000
119 | SHORT | RD/WR | - | Comparator 1B, operator | 0, 1
„>=“ = 0, „<“ = 1
120 | FLOAT | RD/WR | - | Comparator 1C, limit | -1012-1..+1012-1
122 | SHORT | RD/WR | - | Comparator 1C, | 0 .. 32000
Address of measurement value
123 | SHORT | RD/WR | Sec. | Comparator 1C, min. on time | 0 .. 32000
124 | SHORT | RD/WR | Sec. | Comparator 1C, lead time | 0 .. 32000
125 | SHORT | RD/WR | - | Comparator 1C, operator | 0, 1
„>=“ = 0, „<“ = 1
126 | SHORT | RD/WR | - | Results of the Comparator group 2 | 0, 1
combine A, B, C
1 = and, 0 = or
127 | FLOAT | RD/WR | - | Comparator 2A, limit | -1012-1..+1012-1
129 | SHORT | RD/WR | - | Comparator 2A, | 0 .. 32000
Address of measurement value
130 | SHORT | RD/WR | Sec. | Comparator 2A, min. on time | 0 .. 32000
131 | SHORT | RD/WR | Sec. | Comparator 2A, lead time | 0 .. 32000
132 | SHORT | RD/WR | - | Comparator 2A, operator | 0, 1
„>=“ = 0, „<“ = 1
133 | FLOAT | RD/WR | - | Comparator 2B, limit | -1012-1..+1012-1
135 | SHORT | RD/WR | - | Comparator 2B, Address of measurement value | 0 .. 32000
136 | SHORT | RD/WR | Sec. | Comparator 2B, min. on time | 0 .. 32000
137 | SHORT | RD/WR | Sec. | Comparator 2B, lead time | 0 .. 32000
138 | SHORT | RD/WR | - | Comparator 2B, operator | 0, 1
„>=“ = 0, „<“ = 1
139 | FLOAT | RD/WR | - | Comparator 2C, limit | -1012-1..+1012-1
141 | SHORT | RD/WR | - | Comparator 2C, | 0 .. 32000
Address of measurement value
142 | SHORT | RD/WR | Sec. | Comparator 2C, min. on time | 0 .. 32000
143 | SHORT | RD/WR | Sec. | Comparator 2C, lead time | 0 .. 32000
144 | SHORT | RD/WR | - | Comparator 2C, operator | 0, 1
„>=“ = 0, „<“ = 1
145 | SHORT | RD/WR | - | „Display blinking“ | 0-3 | 0
Bit 1 = 1/0: active/inactive for
comparator group output 1
Bit 2 = 1/0: active/inactive for
comparator group output 2
200 | SHORT | RD/WR | - | Source selection for DigitalOutput 1 | 0 .. 4 | 1
0 = Comparator 1
1 = Pulse output (S0)
1 = External source - Modbus
2 = External source -Profibus (option)
3 = External source -Ethernet (option)
201 | SHORT | RD/WR | - | Output 1 inverted | 0 .. 1 | 0
202 | SHORT | RD/WR | - | Source selection for DigitalOutput 2 | 0 .. 4 | 1
0 = Comparator 2
1 = Pulse output (S0)
1 = External source - Modbus
2 = External source -Profibus (option)
3 = External source -Ethernet (option)
203 | SHORT | RD/WR | - | Output 2 inverted | 0 .. 1 | 0
300 | String | RD/WR | - | Indication profile | GridVis | 0
400 | String | RD/WR | - | Indication rotation profile | GridVis | 0
500 | SHORT | RD/WR | - | Connection configuration, I L1 | -3 .. 3 | 1
501 | SHORT | RD/WR | - | Connection configuration, I L2 | -3 .. 3 | 2
502 | SHORT | RD/WR | - | Connection configuration, I L3 | -3 .. 3 | 3
-1 = Measurement in phase L1,
|  |  |  | Connection (s1-s2) changed |  |  | -2 = Measurement in phase L2,
Connection (s1-s2) changed
-3 = Measurement in phase L3,
Connection (s1-s2) changed
0 = Channel switched off
1 = Measurement in phase L1
2 = Measurement in phase L2
3 = Measurement in phase L3
503 | SHORT | RD/WR | - | Connection configuration, U L1 | 0 .. 3 | 1
504 | SHORT | RD/WR | - | Connection configuration, U L2 | 0 .. 3 | 2
505 | SHORT | RD/WR | - | Connection configuration, U L3 | 0 .. 3 | 3
0 = Channel switched off
1 = Measurement in phase L1
2 = Measurement in phase L2
3 = Measurement in phase L3
506 | SHORT | RD/WR | - | Delete min. and maximum values | 0..1 | 0
507 | SHORT | RD/WR | - | Delete energy values | 0..1 | 0
508 | SHORT | RD/WR | - | Write in EEPROM | 0..1 | 0
509 | SHORT | RD/WR | - | Connection diagram voltage | 0..8 1) | 0
510 | SHORT | RD/WR | - | Connection diagram current | 0..8 | 0
511 | SHORT | RD/WR | - | Relevant voltage, for THD and FFT | 0..1 | 0
display of THD and FFT
0=THD L-N, FFT L-N
1=THD L-L, FFT L-L
512 | SHORT | RD/WR | - | Year * | 0..99
513 | SHORT | RD/WR | - | Month * | 0..12
514 | SHORT | RD/WR | - | Day * | 0..31
515 | SHORT | RD/WR | - | Hour * | 0..24
516 | SHORT | RD/WR | - | Minute * | 0..59
517 | SHORT | RD/WR | - | Second * | 0..59
600 | UINT | RD/WR | - | Overrange | 0, 0xFFFFFFFF
602 | SHORT | RD/WR | - | Modbus value for output 1 | 0..1
605 | SHORT | RD/WR | - | Modbus-value for output 2 | 0..1
608 | SHORT | RD | - | Condition output 1
609 | SHORT | RD | - | Condition output 2
610 | SHORT | RD | - | Comparator 1 output A
611 | SHORT | RD | - | Comparator 1 output B
612 | SHORT | RD | - | Comparator 1 output C
613 | SHORT | RD | - | Comparator 2 output A
614 | SHORT | RD | - | Comparator 2 output B
615 | SHORT | RD | - | Comparator 2 output C
616 | SHORT | RD | - | Linkage result of comparator group 1
617 | SHORT | RD | - | Linkage result of comparator group 2
618 | SHORT | RD/WR | - | Rate, real energy** | 0..127 | 0
619 | SHORT | RD/WR | - | Rate, real energy consumed** | 0..127 | 0
620 | SHORT | RD/WR | - | Rate, real energy delivered** | 0..127 | 0
621 | SHORT | RD/WR | - | Rate, reactive energy** | 0..127 | 0
622 | SHORT | RD/WR | - | Rate, reactive energy inductive** | 0..127 | 0
623 | SHORT | RD/WR | - | Rate, reactive energy capacitive** | 0..127 | 0
624 | SHORT | RD/WR | - | Rate, apparent energy** | 0..127 | 0
750 | SHORT | RD | - | Software release
754 | SERNR | RD | - | Serial number
756 | SERNR | RD | - | Production number
761 | USHORT | RD | - | Module number (0=no module, 1=Profibus, 2=CBM, 3=Ethernet)
Adress list
Frequently required readings
Address | Format | RD/WR | Unit | Note | Index
19000 | FLOAT | RD | V | Voltage L1-N | [0]
19002 | FLOAT | RD | V | Voltage L2-N | [1]
19004 | FLOAT | RD | V | Voltage L3-N | [2]
19006 | FLOAT | RD | V | Voltage L1-L2 | [0]
19008 | FLOAT | RD | V | Voltage L2-L3 | [1]
19010 | FLOAT | RD | V | Voltage L1-L3 | [2]
19012 | FLOAT | RD | A | Current I L1 | [0]
19014 | FLOAT | RD | A | Current I L2 | [1]
19016 | FLOAT | RD | A | Current I L3 | [2]
19018 | FLOAT | RD | A | Vector sum; IN=I1+I2+I3 | [3]
19020 | FLOAT | RD | W | Real power P1 L1N | [0]
19022 | FLOAT | RD | W | Real power P2 L2N | [1]
19024 | FLOAT | RD | W | Real power P3 L3N | [2]
19026 | FLOAT | RD | W | Sum; Psum3=P1+P2+P3 | [3]
19028 | FLOAT | RD | VA | Apparent power S1 L1N | [0]
19030 | FLOAT | RD | VA | Apparent power S2 L2N | [1]
19032 | FLOAT | RD | VA | Apparent power S3 L3N | [2]
19034 | FLOAT | RD | VA | Sum; Ssum3=S1+S2+S3 | [3]
19036 | FLOAT | RD | var | Fund. reactive power Q1 L1N | [0]
19038 | FLOAT | RD | var | Fund. reactive power Q2 L2N | [1]
19040 | FLOAT | RD | var | Fund. reactive power Q3 L3N | [2]
19042 | FLOAT | RD | var | Sum; Qsum3=Q1+Q2+Q3 | [3]
19044 | FLOAT | RD | - | CosPhi; UL1 IL1 (fundamental comp.) | [0]
19046 | FLOAT | RD | - | CosPhi; UL2 IL2 (fundamental comp.) | [1]
19048 | FLOAT | RD | - | CosPhi; UL3 IL3 (fundamental comp.) | [2]
19050 | FLOAT | RD | Hz | Measured frequency
19052 | FLOAT | RD | - | Rotation field; 1=right, 0=none, -1=left
19054 | FLOAT | RD | Wh | Real energy L1 | [0]
19056 | FLOAT | RD | Wh | Real energy L2 | [0]
19058 | FLOAT | RD | Wh | Real energy L3 | [0]
19060 | FLOAT | RD | Wh | Real energy L1..L3 | [0]
19062 | FLOAT | RD | Wh | Real energy L1, consumed | [0]
19064 | FLOAT | RD | Wh | Real energy L2, consumed | [0]
19066 | FLOAT | RD | Wh | Real energy L3, consumed | [0]
19068 | FLOAT | RD | Wh | Real energy L1..L3, consumed, rate 1 | [1]
19070 | FLOAT | RD | Wh | Real energy L1, delivered | [0]
19072 | FLOAT | RD | Wh | Real energy L2, delivered | [0]
19074 | FLOAT | RD | Wh | Real energy L3, delivered | [0]
19076 | FLOAT | RD | Wh | Real energy L1..L3, delivered | [0]
19078 | FLOAT | RD | VAh | Apparent energy L1 | [0]
19080 | FLOAT | RD | VAh | Apparent energy L2 | [0]
19082 | FLOAT | RD | VAh | Apparent energy L3 | [0]
19084 | FLOAT | RD | VAh | Apparent energy L1..L3 | [0]
19086 | FLOAT | RD | varh | Reactive energy L1 | [0]
19088 | FLOAT | RD | varh | Reactive energy L2 | [0]
19090 | FLOAT | RD | varh | Reactive energy L3 | [0]
19092 | FLOAT | RD | varh | Reactive energy L1..L3 | [0]
19094 | FLOAT | RD | varh | Reactive energy ind. L1 | [0]
19096 | FLOAT | RD | varh | Reactive energy ind. L2 | [0]
19098 | FLOAT | RD | varh | Reactive energy ind. L3 | [0]
19100 | FLOAT | RD | varh | Reactive energy ind. L1..L3 | [0]
19102 | FLOAT | RD | varh | Reactive energy cap. L1 | [0]
19104 | FLOAT | RD | varh | Reactive energy cap. L2 | [0]
19106 | FLOAT | RD | varh | Reactive energy cap. L3 | [0]
19108 | FLOAT | RD | varh | Reactive energy cap. L1..L3 | [0]
19110 | FLOAT | RD | % | Harmonic, THD U L1-N | [0]
19112 | FLOAT | RD | % | Harmonic, THD U L2-N | [1]
19114 | FLOAT | RD | % | Harmonic, THD U L3-N | [2]
19116 | FLOAT | RD | % | Harmonic, THD I L1 | [0]
19118 | FLOAT | RD | % | Harmonic, THD I L2 | [1]
19120 | FLOAT | RD | % | Harmonic, THD I L3 | [2]
Measured values, type float
Address | Format | RD/WR | Unit | Note | Index
800 | FLOAT | RD | Hz | Measured frequency
802 | FLOAT | RD | - | Voltage, zero sequence
804 | FLOAT | RD | - | Voltage, negative sequence
806 | FLOAT | RD | - | Voltage, positive sequence
808 | FLOAT | RD | V | Voltage U1 L1-N | [0]
810 | FLOAT | RD | V | Voltage U2 L2-N | [1]
812 | FLOAT | RD | V | Voltage U3 L3-N | [2]
814 | FLOAT | RD | V | Voltage U1 L1-L2 | [0]
816 | FLOAT | RD | V | Voltage U2 L2-L3 | [1]
818 | FLOAT | RD | V | Voltage U3 L3-L1 | [2]
820 | FLOAT | RD | - | Fund. power factor, CosPhi; ULN, IL1 | [0]
822 | FLOAT | RD | - | Fund. power factor, CosPhi; ULN, IL2 | [1]
824 | FLOAT | RD | - | Fund. power factor, CosPhi; ULN, IL3 | [2]
826 | FLOAT | RD | - | Sum; CosPhisum3=P0sum3/Ssum3 | [3]
828 | FLOAT | RD | - | Power factor; UL1N, IL1 | [0]
830 | FLOAT | RD | - | Power factor; UL2N, IL2 | [1]
832 | FLOAT | RD | - | Power factor; UL3N, IL3 | [2]
834 | FLOAT | RD | - | Sum; Power factor sum3=Psum3/Ssum3 | [3]
836 | FLOAT | RD | % | THD, U L1N, bezogen auf U0 L1 | [0]
838 | FLOAT | RD | % | THD, U L2N, bezogen auf U0 L2 | [1]
840 | FLOAT | RD | % | THD, U L3N, bezogen auf U0 L3 | [2]
842 | FLOAT | RD | % | THD, U L1L2, bezogen auf U0 L1L2 | [0]
844 | FLOAT | RD | % | THD, U L2L3, bezogen auf U0 L2L3 | [1]
846 | FLOAT | RD | % | THD, U L3L1, bezogen auf U0 L3L1 | [2]
848 | FLOAT | RD | V | Voltage, real part U1 L1N | [0]
850 | FLOAT | RD | V | Voltage, real part U2 L2N | [1]
852 | FLOAT | RD | V | Voltage, real part U3 L3N | [2]
854 | FLOAT | RD | V | Voltage, imaginary part U L1N | [0]
856 | FLOAT | RD | V | Voltage, imaginary part U L2N | [1]
858 | FLOAT | RD | V | Voltage, imaginary part U L3N | [2]
860 | FLOAT | RD | A | Current I1 L1 | [0]
862 | FLOAT | RD | A | Current I2 L2 | [1]
864 | FLOAT | RD | A | Current I3 L3 | [2]
866 | FLOAT | RD | A | Vector sum; IN=I1+I2+I3 | [3]
868 | FLOAT | RD | W | Real power P1 L1N | [0]
870 | FLOAT | RD | W | Real power P2 L2N | [1]
872 | FLOAT | RD | W | Real power P3 L3N | [2]
874 | FLOAT | RD | W | Sum; Psum3=P1+P2+P3 | [3]
876 | FLOAT | RD | var | Fund. reactive power Q1 L1N | [0]
878 | FLOAT | RD | var | Fund. reactive power Q2 L2N | [1]
880 | FLOAT | RD | var | Fund. reactive power Q3 L3N | [2]
882 | FLOAT | RD | var | Sum; Qsum3=Q1+Q2+Q3 | [3]
884 | FLOAT | RD | VA | Apparent power S1 L1N | [0]
886 | FLOAT | RD | VA | Apparent power S2 L2N | [1]
888 | FLOAT | RD | VA | Apparent power S3 L3N | [2]
890 | FLOAT | RD | VA | Sum; Ssum3=S1+S2+S3 | [3]
892 | FLOAT | RD | W | Fund. real power P01 L1N | [0]
894 | FLOAT | RD | W | Fund. real power P02 L2N | [1]
896 | FLOAT | RD | W | Fund. real power P03 L3N | [2]
898 | FLOAT | RD | W | Sum; P0sum3=P01+P02+P03 | [3]
900 | FLOAT | RD | var | Harmonic distortion power D1 L1N | [0]
902 | FLOAT | RD | var | Harmonic distortion power D2 L2N | [1]
904 | FLOAT | RD | var | Harmonic distortion power D3 L3N | [2]
906 | FLOAT | RD | var | Sum; Dsum3=D1+D2+D3 | [3]
908 | FLOAT | RD | % | THDI1 I1, bezogen auf I01 | [0]
910 | FLOAT | RD | % | THDI2 I2, bezogen auf I02 | [1]
912 | FLOAT | RD | % | THDI3 I3, bezogen auf I03 | [2]
914 | FLOAT | RD | % | TDDI1 I1, bezogen auf den Nenn-Laststrom | [0]
916 | FLOAT | RD | % | TDDI2 I2, bezogen auf den Nenn-Laststrom | [1]
918 | FLOAT | RD | % | TDDI3 I3, bezogen auf den Nenn-Laststrom | [2]
920 | FLOAT | RD | - | Current, zero sequence
922 | FLOAT | RD | - | Current, negative sequence
924 | FLOAT | RD | - | Current, positive sequence
926 | FLOAT | RD | A | Current, real part I L1 | [0]
928 | FLOAT | RD | A | Current, real part I L2 | [1]
930 | FLOAT | RD | A | Current, real part I L3 | [2]
932 | FLOAT | RD | A | Current, imaginary part I L | [0]
934 | FLOAT | RD | A | Current, imaginary part I L | [1]
936 | FLOAT | RD | A | Current, imaginary part I L | [2]
938 | FLOAT | RD | - | Rotation field; 1=right, 0=none, -1=left
6154 | FLOAT | RD |  | Crest factor, U L1
6156 | FLOAT | RD |  | Crest factor, U L2
6158 | FLOAT | RD |  | Crest factor, U L3
6160 | FLOAT | RD |  | Crest factor, I L1
6162 | FLOAT | RD |  | Crest factor, I L2
6164 | FLOAT | RD |  | Crest factor, I L3
Measured values, type short
Address | Format | RD/WR | Unit | Note | Index
3526 | SHORT | RD | Hz | measured frequency |  | 0.01
3527 | SHORT | RD | V | Voltage, zero sequence |  | 0.1
3528 | SHORT | RD | V | Voltage, negative sequence |  | 0.1
3529 | SHORT | RD | V | Voltage, positive sequence |  | 0.1
3530 | SHORT | RD | V | Voltage U1 L1-N | [0] | 0.1
3531 | SHORT | RD | V | Voltage U2 L2-N | [1] | 0.1
3532 | SHORT | RD | V | Voltage U3 L3-N | [2] | 0.1
3533 | SHORT | RD | V | Voltage U1 L1-L2 | [0] | 0.1
3534 | SHORT | RD | V | Voltage U2 L2-L3 | [1] | 0.1
3535 | SHORT | RD | V | Voltage U3 L3-L1 | [2] | 0.1
3776 | SHORT | RD | - | Fund. power factor, CosPhi; ULN IL | [0] | 0.01
3777 | SHORT | RD | - | Fund. power factor, CosPhi; ULN IL | [1] | 0.01
3778 | SHORT | RD | - | Fund. power factor, CosPhi; ULN IL | [2] | 0.01
3779 | SHORT | RD | - | Sum; CosPhisum3=P0sum3/Ssum3 | [3] | 0.01
3780 | SHORT | RD | - | Power factor; ULN IL | [0] | 0.01
3781 | SHORT | RD | - | Power factor; ULN IL | [1] | 0.01
3782 | SHORT | RD | - | Power factor; ULN IL | [2] | 0.01
3783 | SHORT | RD | - | Sum; Power factor sum3=Psum3/Ssum3 | [3]
3784 | SHORT | RD | % | THD U LN | [0] | 0.1
3785 | SHORT | RD | % | THD U LN | [1] | 0.1
3786 | SHORT | RD | % | THD U LN | [2] | 0.1
3787 | SHORT | RD | % | THD U LL | [0] | 0.1
3788 | SHORT | RD | % | THD U LL | [1] | 0.1
3789 | SHORT | RD | % | THD U LL | [2] | 0.1
3790 | SHORT | RD | V | Voltage, real part U LN | [0] | 0.1
3791 | SHORT | RD | V | Voltage, real part U LN | [1] | 0.1
3792 | SHORT | RD | V | Voltage, real part U LN | [2] | 0.1
3793 | SHORT | RD | V | Voltage, imaginary part U LN | [0] | 0.1
3794 | SHORT | RD | V | Voltage, imaginary part U LN | [1] | 0.1
3795 | SHORT | RD | V | Voltage, imaginary part U LN | [2] | 0.1
3916 | SHORT | RD | mA | Current I L | [0] | 1
3917 | SHORT | RD | mA | Current I L | [1] | 1
3918 | SHORT | RD | mA | Current I L | [2] | 1
3919 | SHORT | RD | mA | Vector sum; IN=I1+I2+I3 | [3] | 1
3920 | SHORT | RD | W | Real power P LN | [0] | 0.1
3921 | SHORT | RD | W | Real power P LN | [1] | 0.1
3922 | SHORT | RD | W | Real power P LN | [2] | 0.1
3923 | SHORT | RD | W | Sum; Psum3=P1+P2+P3 | [3] | 0.1
3924 | SHORT | RD | var | Fund. reactive power Q LN | [0] | 0.1
3925 | SHORT | RD | var | Fund. reactive power Q LN | [1] | 0.1
3926 | SHORT | RD | var | Fund. reactive power Q LN | [2] | 0.1
3927 | SHORT | RD | var | Sum; Qsum3=Q1+Q2+Q3 | [3] | 0.1
3928 | SHORT | RD | VA | Apparent power S LN | [0] | 0.1
3929 | SHORT | RD | VA | Apparent power S LN | [1] | 0.1
3930 | SHORT | RD | VA | Apparent power S LN | [2] | 0.1
3931 | SHORT | RD | VA | Sum; Ssum3=S1+S2+S3 | [3] | 0.1
3932 | SHORT | RD | W | Fund. real power P0 LN | [0] | 0.1
3933 | SHORT | RD | W | Fund. real power P0 LN | [1] | 0.1
3934 | SHORT | RD | W | Fund. real power P0 LN | [2] | 0.1
3935 | SHORT | RD | W | Sum; CosPhisum3=P0sum3/Ssum3 | [3] | 0.1
3936 | SHORT | RD | var | Harmonic distortion power D LN | [0] | 0.1
3937 | SHORT | RD | var | Harmonic distortion power D LN | [1] | 0.1
3938 | SHORT | RD | var | Harmonic distortion power D LN | [2] | 0.1
3939 | SHORT | RD | var | Sum; Dsum3=D1+D2+D3 | [3] | 0.1
3940 | SHORT | RD | % | THD I | [0] | 0.1
3941 | SHORT | RD | % | THD I | [1] | 0.1
3942 | SHORT | RD | % | THD I | [2] | 0.1
3943 | SHORT | RD | % | TDD I | [0] | 0.1
3944 | SHORT | RD | % | TDD I | [1] | 0.1
3945 | SHORT | RD | % | TDD I | [2] | 0.1
3946 | SHORT | RD | mA | Current, zero sequence |  | 1
3947 | SHORT | RD | mA | Current, negative sequence |  | 1
3948 | SHORT | RD | mA | Current, positive sequence |  | 1
3949 | SHORT | RD | mA | Current, real part I L | [0] | 1
3950 | SHORT | RD | mA | Current, real part I L | [1] | 1
3951 | SHORT | RD | mA | Current, real part I L | [2] | 1
3952 | SHORT | RD | mA | Current, imaginary part I L | [0] | 1
3953 | SHORT | RD | mA | Current, imaginary part I L | [1] | 1
3954 | SHORT | RD | mA | Current, imaginary part I L | [2] | 1
3955 | SHORT | RD | - | Rotation field; 1=right, 0=none, -1=left
Mean values, type float
Address | Format | RD/WR | Unit | Note | Index
1720 | FLOAT | RD | Hz | Average, measured frequency
1722 | FLOAT | RD | - | Average, Voltage, zero sequence
1724 | FLOAT | RD | - | Average, Voltage, negative sequence
1726 | FLOAT | RD | - | Average, Voltage, positive sequence
1728 | FLOAT | RD | V | Average, Voltage LN | [0]
1730 | FLOAT | RD | V | Average, Voltage LN | [1]
1732 | FLOAT | RD | V | Average, Voltage LN | [2]
1734 | FLOAT | RD | V | Average, Voltage LL | [0]
1736 | FLOAT | RD | V | Average, Voltage LL | [1]
1738 | FLOAT | RD | V | Average, Voltage LL | [2]
2220 | FLOAT | RD | - | Average, Fund. power factor, CosPhi; ULN IL | [0]
2222 | FLOAT | RD | - | Average, Fund. power factor, CosPhi; ULN IL | [1]
2224 | FLOAT | RD | - | Average, Fund. power factor, CosPhi; ULN IL | [2]
2226 | FLOAT | RD | - | Average, Sum; CosPhisum3=P0sum3/Ssum3 | [3]
2228 | FLOAT | RD | - | Average, Power factor; ULN IL | [0]
2230 | FLOAT | RD | - | Average, Power factor; ULN IL | [1]
2232 | FLOAT | RD | - | Average, Power factor; ULN IL | [2]
2234 | FLOAT | RD | - | Average, Sum; Power factor sum3=Psum3/Ssum3 | [3]
2236 | FLOAT | RD | V | Average, THD, U LN | [0]
2238 | FLOAT | RD | V | Average, THD, U LN | [1]
2240 | FLOAT | RD | V | Average, THD, U LN | [2]
2242 | FLOAT | RD | V | Average, THD, U LL | [0]
2244 | FLOAT | RD | V | Average, THD, U LL | [1]
2246 | FLOAT | RD | V | Average, THD, U LL | [2]
2248 | FLOAT | RD | V | Average, Voltage, real part U LN | [0]
2250 | FLOAT | RD | V | Average, Voltage, real part U LN | [1]
2252 | FLOAT | RD | V | Average, Voltage, real part U LN | [2]
2254 | FLOAT | RD | V | Average, Voltage, imaginary part U LN | [0]
2256 | FLOAT | RD | V | Average, Voltage, imaginary part U LN | [1]
2258 | FLOAT | RD | V | Average, Voltage, imaginary part U LN | [2]
2500 | FLOAT | RD | A | Average, Current IL | [0]
2502 | FLOAT | RD | A | Average, Current IL | [1]
2504 | FLOAT | RD | A | Average, Current IL | [2]
2506 | FLOAT | RD | A | Average, Vector sum; IN=I1+I2+I3 | [3]
2508 | FLOAT | RD | W | Average, Real power P LN | [0]
2510 | FLOAT | RD | W | Average, Real power PLN | [1]
2512 | FLOAT | RD | W | Average, Real power P LN | [2]
2514 | FLOAT | RD | W | Average, Sum; Psum3=P1+P2+P3 | [3]
2516 | FLOAT | RD | var | Average, Fund. reactive power Q LN | [0]
2518 | FLOAT | RD | var | Average, Fund. reactive power Q LN | [1]
2520 | FLOAT | RD | var | Average, Fund. reactive power Q LN | [2]
2522 | FLOAT | RD | var | Average, Sum; Qsum3=Q1+Q2+Q3 | [3]
2524 | FLOAT | RD | VA | Average, Apparent power S LN | [0]
2526 | FLOAT | RD | VA | Average, Apparent power S LN | [1]
2528 | FLOAT | RD | VA | Average, Apparent power S LN | [2]
2530 | FLOAT | RD | VA | Average, Sum; Ssum3=S1+S2+S3 | [3]
2532 | FLOAT | RD | W | Average, Fund. real power P0 LN | [0]
2534 | FLOAT | RD | W | Average, Fund. real power P0 LN | [1]
2536 | FLOAT | RD | W | Average, Fund. real power P0 LN | [2]
2538 | FLOAT | RD | W | Average, Sum; CosPhisum3=P0sum3/Ssum3 | [3]
2540 | FLOAT | RD | var | Average, Harmonic distortion power D LN | [0]
2542 | FLOAT | RD | var | Average, Harmonic distortion power D LN | [1]
2544 | FLOAT | RD | var | Average, Harmonic distortion power D LN | [2]
2546 | FLOAT | RD | var | Average, Sum; Dsum3=D1+D2+D3 | [3]
2548 | FLOAT | RD | % | Average, THD I | [0]
2550 | FLOAT | RD | % | Average, THD I | [1]
2552 | FLOAT | RD | % | Average, THD I | [2]
2554 | FLOAT | RD | % | Average, TDD I | [0]
2556 | FLOAT | RD | % | Average, TDD I | [1]
2558 | FLOAT | RD | % | Average, TDD I | [2]
2560 | FLOAT | RD | - | Average, Current, zero sequence
2562 | FLOAT | RD | - | Average, Current, negative sequence
2564 | FLOAT | RD | - | Average, Current, positive sequence
2566 | FLOAT | RD | A | Average, Current, real part I L | [0]
2568 | FLOAT | RD | A | Average, Current, real part I L | [1]
2570 | FLOAT | RD | A | Average, Current, real part I L | [2]
2572 | FLOAT | RD | A | Average, Current, imaginary part IL | [0]
2574 | FLOAT | RD | A | Average, Current, imaginary part IL | [1]
2576 | FLOAT | RD | A | Average, Current, imaginary part IL | [2]
Mean values, type short
Address | Format | RD/WR | Unit | Note | Index | Resolution
3956 | SHORT | RD | Hz | Average, measured frequency |  | 0.01
3957 | SHORT | RD | V | Average, Voltage, zero sequence |  | 0.1
3958 | SHORT | RD | V | Average, Voltage, negative sequence |  | 0.1
3959 | SHORT | RD | V | Average, Voltage, positive sequence |  | 0.1
3960 | SHORT | RD | V | Average, Voltage L-N | [0] | 0.1
3961 | SHORT | RD | V | Average, Voltage L-N | [1] | 0.1
3962 | SHORT | RD | V | Average, Voltage L-N | [2] | 0.1
3963 | SHORT | RD | V | Average, Voltage L-L | [0] | 0.1
3964 | SHORT | RD | V | Average, Voltage L-L | [1] | 0.1
3965 | SHORT | RD | V | Average, Voltage L-L | [2] | 0.1
4206 | SHORT | RD | - | Average, Fund. power factor, CosPhi; ULN IL | [0] | 0.01
4207 | SHORT | RD | - | Average, Fund. power factor, CosPhi; ULN IL | [1] | 0.01
4208 | SHORT | RD | - | Average, Fund. power factor, CosPhi; ULN IL | [2] | 0.01
4209 | SHORT | RD | - | Average, Sum; CosPhisum3=P0sum3/Ssum3 | [3] | 0.01
4210 | SHORT | RD | - | Average, Power factor; ULN IL | [0] | 0.01
4211 | SHORT | RD | - | Average, Power factor; ULN IL | [1] | 0.01
4212 | SHORT | RD | - | Average, Power factor; ULN IL | [2] | 0.01
4213 | SHORT | RD | - | Average, Sum; Power factor sum3=Psum3/Ssum3 | [3]
4214 | SHORT | RD | % | Average, THD U LN | [0] | 0.1
4215 | SHORT | RD | % | Average, THD U LN | [1] | 0.1
4216 | SHORT | RD | % | Average, THD U LN | [2] | 0.1
4217 | SHORT | RD | % | Average, THD U LL | [0] | 0.1
4218 | SHORT | RD | % | Average, THD U LL | [1] | 0.1
4219 | SHORT | RD | % | Average, THD U LL | [2] | 0.1
4220 | SHORT | RD | V | Average, real part U LN | [0] | 0.1
4221 | SHORT | RD | V | Average, real part U LN | [1] | 0.1
4222 | SHORT | RD | V | Average, real part U LN | [2] | 0.1
4223 | SHORT | RD | V | Average, imaginary part U LN | [0] | 0.1
4224 | SHORT | RD | V | Average, imaginary part U LN | [1] | 0.1
4225 | SHORT | RD | V | Average, imaginary part U LN | [2] | 0.1
4346 | SHORT | RD | mA | Average, Current I L | [0] | 1
4347 | SHORT | RD | mA | Average, Current I L | [1] | 1
4348 | SHORT | RD | mA | Average, Current I L | [2] | 1
4349 | SHORT | RD | mA | Average, Vector sum; IN=I1+I2+I3 | [3] | 1
4350 | SHORT | RD | W | Average, Real power P LN | [0] | 0.1
4351 | SHORT | RD | W | Average, Real power P LN | [1] | 0.1
4352 | SHORT | RD | W | Average, Real power P LN | [2] | 0.1
4353 | SHORT | RD | W | Average, Sum; Psum3=P1+P2+P3 | [3] | 0.1
4354 | SHORT | RD | var | Average, Fund. reactive power Q LN | [0] | 0.1
4355 | SHORT | RD | var | Average, Fund. reactive power Q LN | [1] | 0.1
4356 | SHORT | RD | var | Average, Fund. reactive power Q LN | [2] | 0.1
4357 | SHORT | RD | var | Average, Sum; Qsum3=Q1+Q2+Q3 | [3] | 0.1
4358 | SHORT | RD | VA | Average, Apparent power S LN | [0] | 0.1
4359 | SHORT | RD | VA | Average, Apparent power S LN | [1] | 0.1
4360 | SHORT | RD | VA | Average, Apparent power S LN | [2] | 0.1
4361 | SHORT | RD | VA | Average, Sum; Ssum3=S1+S2+S3 | [3] | 0.1
4362 | SHORT | RD | W | Average, Fund. real power P0 LN | [0] | 0.1
4363 | SHORT | RD | W | Average, Fund. real power P0 LN | [1] | 0.1
4364 | SHORT | RD | W | Average, Fund. real power P0 LN | [2] | 0.1
4365 | SHORT | RD | W | Average, Sum; CosPhisum3=P0sum3/Ssum3 | [3] | 0.1
4366 | SHORT | RD | var | Average, Harmonic distortion power D LN | [0] | 0.1
4367 | SHORT | RD | var | Average, Harmonic distortion power D LN | [1] | 0.1
4368 | SHORT | RD | var | Average, Harmonic distortion power D LN | [2] | 0.1
4369 | SHORT | RD | var | Average, Sum; Dsum3=D1+D2+D3 | [3] | 0.1
4370 | SHORT | RD | % | Average, THD I | [0] | 0.1
4371 | SHORT | RD | % | Average, THD I | [1] | 0.1
4372 | SHORT | RD | % | Average, THD I | [2] | 0.1
4373 | SHORT | RD | % | Average, TDD I | [0] | 0.1
4374 | SHORT | RD | % | Average, TDD I | [1] | 0.1
4375 | SHORT | RD | % | Average, TDD I | [2] | 0.1
4376 | SHORT | RD | mA | Average, Current, zero sequence |  | 1
4377 | SHORT | RD | mA | Average, Current, negative sequence |  | 1
4378 | SHORT | RD | mA | Average, Current, positive sequence |  | 1
4379 | SHORT | RD | mA | Average, Current, real part I L | [0] | 1
4380 | SHORT | RD | mA | Average, Current, real part I L | [1] | 1
4381 | SHORT | RD | mA | Average, Current, real part I L | [2] | 1
4382 | SHORT | RD | A | Average, Current, imaginary part I L | [0] | 1
4383 | SHORT | RD | A | Average, Current, imaginary part I L | [1] | 1
4384 | SHORT | RD | A | Average, Current, imaginary part I L | [2] | 1
Minimum values, type float
Address | Format | RD/WR | Unit | Note | Index
3436 | FLOAT | RD/WR | Hz | Minimum, measured frequency
3438 | FLOAT | RD/WR | - | Minimum, Voltage, zero sequence
3440 | FLOAT | RD/WR | - | Minimum, Voltage, negative sequence
3442 | FLOAT | RD/WR | - | Minimum, Voltage, positive sequence
3444 | FLOAT | RD/WR | V | Minimum, Voltage L-N | [0]
3446 | FLOAT | RD/WR | V | Minimum, Voltage L-N | [1]
3448 | FLOAT | RD/WR | V | Minimum, Voltage L-N | [2]
3450 | FLOAT | RD/WR | V | Minimum, Voltage L-L | [0]
3452 | FLOAT | RD/WR | V | Minimum, Voltage L-L | [1]
3454 | FLOAT | RD/WR | V | Minimum, Voltage L-L | [2]
3456 | FLOAT | RD/WR | - | Minimum, Fund. power factor, CosPhi; ULN IL | [0]
3458 | FLOAT | RD/WR | - | Minimum, Fund. power factor, CosPhi; ULN IL | [1]
3460 | FLOAT | RD/WR | - | Minimum, Fund. power factor, CosPhi; ULN IL | [2]
3462 | FLOAT | RD/WR | - | Minimum, Sum; CosPhisum3=P0sum3/Ssum3 | [3]
3464 | FLOAT | RD/WR | - | Minimum, Power factor; ULN I L | [0]
3466 | FLOAT | RD/WR | - | Minimum, Power factor; ULN I L | [1]
3468 | FLOAT | RD/WR | - | Minimum, Power factor; ULN I L | [2]
3470 | FLOAT | RD/WR | - | Minimum, Sum; Power factor sum3=Psum3/Ssum3 | [3]
3472 | FLOAT | RD/WR | % | Minimum, THD U LN | [0]
3474 | FLOAT | RD/WR | % | Minimum, THD U LN | [1]
3476 | FLOAT | RD/WR | % | Minimum, THD U LN | [2]
3478 | FLOAT | RD/WR | % | Minimum, THD U LL | [0]
3480 | FLOAT | RD/WR | % | Minimum, THD U LL | [1]
3482 | FLOAT | RD/WR | % | Minimum, THD U LL | [2]
3484 | FLOAT | RD/WR | V | Minimum, Voltage, real part U LN | [0]
3486 | FLOAT | RD/WR | V | Minimum, Voltage, real part U LN | [1]
3488 | FLOAT | RD/WR | V | Minimum, Voltage, real part U LN | [2]
3490 | FLOAT | RD/WR | V | Minimum, Voltage, imaginary part U LN | [0]
3492 | FLOAT | RD/WR | V | Minimum, Voltage, imaginary part U LN | [1]
3494 | FLOAT | RD/WR | V | Minimum, Voltage, imaginary part U LN | [2]
Minimum values, type short
Address | Format | RD/WR | Unit | Note | Index | Resolution
4814 | SHORT | RD/WR | Hz | measured frequency |  | 0.01
4815 | SHORT | RD/WR | V | Voltage, zero sequence |  | 0.1
4816 | SHORT | RD/WR | V | Voltage, negative sequence |  | 0.1
4817 | SHORT | RD/WR | V | Voltage, positive sequence |  | 0.1
4818 | SHORT | RD/WR | V | Voltage L-N | [0] | 0.1
4819 | SHORT | RD/WR | V | Voltage L-N | [1] | 0.1
4820 | SHORT | RD/WR | V | Voltage L-N | [2] | 0.1
4821 | SHORT | RD/WR | V | Voltage L-L | [0] | 0.1
4822 | SHORT | RD/WR | V | Voltage L-L | [1] | 0.1
4823 | SHORT | RD/WR | V | Voltage L-L | [2] | 0.1
4824 | SHORT | RD/WR | - | Fund. power factor, CosPhi; ULN IL | [0] | 0.01
4825 | SHORT | RD/WR | - | Fund. power factor, CosPhi; ULN IL | [1] | 0.01
4826 | SHORT | RD/WR | - | Fund. power factor, CosPhi; ULN IL | [2] | 0.01
4827 | SHORT | RD/WR | - | Sum; CosPhi sum3=P0sum3/Ssum3 | [3] | 0.01
4828 | SHORT | RD/WR | - | Power factor; ULN IL | [0] | 0.01
4829 | SHORT | RD/WR | - | Power factor; ULN IL | [1] | 0.01
4830 | SHORT | RD/WR | - | Power factor; ULN IL | [2] | 0.01
4831 | SHORT | RD/WR | - | Sum; Power factor sum3=Psum3/Ssum3 | [3]
4832 | SHORT | RD/WR | % | THD U LN | [0] | 0.1
4833 | SHORT | RD/WR | % | THD U LN | [1] | 0.1
4834 | SHORT | RD/WR | % | THD U LN | [2] | 0.1
4835 | SHORT | RD/WR | % | THD U LL | [0] | 0.1
4836 | SHORT | RD/WR | % | THD U LL | [1] | 0.1
4837 | SHORT | RD/WR | % | THD U LL | [2] | 0.1
4838 | SHORT | RD/WR | V | Voltage, real part U LN | [0] | 0.1
4839 | SHORT | RD/WR | V | Voltage, real part U LN | [1] | 0.1
4840 | SHORT | RD/WR | V | Voltage, real part U LN | [2] | 0.1
4841 | SHORT | RD/WR | V | Voltage, imaginary part U LN | [0] | 0.1
4842 | SHORT | RD/WR | V | Voltage, imaginary part U LN | [1] | 0.1
4843 | SHORT | RD/WR | V | Voltage, imaginary part U LN | [2] | 0.1
Maximum values, type float
Address | Format | RD/WR | Unit | Note | Index
2578 | FLOAT | RD/WR | Hz | Maximum, measured frequency
2580 | FLOAT | RD/WR | - | Maximum, Voltage, zero sequence
2582 | FLOAT | RD/WR | - | Maximum, Voltage, negative sequence
2584 | FLOAT | RD/WR | - | Maximum, Voltage, positive sequence
2586 | FLOAT | RD/WR | V | Maximum, Voltage L-N | [0]
2588 | FLOAT | RD/WR | V | Maximum, Voltage L-N | [1]
2590 | FLOAT | RD/WR | V | Maximum, Voltage L-N | [2]
2592 | FLOAT | RD/WR | V | Maximum, Voltage L-L | [0]
2594 | FLOAT | RD/WR | V | Maximum, Voltage L-L | [1]
2596 | FLOAT | RD/WR | V | Maximum, Voltage L-L | [2]
3078 | FLOAT | RD/WR | - | Maximum, Fund. power factor, CosPhi; ULN IL | [0]
3080 | FLOAT | RD/WR | - | Maximum, Fund. power factor, CosPhi; ULN IL | [1]
3082 | FLOAT | RD/WR | - | Maximum, Fund. power factor, CosPhi; ULN IL | [2]
3084 | FLOAT | RD/WR | - | Maximum, Sum; CosPhisum3=P0sum3/Ssum3 | [3]
3086 | FLOAT | RD/WR | - | Maximum, Power factor; ULN IL | [0]
3088 | FLOAT | RD/WR | - | Maximum, Power factor; ULN IL | [1]
3090 | FLOAT | RD/WR | - | Maximum, Power factor; ULN IL | [2]
3092 | FLOAT | RD/WR | - | Maximum, Sum; Power factor sum3=Psum3/Ssum | [3]
3094 | FLOAT | RD/WR | % | Maximum, THD, U LN | [0]
3096 | FLOAT | RD/WR | % | Maximum, THD, U LN | [1]
3098 | FLOAT | RD/WR | % | Maximum, THD, U LN | [2]
3100 | FLOAT | RD/WR | % | Maximum, THD, U LL | [0]
3102 | FLOAT | RD/WR | % | Maximum, THD, U LL | [1]
3104 | FLOAT | RD/WR | % | Maximum, THD, U LL | [2]
3106 | FLOAT | RD/WR | V | Maximum, Voltage, real part U LN | [0]
3108 | FLOAT | RD/WR | V | Maximum, Voltage, real part U LN | [1]
3110 | FLOAT | RD/WR | V | Maximum, Voltage, real part U LN | [2]
3112 | FLOAT | RD/WR | V | Maximum, Voltage, imaginary part U LN | [0]
3114 | FLOAT | RD/WR | V | Maximum, Voltage, imaginary part U LN | [1]
3116 | FLOAT | RD/WR | V | Maximum, Voltage, imaginary part U LN | [2]
3358 | FLOAT | RD/WR | A | Maximum, Current I L | [0]
3360 | FLOAT | RD/WR | A | Maximum, Current I L | [1]
3362 | FLOAT | RD/WR | A | Maximum, Current I L | [2]
3364 | FLOAT | RD/WR | A | Maximum, Vector sum; IN=I1+I2+I3 | [3]
3366 | FLOAT | RD/WR | W | Maximum, Real power P LN | [0]
3368 | FLOAT | RD/WR | W | Maximum, Real power P LN | [1]
3370 | FLOAT | RD/WR | W | Maximum, Real power P LN | [2]
3372 | FLOAT | RD/WR | W | Maximum, Sum; Psum3=P1+P2+P3 | [3]
3374 | FLOAT | RD/WR | var | Maximum, Fund. reactive power Q LN | [0]
3376 | FLOAT | RD/WR | var | Maximum, Fund. reactive power Q LN | [1]
3378 | FLOAT | RD/WR | var | Maximum, Fund. reactive power Q LN | [2]
3380 | FLOAT | RD/WR | var | Maximum, Sum; Qsum3=Q1+Q2+Q3 | [3]
3382 | FLOAT | RD/WR | VA | Maximum, Average, Apparent power S LN | [0]
3384 | FLOAT | RD/WR | VA | Maximum, Average, Apparent power S LN | [1]
3386 | FLOAT | RD/WR | VA | Maximum, Average, Apparent power S LN | [2]
3388 | FLOAT | RD/WR | VA | Maximum, Average, Sum; Ssum3=S1+S2+S3 | [3]
3390 | FLOAT | RD/WR | W | Maximum, Fund. real power P0 LN | [0]
3392 | FLOAT | RD/WR | W | Maximum, Fund. real power P0 LN | [1]
3394 | FLOAT | RD/WR | W | Maximum, Fund. real power P0 LN | [2]
3396 | FLOAT | RD/WR | W | Maximum, Sum; P0sum3=P01+P02+P03 | [3]
3398 | FLOAT | RD/WR | var | Maximum, Harmonic distortion power D LN | [0]
3400 | FLOAT | RD/WR | var | Maximum, Harmonic distortion power D LN | [1]
3402 | FLOAT | RD/WR | var | Maximum, Harmonic distortion power D LN | [2]
3404 | FLOAT | RD/WR | var | Maximum, Sum; Dsum3=D1+D2+D3 | [3]
3406 | FLOAT | RD/WR | A | Maximum, THD I | [0]
3408 | FLOAT | RD/WR | A | Maximum, THD I | [1]
3410 | FLOAT | RD/WR | A | Maximum, THD I | [2]
3412 | FLOAT | RD/WR | A | Maximum, TDD I | [0]
3414 | FLOAT | RD/WR | A | Maximum, TDD I | [1]
3416 | FLOAT | RD/WR | A | Maximum, TDD I | [2]
3418 | FLOAT | RD/WR | - | Maximum, Current, zero sequence
3420 | FLOAT | RD/WR | - | Maximum, Current, negative sequence
3422 | FLOAT | RD/WR | - | Maximum, positive sequence
3424 | FLOAT | RD/WR | A | Maximum, real part I L | [0]
3426 | FLOAT | RD/WR | A | Maximum, real part I L | [1]
3428 | FLOAT | RD/WR | A | Maximum, real part I L | [2]
3430 | FLOAT | RD/WR | A | Maximum, imaginary part I L | [0]
3432 | FLOAT | RD/WR | A | Maximum, imaginary part I L | [1]
3434 | FLOAT | RD/WR | A | Maximum, imaginary part I L | [2]
Maximum values, type short
Address | Format | RD/WR | Unit | Note | Index | Resolution
4385 | SHORT | RD/WR | Hz | Maximum, measured frequency |  | 0.01
4386 | SHORT | RD/WR | V | Maximum, Voltage, zero sequence |  | 0.1
4387 | SHORT | RD/WR | V | Maximum, Voltage, negative sequence |  | 0.1
4388 | SHORT | RD/WR | V | Maximum, Voltage, positive sequence |  | 0.1
4389 | SHORT | RD/WR | V | Maximum, Voltage L-N | [0] | 0.1
4390 | SHORT | RD/WR | V | Maximum, Voltage L-N | [1] | 0.1
4391 | SHORT | RD/WR | V | Maximum, Voltage L-N | [2] | 0.1
4392 | SHORT | RD/WR | V | Maximum, Voltage L-L | [0] | 0.1
4393 | SHORT | RD/WR | V | Maximum, Voltage L-L | [1] | 0.1
4394 | SHORT | RD/WR | V | Maximum, Voltage L-L | [2] | 0.1
4635 | SHORT | RD/WR | - | Maximum, Fund. power factor, CosPhi; ULN IL | [0] | 0.01
4636 | SHORT | RD/WR | - | Maximum, Fund. power factor, CosPhi; ULN IL | [1] | 0.01
4637 | SHORT | RD/WR | - | Maximum, Fund. power factor, CosPhi; ULN IL | [2] | 0.01
4638 | SHORT | RD/WR | - | Maximum, Sum; CosPhisum3=P0sum3/Ssum3 | [3] | 0.01
4639 | SHORT | RD/WR | - | Maximum, Power factor; ULN IL | [0] | 0.01
4640 | SHORT | RD/WR | - | Maximum, Power factor; ULN IL | [1] | 0.01
4641 | SHORT | RD/WR | - | Maximum, Power factor; ULN IL | [2] | 0.01
4642 | SHORT | RD/WR | - | Maximum, Sum; Power factor sum3=Psum3/Ssum3 | [3]
4643 | SHORT | RD/WR | % | Maximum, THD U LN | [0] | 0.1
4644 | SHORT | RD/WR | % | Maximum, THD U LN | [1] | 0.1
4645 | SHORT | RD/WR | % | Maximum, THD U LN | [2] | 0.1
4646 | SHORT | RD/WR | % | Maximum, THD U LL | [0] | 0.1
4647 | SHORT | RD/WR | % | Maximum, THD U LL | [1] | 0.1
4648 | SHORT | RD/WR | % | Maximum, THD U LL | [2] | 0.1
4649 | SHORT | RD/WR | V | Maximum, real part U LN | [0] | 0.1
4650 | SHORT | RD/WR | V | Maximum, real part U LN | [1] | 0.1
4651 | SHORT | RD/WR | V | Maximum, real part U LN | [2] | 0.1
4652 | SHORT | RD/WR | V | Maximum, imaginary part U LN | [0] | 0.1
4653 | SHORT | RD/WR | V | Maximum, imaginary part U LN | [1] | 0.1
4654 | SHORT | RD/WR | V | Maximum, imaginary part U LN | [2] | 0.1
4775 | SHORT | RD/WR | mA | Maximum, Current I L | [0] | 1
4776 | SHORT | RD/WR | mA | Maximum, Current I L | [1] | 1
4777 | SHORT | RD/WR | mA | Maximum, Current I L | [2] | 1
4778 | SHORT | RD/WR | mA | Maximum, Vector sum; IN=I1+I2+I3 | [3] | 1
4779 | SHORT | RD/WR | W | Maximum, Real power P LN | [0] | 0.1
4780 | SHORT | RD/WR | W | Maximum, Real power P LN | [1] | 0.1
4781 | SHORT | RD/WR | W | Maximum, Real power P LN | [2] | 0.1
4782 | SHORT | RD/WR | W | Maximum, Sum; Psum3=P1+P2+P3 | [3] | 0.1
4783 | SHORT | RD/WR | var | Maximum, Fund. reactive power Q LN | [0] | 0.1
4784 | SHORT | RD/WR | var | Maximum, Fund. reactive power Q LN | [1] | 0.1
4785 | SHORT | RD/WR | var | Maximum, Fund. reactive power Q LN | [2] | 0.1
4786 | SHORT | RD/WR | var | Maximum, Sum; Qsum3=Q1+Q2+Q3 | [3] | 0.1
4787 | SHORT | RD/WR | VA | Maximum, Apparent power S LN | [0] | 0.1
4788 | SHORT | RD/WR | VA | Maximum, Apparent power S LN | [1] | 0.1
4789 | SHORT | RD/WR | VA | Maximum, Apparent power S LN | [2] | 0.1
4790 | SHORT | RD/WR | VA | Maximum, Sum; Ssum3=S1+S2+S3 | [3] | 0.1
4791 | SHORT | RD/WR | W | Maximum, Fund. real power P0 LN | [0] | 0.1
4792 | SHORT | RD/WR | W | Maximum, Fund. real power P0 LN | [1] | 0.1
4793 | SHORT | RD/WR | W | Maximum, Fund. real power P0 LN | [2] | 0.1
4794 | SHORT | RD/WR | W | Maximum, Sum; P0sum3=P01+P02+P03 | [3] | 0.1
4795 | SHORT | RD/WR | var | Maximum, Harmonic distortion power D LN | [0] | 0.1
4796 | SHORT | RD/WR | var | Maximum, Harmonic distortion power D LN | [1] | 0.1
4797 | SHORT | RD/WR | var | Maximum, Harmonic distortion power D LN | [2] | 0.1
4798 | SHORT | RD/WR | var | Maximum, Sum; Dsum3=D1+D2+D3 | [3] | 0.1
4799 | SHORT | RD/WR | % | Maximum, THD I | [0] | 0.1
4800 | SHORT | RD/WR | % | Maximum, THD I | [1] | 0.1
4801 | SHORT | RD/WR | % | Maximum, THD I | [2] | 0.1
4802 | SHORT | RD/WR | % | Maximum, TDD I | [0] | 0.1
4803 | SHORT | RD/WR | % | Maximum, TDD I | [1] | 0.1
4804 | SHORT | RD/WR | % | Maximum, TDD I | [2] | 0.1
4805 | SHORT | RD/WR | mA | Maximum, Current, zero sequence |  | 1
4806 | SHORT | RD/WR | mA | Maximum, Current, negative sequence |  | 1
4807 | SHORT | RD/WR | mA | Maximum, Current, positive sequence |  | 1
4808 | SHORT | RD/WR | mA | Maximum, Current, real part IL | [0] | 1
4809 | SHORT | RD/WR | mA | Maximum, Current, real part IL | [1] | 1
4810 | SHORT | RD/WR | mA | Maximum, Current, real part IL | [2] | 1
4811 | SHORT | RD/WR | mA | Maximum, Current, imaginary part I L | [0] | 1
4812 | SHORT | RD/WR | mA | Maximum, Current, imaginary part I L | [1] | 1
4813 | SHORT | RD/WR | mA | Maximum, Current, imaginary part I L | [2] | 1
Maximum values of mean values, type float
Address | Format | RD/WR | Unit | Note | Index
3496 | FLOAT | RD/WR | A | Max. values of average val., Current I L | [0]
3498 | FLOAT | RD/WR | A | Max. values of average val., Current I L | [1]
3500 | FLOAT | RD/WR | A | Max. values of average val., Current I L | [2]
3502 | FLOAT | RD/WR | A | Max. values of average val., Vector sum; IN=I1+I2+I3 | [3]
3504 | FLOAT | RD/WR | W | Max. values of average val., Real power P LN | [0]
3506 | FLOAT | RD/WR | W | Max. values of average val., Real power P LN | [1]
3508 | FLOAT | RD/WR | W | Max. values of average val., Real power P LN | [2]
3510 | FLOAT | RD/WR | W | Max. values of average val., Sum; Psum3=P1+P2+P3 | [3]
Maximum values of mean values, type short
Address | Format | RD/WR | Unit | Note | Index | Resolution
4844 | SHORT | RD/WR | mA | Max. value of average val., Current I L | [0] | 1
4845 | SHORT | RD/WR | mA | Max. value of average val., Current I L | [1] | 1
4846 | SHORT | RD/WR | mA | Max. value of average val., Current I L | [2] | 1
4847 | SHORT | RD/WR | mA | Max. value of average val., Vector sum; IN=I1+I2+I3 | [3] | 1
4848 | SHORT | RD/WR | W | Max. value of average val., Real power P LN | [0] | 0.1
4849 | SHORT | RD/WR | W | Max. value of average val., Real power P LN | [1] | 0.1
4850 | SHORT | RD/WR | W | Max. value of average val., Real power P LN | [2] | 0.1
4851 | SHORT | RD/WR | W | Max. value of average val., Sum; Psum3=P1+P2+P3 | [3] | 0.1
Energy, type Integer
The energy values in integer format do not provide any current- and voltage transformer ratios.
Address | Format | RD/WR | Unit | Note | Index
5448 | INT | RD | Wh | Real energy, L1, rate | [0]
5450 | INT | RD | Wh | Real energy, L1, rate | [1]
5452 | INT | RD | Wh | Real energy, L1, rate | [2]
5454 | INT | RD | Wh | Real energy, L1, rate | [3]
5456 | INT | RD | Wh | Real energy, L1, rate | [4]
5458 | INT | RD | Wh | Real energy, L1, rate | [5]
5460 | INT | RD | Wh | Real energy, L1, rate | [6]
5462 | INT | RD | Wh | Real energy, L1, rate | [7]
5464 | INT | RD | Wh | Real energy, L1, obtained, rate | [0]
5466 | INT | RD | Wh | Real energy, L1, obtained, rate | [1]
5468 | INT | RD | Wh | Real energy, L1, obtained, rate | [2]
5470 | INT | RD | Wh | Real energy, L1, obtained, rate | [3]
5472 | INT | RD | Wh | Real energy, L1, obtained, rate | [4]
5474 | INT | RD | Wh | Real energy, L1, obtained, rate | [5]
5476 | INT | RD | Wh | Real energy, L1, obtained, rate | [6]
5478 | INT | RD | Wh | Real energy, L1, obtained, rate | [7]
5480 | INT | RD | Wh | Real energy, L1, supplied, rate | [0]
5482 | INT | RD | Wh | Real energy, L1, supplied, rate | [1]
5484 | INT | RD | Wh | Real energy, L1, supplied, rate | [2]
5486 | INT | RD | Wh | Real energy, L1, supplied, rate | [3]
5488 | INT | RD | Wh | Real energy, L1, supplied, rate | [4]
5490 | INT | RD | Wh | Real energy, L1, supplied, rate | [5]
5492 | INT | RD | Wh | Real energy, L1, supplied, rate | [6]
5494 | INT | RD | Wh | Real energy, L1, supplied, rate | [7]
5496 | INT | RD | varh | Reactive energy, L1, rate | [0]
5498 | INT | RD | varh | Reactive energy, L1, rate | [1]
5500 | INT | RD | varh | Reactive energy, L1, rate | [2]
5502 | INT | RD | varh | Reactive energy, L1, rate | [3]
5504 | INT | RD | varh | Reactive energy, L1, rate | [4]
5506 | INT | RD | varh | Reactive energy, L1, rate | [5]
5508 | INT | RD | varh | Reactive energy, L1, rate | [6]
5510 | INT | RD | varh | Reactive energy, L1, rate | [7]
5512 | INT | RD | varh | Reactive energy, L1, ind., rate | [0]
5514 | INT | RD | varh | Reactive energy, L1, ind., rate | [1]
5516 | INT | RD | varh | Reactive energy, L1, ind., rate | [2]
5518 | INT | RD | varh | Reactive energy, L1, ind., rate | [3]
5520 | INT | RD | varh | Reactive energy, L1, ind., rate | [4]
5522 | INT | RD | varh | Reactive energy, L1, ind., rate | [5]
5524 | INT | RD | varh | Reactive energy, L1, ind., rate | [6]
5526 | INT | RD | varh | Reactive energy, L1, ind., rate | [7]
5528 | INT | RD | varh | Reactive energy, L1, cap., rate | [0]
5530 | INT | RD | varh | Reactive energy, L1, cap., rate | [1]
5532 | INT | RD | varh | Reactive energy, L1, cap., rate | [2]
5534 | INT | RD | varh | Reactive energy, L1, cap., rate | [3]
5536 | INT | RD | varh | Reactive energy, L1, cap., rate | [4]
5538 | INT | RD | varh | Reactive energy, L1, cap., rate | [5]
5540 | INT | RD | varh | Reactive energy, L1, cap., rate | [6]
5542 | INT | RD | varh | Reactive energy, L1, cap., rate | [7]
5544 | INT | RD | VAh | Apparent energy, L1, rate | [0]
5546 | INT | RD | VAh | Apparent energy, L1, rate | [1]
5548 | INT | RD | VAh | Apparent energy, L1, rate | [2]
5550 | INT | RD | VAh | Apparent energy, L1, rate | [3]
5552 | INT | RD | VAh | Apparent energy, L1, rate | [4]
5554 | INT | RD | VAh | Apparent energy, L1, rate | [5]
5556 | INT | RD | VAh | Apparent energy, L1, rate | [6]
5558 | INT | RD | VAh | Apparent energy, L1, rate | [7]
5560 | INT | RD | Wh | Real energy, L2, rate | [0]
5562 | INT | RD | Wh | Real energy, L2, rate | [1]
5564 | INT | RD | Wh | Real energy, L2, rate | [2]
5566 | INT | RD | Wh | Real energy, L2, rate | [3]
5568 | INT | RD | Wh | Real energy, L2, rate | [4]
5570 | INT | RD | Wh | Real energy, L2, rate | [5]
5572 | INT | RD | Wh | Real energy, L2, rate | [6]
5574 | INT | RD | Wh | Real energy, L2, rate | [7]
5576 | INT | RD | Wh | Real energy, L2, obtained, rate | [0]
5578 | INT | RD | Wh | Real energy, L2, obtained, rate | [1]
5580 | INT | RD | Wh | Real energy, L2, obtained, rate | [2]
5582 | INT | RD | Wh | Real energy, L2, obtained, rate | [3]
5584 | INT | RD | Wh | Real energy, L2, obtained, rate | [4]
5586 | INT | RD | Wh | Real energy, L2, obtained, rate | [5]
5588 | INT | RD | Wh | Real energy, L2, obtained, rate | [6]
5590 | INT | RD | Wh | Real energy, L2, obtained, rate | [7]
5592 | INT | RD | Wh | Real energy, L2, supplied, rate | [0]
5594 | INT | RD | Wh | Real energy, L2, supplied, rate | [1]
5596 | INT | RD | Wh | Real energy, L2, supplied, rate | [2]
5598 | INT | RD | Wh | Real energy, L2, supplied, rate | [3]
5600 | INT | RD | Wh | Real energy, L2, supplied, rate | [4]
5602 | INT | RD | Wh | Real energy, L2, supplied, rate | [5]
5604 | INT | RD | Wh | Real energy, L2, supplied, rate | [6]
5606 | INT | RD | Wh | Real energy, L2, supplied, rate | [7]
5608 | INT | RD | varh | Reactive energy, L2, rate | [0]
5610 | INT | RD | varh | Reactive energy, L2, rate | [1]
5612 | INT | RD | varh | Reactive energy, L2, rate | [2]
5614 | INT | RD | varh | Reactive energy, L2, rate | [3]
5616 | INT | RD | varh | Reactive energy, L2, rate | [4]
5618 | INT | RD | varh | Reactive energy, L2, rate | [5]
5620 | INT | RD | varh | Reactive energy, L2, rate | [6]
5622 | INT | RD | varh | Reactive energy, L2, rate | [7]
5624 | INT | RD | varh | Reactive energy, L2, ind., rate | [0]
5626 | INT | RD | varh | Reactive energy, L2, ind., rate | [1]
5628 | INT | RD | varh | Reactive energy, L2, ind., rate | [2]
5630 | INT | RD | varh | Reactive energy, L2, ind., rate | [3]
5632 | INT | RD | varh | Reactive energy, L2, ind., rate | [4]
5634 | INT | RD | varh | Reactive energy, L2, ind., rate | [5]
5636 | INT | RD | varh | Reactive energy, L2, ind., rate | [6]
5638 | INT | RD | varh | Reactive energy, L2, ind., rate | [7]
5640 | INT | RD | varh | Reactive energy, L2, cap., rate | [0]
5642 | INT | RD | varh | Reactive energy, L2, cap., rate | [1]
5644 | INT | RD | varh | Reactive energy, L2, cap., rate | [2]
5646 | INT | RD | varh | Reactive energy, L2, cap., rate | [3]
5648 | INT | RD | varh | Reactive energy, L2, cap., rate | [4]
5650 | INT | RD | varh | Reactive energy, L2, cap., rate | [5]
5652 | INT | RD | varh | Reactive energy, L2, cap., rate | [6]
5654 | INT | RD | varh | Reactive energy, L2, cap., rate | [7]
5656 | INT | RD | VAh | Apparent energy, L2, rate | [0]
5658 | INT | RD | VAh | Apparent energy, L2, rate | [1]
5660 | INT | RD | VAh | Apparent energy, L2, rate | [2]
5662 | INT | RD | VAh | Apparent energy, L2, rate | [3]
5664 | INT | RD | VAh | Apparent energy, L2, rate | [4]
5666 | INT | RD | VAh | Apparent energy, L2, rate | [5]
5668 | INT | RD | VAh | Apparent energy, L2, rate | [6]
5670 | INT | RD | VAh | Apparent energy, L2, rate | [7]
5672 | INT | RD | Wh | Real energy, L3, rate | [0]
5674 | INT | RD | Wh | Real energy, L3, rate | [1]
5676 | INT | RD | Wh | Real energy, L3, rate | [2]
5678 | INT | RD | Wh | Real energy, L3, rate | [3]
5680 | INT | RD | Wh | Real energy, L3, rate | [4]
5682 | INT | RD | Wh | Real energy, L3, rate | [5]
5684 | INT | RD | Wh | Real energy, L3, rate | [6]
5686 | INT | RD | Wh | Real energy, L3, rate | [7]
5688 | INT | RD | Wh | Real energy, L3, obtained, rate | [0]
5690 | INT | RD | Wh | Real energy, L3, obtained, rate | [1]
5692 | INT | RD | Wh | Real energy, L3, obtained, rate | [2]
5694 | INT | RD | Wh | Real energy, L3, obtained, rate | [3]
5696 | INT | RD | Wh | Real energy, L3, obtained, rate | [4]
5698 | INT | RD | Wh | Real energy, L3, obtained, rate | [5]
5700 | INT | RD | Wh | Real energy, L3, obtained, rate | [6]
5702 | INT | RD | Wh | Real energy, L3, obtained, rate | [7]
5704 | INT | RD | Wh | Real energy, L3, supplied, rate | [0]
5706 | INT | RD | Wh | Real energy, L3, supplied, rate | [1]
5708 | INT | RD | Wh | Real energy, L3, supplied, rate | [2]
5710 | INT | RD | Wh | Real energy, L3, supplied, rate | [3]
5712 | INT | RD | Wh | Real energy, L3, supplied, rate | [4]
5714 | INT | RD | Wh | Real energy, L3, supplied, rate | [5]
5716 | INT | RD | Wh | Real energy, L3, supplied, rate | [6]
5718 | INT | RD | Wh | Real energy, L3, supplied, rate | [7]
5720 | INT | RD | varh | Reactive energy, L3, rate | [0]
5722 | INT | RD | varh | Reactive energy, L3, rate | [1]
5724 | INT | RD | varh | Reactive energy, L3, rate | [2]
5726 | INT | RD | varh | Reactive energy, L3, rate | [3]
5728 | INT | RD | varh | Reactive energy, L3, rate | [4]
5730 | INT | RD | varh | Reactive energy, L3, rate | [5]
5732 | INT | RD | varh | Reactive energy, L3, rate | [6]
5734 | INT | RD | varh | Reactive energy, L3, rate | [7]
5736 | INT | RD | varh | Reactive energy, L3, ind., rate | [0]
5738 | INT | RD | varh | Reactive energy, L3, ind., rate | [1]
5740 | INT | RD | varh | Reactive energy, L3, ind., rate | [2]
5742 | INT | RD | varh | Reactive energy, L3, ind., rate | [3]
5744 | INT | RD | varh | Reactive energy, L3, ind., rate | [4]
5746 | INT | RD | varh | Reactive energy, L3, ind., rate | [5]
5748 | INT | RD | varh | Reactive energy, L3, ind., rate | [6]
5750 | INT | RD | varh | Reactive energy, L3, ind., rate | [7]
5752 | INT | RD | varh | Reactive energy, L3, cap., rate | [0]
5754 | INT | RD | varh | Reactive energy, L3, cap., rate | [1]
5756 | INT | RD | varh | Reactive energy, L3, cap., rate | [2]
5758 | INT | RD | varh | Reactive energy, L3, cap., rate | [3]
5760 | INT | RD | varh | Reactive energy, L3, cap., rate | [4]
5762 | INT | RD | varh | Reactive energy, L3, cap., rate | [5]
5764 | INT | RD | varh | Reactive energy, L3, cap., rate | [6]
5766 | INT | RD | varh | Reactive energy, L3, cap., rate | [7]
5768 | INT | RD | VAh | Apparent energy, L3, rate | [0]
5770 | INT | RD | VAh | Apparent energy, L3, rate | [1]
5772 | INT | RD | VAh | Apparent energy, L3, rate | [2]
5774 | INT | RD | VAh | Apparent energy, L3, rate | [3]
5776 | INT | RD | VAh | Apparent energy, L3, rate | [4]
5778 | INT | RD | VAh | Apparent energy, L3, rate | [5]
5780 | INT | RD | VAh | Apparent energy, L3, rate | [6]
5782 | INT | RD | VAh | Apparent energy, L3, rate | [7]
5784 | INT | RD | Wh | Real energy, sum. L1..L3, rate | [0]
5786 | INT | RD | Wh | Real energy, sum. L1..L3, rate | [1]
5788 | INT | RD | Wh | Real energy, sum. L1..L3, rate | [2]
5790 | INT | RD | Wh | Real energy, sum. L1..L3, rate | [3]
5792 | INT | RD | Wh | Real energy, sum. L1..L3, rate | [4]
5794 | INT | RD | Wh | Real energy, sum. L1..L3, rate | [5]
5796 | INT | RD | Wh | Real energy, sum. L1..L3, rate | [6]
5798 | INT | RD | Wh | Real energy, sum. L1..L3, rate | [7]
5800 | INT | RD | Wh | Real energy, sum. L1..L3, obtained, rate | [0]
5802 | INT | RD | Wh | Real energy, sum. L1..L3, obtained, rate | [1]
5804 | INT | RD | Wh | Real energy, sum. L1..L3, obtained, rate | [2]
5806 | INT | RD | Wh | Real energy, sum. L1..L3, obtained, rate | [3]
5808 | INT | RD | Wh | Real energy, sum. L1..L3, obtained, rate | [4]
5810 | INT | RD | Wh | Real energy, sum. L1..L3, obtained, rate | [5]
5812 | INT | RD | Wh | Real energy, sum. L1..L3, obtained, rate | [6]
5814 | INT | RD | Wh | Real energy, sum. L1..L3, obtained, rate | [7]
5816 | INT | RD | Wh | Real energy, sum. L1..L3, supplied, rate | [0]
5818 | INT | RD | Wh | Real energy, sum. L1..L3, supplied, rate | [1]
5820 | INT | RD | Wh | Real energy, sum. L1..L3, supplied, rate | [2]
5822 | INT | RD | Wh | Real energy, sum. L1..L3, supplied, rate | [3]
5824 | INT | RD | Wh | Real energy, sum. L1..L3, supplied, rate | [4]
5826 | INT | RD | Wh | Real energy, sum. L1..L3, supplied, rate | [5]
5828 | INT | RD | Wh | Real energy, sum. L1..L3, supplied, rate | [6]
5830 | INT | RD | Wh | Real energy, sum. L1..L3, supplied, rate | [7]
5832 | INT | RD | varh | Reactive energy, sum. L1..L3, rate | [0]
5834 | INT | RD | varh | Reactive energy, sum. L1..L3, rate | [1]
5836 | INT | RD | varh | Reactive energy, sum. L1..L3, rate | [2]
5838 | INT | RD | varh | Reactive energy, sum. L1..L3, rate | [3]
5840 | INT | RD | varh | Reactive energy, sum. L1..L3, rate | [4]
5842 | INT | RD | varh | Reactive energy, sum. L1..L3, rate | [5]
5844 | INT | RD | varh | Reactive energy, sum. L1..L3, rate | [6]
5846 | INT | RD | varh | Reactive energy, sum. L1..L3, rate | [7]
5848 | INT | RD | varh | Reactive energy, sum. L1..L3, ind., rate | [0]
5850 | INT | RD | varh | Reactive energy, sum. L1..L3, ind., rate | [1]
5852 | INT | RD | varh | Reactive energy, sum. L1..L3, ind., rate | [2]
5854 | INT | RD | varh | Reactive energy, sum. L1..L3, ind., rate | [3]
5856 | INT | RD | varh | Reactive energy, sum. L1..L3, ind., rate | [4]
5858 | INT | RD | varh | Reactive energy, sum. L1..L3, ind., rate | [5]
5860 | INT | RD | varh | Reactive energy, sum. L1..L3, ind., rate | [6]
5862 | INT | RD | varh | Reactive energy, sum. L1..L3, ind., rate | [7]
5864 | INT | RD | varh | Reactive energy, sum. L1..L3, cap., rate | [0]
5866 | INT | RD | varh | Reactive energy, sum. L1..L3, cap., rate | [1]
5868 | INT | RD | varh | Reactive energy, sum. L1..L3, cap., rate | [2]
5870 | INT | RD | varh | Reactive energy, sum. L1..L3, cap., rate | [3]
5872 | INT | RD | varh | Reactive energy, sum. L1..L3, cap., rate | [4]
5874 | INT | RD | varh | Reactive energy, sum. L1..L3, cap., rate | [5]
5876 | INT | RD | varh | Reactive energy, sum. L1..L3, cap., rate | [6]
5878 | INT | RD | varh | Reactive energy, sum. L1..L3, cap., rate | [7]
5880 | INT | RD | VAh | Apparent energy, sum. L1..L3, rate | [0]
5882 | INT | RD | VAh | Apparent energy, sum. L1..L3, rate | [1]
5884 | INT | RD | VAh | Apparent energy, sum. L1..L3, rate | [2]
5886 | INT | RD | VAh | Apparent energy, sum. L1..L3, rate | [3]
5888 | INT | RD | VAh | Apparent energy, sum. L1..L3, rate | [4]
5890 | INT | RD | VAh | Apparent energy, sum. L1..L3, rate | [5]
5892 | INT | RD | VAh | Apparent energy, sum. L1..L3, rate | [6]
5894 | INT | RD | VAh | Apparent energy, sum. L1..L3, rate | [7]
5896 | INT | RD | sec | Operation hours meter
5898 | INT | RD | sec | Total running time, comparator | [0]
5900 | INT | RD | sec | Total running time, comparator | [1]
5902 | INT | RD | sec | Total running time, comparator | [2]
5904 | INT | RD | sec | Total running time, comparator | [3]
5906 | INT | RD | sec | Total running time, comparator | [4]
5908 | INT | RD | sec | Total running time, comparator | [5]
Energy, type Float
Address | Format | RD/WR | Unit | Note | Index
5000 | FLOAT | RD/WR | Wh | Real energy, L1, rate | [0]
5002 | FLOAT | RD/WR | Wh | Real energy, L1, rate | [1]
5004 | FLOAT | RD/WR | Wh | Real energy, L1, rate | [2]
5006 | FLOAT | RD/WR | Wh | Real energy, L1, rate | [3]
5008 | FLOAT | RD/WR | Wh | Real energy, L1, rate | [4]
5010 | FLOAT | RD/WR | Wh | Real energy, L1, rate | [5]
5012 | FLOAT | RD/WR | Wh | Real energy, L1, rate | [6]
5014 | FLOAT | RD/WR | Wh | Real energy, L1, rate | [7]
5016 | FLOAT | RD/WR | Wh | Real energy, L1, obtained, rate | [0]
5018 | FLOAT | RD/WR | Wh | Real energy, L1, obtained, rate | [1]
5020 | FLOAT | RD/WR | Wh | Real energy, L1, obtained, rate | [2]
5022 | FLOAT | RD/WR | Wh | Real energy, L1, obtained, rate | [3]
5024 | FLOAT | RD/WR | Wh | Real energy, L1, obtained, rate | [4]
5026 | FLOAT | RD/WR | Wh | Real energy, L1, obtained, rate | [5]
5028 | FLOAT | RD/WR | Wh | Real energy, L1, obtained, rate | [6]
5030 | FLOAT | RD/WR | Wh | Real energy, L1, obtained, rate | [7]
5032 | FLOAT | RD/WR | Wh | Real energy, L1, supplied, rate | [0]
5034 | FLOAT | RD/WR | Wh | Real energy, L1, supplied, rate | [1]
5036 | FLOAT | RD/WR | Wh | Real energy, L1, supplied, rate | [2]
5038 | FLOAT | RD/WR | Wh | Real energy, L1, supplied, rate | [3]
5040 | FLOAT | RD/WR | Wh | Real energy, L1, supplied, rate | [4]
5042 | FLOAT | RD/WR | Wh | Real energy, L1, supplied, rate | [5]
5044 | FLOAT | RD/WR | Wh | Real energy, L1, supplied, rate | [6]
5046 | FLOAT | RD/WR | Wh | Real energy, L1, supplied, rate | [7]
5048 | FLOAT | RD/WR | varh | Reactive energy, L1, rate | [0]
5050 | FLOAT | RD/WR | varh | Reactive energy, L1, rate | [1]
5052 | FLOAT | RD/WR | varh | Reactive energy, L1, rate | [2]
5054 | FLOAT | RD/WR | varh | Reactive energy, L1, rate | [3]
5056 | FLOAT | RD/WR | varh | Reactive energy, L1, rate | [4]
5058 | FLOAT | RD/WR | varh | Reactive energy, L1, rate | [5]
5060 | FLOAT | RD/WR | varh | Reactive energy, L1, rate | [6]
5062 | FLOAT | RD/WR | varh | Reactive energy, L1, rate | [7]
5064 | FLOAT | RD/WR | varh | Reactive energy, L1, ind., rate | [0]
5066 | FLOAT | RD/WR | varh | Reactive energy, L1, ind., rate | [1]
5068 | FLOAT | RD/WR | varh | Reactive energy, L1, ind., rate | [2]
5070 | FLOAT | RD/WR | varh | Reactive energy, L1, ind., rate | [3]
5072 | FLOAT | RD/WR | varh | Reactive energy, L1, ind., rate | [4]
5074 | FLOAT | RD/WR | varh | Reactive energy, L1, ind., rate | [5]
5076 | FLOAT | RD/WR | varh | Reactive energy, L1, ind., rate | [6]
5078 | FLOAT | RD/WR | varh | Reactive energy, L1, ind., rate | [7]
5080 | FLOAT | RD/WR | varh | Reactive energy, L1, cap., rate | [0]
5082 | FLOAT | RD/WR | varh | Reactive energy, L1, cap., rate | [1]
5084 | FLOAT | RD/WR | varh | Reactive energy, L1, cap., rate | [2]
5086 | FLOAT | RD/WR | varh | Reactive energy, L1, cap., rate | [3]
5088 | FLOAT | RD/WR | varh | Reactive energy, L1, cap., rate | [4]
5090 | FLOAT | RD/WR | varh | Reactive energy, L1, cap., rate | [5]
5092 | FLOAT | RD/WR | varh | Reactive energy, L1, cap., rate | [6]
5094 | FLOAT | RD/WR | varh | Reactive energy, L1, cap., rate | [7]
5096 | FLOAT | RD/WR | VAh | Apparent energy, L1, rate | [0]
5098 | FLOAT | RD/WR | VAh | Apparent energy, L1, rate | [1]
5100 | FLOAT | RD/WR | VAh | Apparent energy, L1, rate | [2]
5102 | FLOAT | RD/WR | VAh | Apparent energy, L1, rate | [3]
5104 | FLOAT | RD/WR | VAh | Apparent energy, L1, rate | [4]
5106 | FLOAT | RD/WR | VAh | Apparent energy, L1, rate | [5]
5108 | FLOAT | RD/WR | VAh | Apparent energy, L1, rate | [6]
5110 | FLOAT | RD/WR | VAh | Apparent energy, L1, rate | [7]
5112 | FLOAT | RD/WR | Wh | Real energy, L2, rate | [0]
5114 | FLOAT | RD/WR | Wh | Real energy, L2, rate | [1]
5116 | FLOAT | RD/WR | Wh | Real energy, L2, rate | [2]
5118 | FLOAT | RD/WR | Wh | Real energy, L2, rate | [3]
5120 | FLOAT | RD/WR | Wh | Real energy, L2, rate | [4]
5122 | FLOAT | RD/WR | Wh | Real energy, L2, rate | [5]
5124 | FLOAT | RD/WR | Wh | Real energy, L2, rate | [6]
5126 | FLOAT | RD/WR | Wh | Real energy, L2, rate | [7]
5128 | FLOAT | RD/WR | Wh | Real energy, L2, obtained, rate | [0]
5130 | FLOAT | RD/WR | Wh | Real energy, L2, obtained, rate | [1]
5132 | FLOAT | RD/WR | Wh | Real energy, L2, obtained, rate | [2]
5134 | FLOAT | RD/WR | Wh | Real energy, L2, obtained, rate | [3]
5136 | FLOAT | RD/WR | Wh | Real energy, L2, obtained, rate | [4]
5138 | FLOAT | RD/WR | Wh | Real energy, L2, obtained, rate | [5]
5140 | FLOAT | RD/WR | Wh | Real energy, L2, obtained, rate | [6]
5142 | FLOAT | RD/WR | Wh | Real energy, L2, obtained, rate | [7]
5144 | FLOAT | RD/WR | Wh | Real energy, L2, supplied, rate | [0]
5146 | FLOAT | RD/WR | Wh | Real energy, L2, supplied, rate | [1]
5148 | FLOAT | RD/WR | Wh | Real energy, L2, supplied, rate | [2]
5150 | FLOAT | RD/WR | Wh | Real energy, L2, supplied, rate | [3]
5152 | FLOAT | RD/WR | Wh | Real energy, L2, supplied, rate | [4]
5154 | FLOAT | RD/WR | Wh | Real energy, L2, supplied, rate | [5]
5156 | FLOAT | RD/WR | Wh | Real energy, L2, supplied, rate | [6]
5158 | FLOAT | RD/WR | Wh | Real energy, L2, supplied, rate | [7]
5160 | FLOAT | RD/WR | varh | Reactive energy, L2, rate | [0]
5162 | FLOAT | RD/WR | varh | Reactive energy, L2, rate | [1]
5164 | FLOAT | RD/WR | varh | Reactive energy, L2, rate | [2]
5166 | FLOAT | RD/WR | varh | Reactive energy, L2, rate | [3]
5168 | FLOAT | RD/WR | varh | Reactive energy, L2, rate | [4]
5170 | FLOAT | RD/WR | varh | Reactive energy, L2, rate | [5]
5172 | FLOAT | RD/WR | varh | Reactive energy, L2, rate | [6]
5174 | FLOAT | RD/WR | varh | Reactive energy, L2, rate | [7]
5176 | FLOAT | RD/WR | varh | Reactive energy, L2, ind., rate | [0]
5178 | FLOAT | RD/WR | varh | Reactive energy, L2, ind., rate | [1]
5180 | FLOAT | RD/WR | varh | Reactive energy, L2, ind., rate | [2]
5182 | FLOAT | RD/WR | varh | Reactive energy, L2, ind., rate | [3]
5184 | FLOAT | RD/WR | varh | Reactive energy, L2, ind., rate | [4]
5186 | FLOAT | RD/WR | varh | Reactive energy, L2, ind., rate | [5]
5188 | FLOAT | RD/WR | varh | Reactive energy, L2, ind., rate | [6]
5190 | FLOAT | RD/WR | varh | Reactive energy, L2, ind., rate | [7]
5192 | FLOAT | RD/WR | varh | Reactive energy, L2, cap., rate | [0]
5194 | FLOAT | RD/WR | varh | Reactive energy, L2, cap., rate | [1]
5196 | FLOAT | RD/WR | varh | Reactive energy, L2, cap., rate | [2]
5198 | FLOAT | RD/WR | varh | Reactive energy, L2, cap., rate | [3]
5200 | FLOAT | RD/WR | varh | Reactive energy, L2, cap., rate | [4]
5202 | FLOAT | RD/WR | varh | Reactive energy, L2, cap., rate | [5]
5204 | FLOAT | RD/WR | varh | Reactive energy, L2, cap., rate | [6]
5206 | FLOAT | RD/WR | varh | Reactive energy, L2, cap., rate | [7]
5208 | FLOAT | RD/WR | VAh | Apparent energy, L2, rate | [0]
5210 | FLOAT | RD/WR | VAh | Apparent energy, L2, rate | [1]
5212 | FLOAT | RD/WR | VAh | Apparent energy, L2, rate | [2]
5214 | FLOAT | RD/WR | VAh | Apparent energy, L2, rate | [3]
5216 | FLOAT | RD/WR | VAh | Apparent energy, L2, rate | [4]
5218 | FLOAT | RD/WR | VAh | Apparent energy, L2, rate | [5]
5220 | FLOAT | RD/WR | VAh | Apparent energy, L2, rate | [6]
5222 | FLOAT | RD/WR | VAh | Apparent energy, L2, rate | [7]
5224 | FLOAT | RD/WR | Wh | Real energy, L3, rate | [0]
5226 | FLOAT | RD/WR | Wh | Real energy, L3, rate | [1]
5228 | FLOAT | RD/WR | Wh | Real energy, L3, rate | [2]
5230 | FLOAT | RD/WR | Wh | Real energy, L3, rate | [3]
5232 | FLOAT | RD/WR | Wh | Real energy, L3, rate | [4]
5234 | FLOAT | RD/WR | Wh | Real energy, L3, rate | [5]
5236 | FLOAT | RD/WR | Wh | Real energy, L3, rate | [6]
5238 | FLOAT | RD/WR | Wh | Real energy, L3, rate | [7]
5240 | FLOAT | RD/WR | Wh | Real energy, L3, obtained, rate | [0]
5242 | FLOAT | RD/WR | Wh | Real energy, L3, obtained, rate | [1]
5244 | FLOAT | RD/WR | Wh | Real energy, L3, obtained, rate | [2]
5246 | FLOAT | RD/WR | Wh | Real energy, L3, obtained, rate | [3]
5248 | FLOAT | RD/WR | Wh | Real energy, L3, obtained, rate | [4]
5250 | FLOAT | RD/WR | Wh | Real energy, L3, obtained, rate | [5]
5252 | FLOAT | RD/WR | Wh | Real energy, L3, obtained, rate | [6]
5254 | FLOAT | RD/WR | Wh | Real energy, L3, obtained, rate | [7]
5256 | FLOAT | RD/WR | Wh | Real energy, L3, supplied, rate | [0]
5258 | FLOAT | RD/WR | Wh | Real energy, L3, supplied, rate | [1]
5260 | FLOAT | RD/WR | Wh | Real energy, L3, supplied, rate | [2]
5262 | FLOAT | RD/WR | Wh | Real energy, L3, supplied, rate | [3]
5264 | FLOAT | RD/WR | Wh | Real energy, L3, supplied, rate | [4]
5266 | FLOAT | RD/WR | Wh | Real energy, L3, supplied, rate | [5]
5268 | FLOAT | RD/WR | Wh | Real energy, L3, supplied, rate | [6]
5270 | FLOAT | RD/WR | Wh | Real energy, L3, supplied, rate | [7]
5272 | FLOAT | RD/WR | varh | Reactive energy, L3, rate | [0]
5274 | FLOAT | RD/WR | varh | Reactive energy, L3, rate | [1]
5276 | FLOAT | RD/WR | varh | Reactive energy, L3, rate | [2]
5278 | FLOAT | RD/WR | varh | Reactive energy, L3, rate | [3]
5280 | FLOAT | RD/WR | varh | Reactive energy, L3, rate | [4]
5282 | FLOAT | RD/WR | varh | Reactive energy, L3, rate | [5]
5284 | FLOAT | RD/WR | varh | Reactive energy, L3, rate | [6]
5286 | FLOAT | RD/WR | varh | Reactive energy, L3, rate | [7]
5288 | FLOAT | RD/WR | varh | Reactive energy, L3, ind., rate | [0]
5290 | FLOAT | RD/WR | varh | Reactive energy, L3, ind., rate | [1]
5292 | FLOAT | RD/WR | varh | Reactive energy, L3, ind., rate | [2]
5294 | FLOAT | RD/WR | varh | Reactive energy, L3, ind., rate | [3]
5296 | FLOAT | RD/WR | varh | Reactive energy, L3, ind., rate | [4]
5298 | FLOAT | RD/WR | varh | Reactive energy, L3, ind., rate | [5]
5300 | FLOAT | RD/WR | varh | Reactive energy, L3, ind., rate | [6]
5302 | FLOAT | RD/WR | varh | Reactive energy, L3, ind., rate | [7]
5304 | FLOAT | RD/WR | varh | Reactive energy, L3, cap., rate | [0]
5306 | FLOAT | RD/WR | varh | Reactive energy, L3, cap., rate | [1]
5308 | FLOAT | RD/WR | varh | Reactive energy, L3, cap., rate | [2]
5310 | FLOAT | RD/WR | varh | Reactive energy, L3, cap., rate | [3]
5312 | FLOAT | RD/WR | varh | Reactive energy, L3, cap., rate | [4]
5314 | FLOAT | RD/WR | varh | Reactive energy, L3, cap., rate | [5]
5316 | FLOAT | RD/WR | varh | Reactive energy, L3, cap., rate | [6]
5318 | FLOAT | RD/WR | varh | Reactive energy, L3, cap., rate | [7]
5320 | FLOAT | RD/WR | VAh | Apparent energy, L3, rate | [0]
5322 | FLOAT | RD/WR | VAh | Apparent energy, L3, rate | [1]
5324 | FLOAT | RD/WR | VAh | Apparent energy, L3, rate | [2]
5326 | FLOAT | RD/WR | VAh | Apparent energy, L3, rate | [3]
5328 | FLOAT | RD/WR | VAh | Apparent energy, L3, rate | [4]
5330 | FLOAT | RD/WR | VAh | Apparent energy, L3, rate | [5]
5332 | FLOAT | RD/WR | VAh | Apparent energy, L3, rate | [6]
5334 | FLOAT | RD/WR | VAh | Apparent energy, L3, rate | [7]
5336 | FLOAT | RD/WR | Wh | Real energy, sum. L1..L3, rate | [0]
5338 | FLOAT | RD/WR | Wh | Real energy, sum. L1..L3, rate | [1]
5340 | FLOAT | RD/WR | Wh | Real energy, sum. L1..L3, rate | [2]
5342 | FLOAT | RD/WR | Wh | Real energy, sum. L1..L3, rate | [3]
5344 | FLOAT | RD/WR | Wh | Real energy, sum. L1..L3, rate | [4]
5346 | FLOAT | RD/WR | Wh | Real energy, sum. L1..L3, rate | [5]
5348 | FLOAT | RD/WR | Wh | Real energy, sum. L1..L3, rate | [6]
5350 | FLOAT | RD/WR | Wh | Real energy, sum. L1..L3, rate | [7]
5352 | FLOAT | RD/WR | Wh | Real energy, sum. L1..L3, obtained, rate | [0]
5354 | FLOAT | RD/WR | Wh | Real energy, sum. L1..L3, obtained, rate | [1]
5356 | FLOAT | RD/WR | Wh | Real energy, sum. L1..L3, obtained, rate | [2]
5358 | FLOAT | RD/WR | Wh | Real energy, sum. L1..L3, obtained, rate | [3]
5360 | FLOAT | RD/WR | Wh | Real energy, sum. L1..L3, obtained, rate | [4]
5362 | FLOAT | RD/WR | Wh | Real energy, sum. L1..L3, obtained, rate | [5]
5364 | FLOAT | RD/WR | Wh | Real energy, sum. L1..L3, obtained, rate | [6]
5366 | FLOAT | RD/WR | Wh | Real energy, sum. L1..L3, obtained, rate | [7]
5368 | FLOAT | RD/WR | Wh | Real energy, sum. L1..L3, supplied, rate | [0]
5370 | FLOAT | RD/WR | Wh | Real energy, sum. L1..L3, supplied, rate | [1]
5372 | FLOAT | RD/WR | Wh | Real energy, sum. L1..L3, supplied, rate | [2]
5374 | FLOAT | RD/WR | Wh | Real energy, sum. L1..L3, supplied, rate | [3]
5376 | FLOAT | RD/WR | Wh | Real energy, sum. L1..L3, supplied, rate | [4]
5378 | FLOAT | RD/WR | Wh | Real energy, sum. L1..L3, supplied, rate | [5]
5380 | FLOAT | RD/WR | Wh | Real energy, sum. L1..L3, supplied, rate | [6]
5382 | FLOAT | RD/WR | Wh | Real energy, sum. L1..L3, supplied, rate | [7]
5384 | FLOAT | RD/WR | varh | Reactive energy, sum. L1..L3, rate | [0]
5386 | FLOAT | RD/WR | varh | Reactive energy, sum. L1..L3, rate | [1]
5388 | FLOAT | RD/WR | varh | Reactive energy, sum. L1..L3, rate | [2]
5390 | FLOAT | RD/WR | varh | Reactive energy, sum. L1..L3, rate | [3]
5392 | FLOAT | RD/WR | varh | Reactive energy, sum. L1..L3, rate | [4]
5394 | FLOAT | RD/WR | varh | Reactive energy, sum. L1..L3, rate | [5]
5396 | FLOAT | RD/WR | varh | Reactive energy, sum. L1..L3, rate | [6]
5398 | FLOAT | RD/WR | varh | Reactive energy, sum. L1..L3, rate | [7]
5400 | FLOAT | RD/WR | varh | Reactive energy, sum. L1..L3, ind., rate | [0]
5402 | FLOAT | RD/WR | varh | Reactive energy, sum. L1..L3, ind., rate | [1]
5404 | FLOAT | RD/WR | varh | Reactive energy, sum. L1..L3, ind., rate | [2]
5406 | FLOAT | RD/WR | varh | Reactive energy, sum. L1..L3, ind., rate | [3]
5408 | FLOAT | RD/WR | varh | Reactive energy, sum. L1..L3, ind., rate | [4]
5410 | FLOAT | RD/WR | varh | Reactive energy, sum. L1..L3, ind., rate | [5]
5412 | FLOAT | RD/WR | varh | Reactive energy, sum. L1..L3, ind., rate | [6]
5414 | FLOAT | RD/WR | varh | Reactive energy, sum. L1..L3, ind., rate | [7]
5416 | FLOAT | RD/WR | varh | Reactive energy, sum. L1..L3, cap., rate | [0]
5418 | FLOAT | RD/WR | varh | Reactive energy, sum. L1..L3, cap., rate | [1]
5420 | FLOAT | RD/WR | varh | Reactive energy, sum. L1..L3, cap., rate | [2]
5422 | FLOAT | RD/WR | varh | Reactive energy, sum. L1..L3, cap., rate | [3]
5424 | FLOAT | RD/WR | varh | Reactive energy, sum. L1..L3, cap., rate | [4]
5426 | FLOAT | RD/WR | varh | Reactive energy, sum. L1..L3, cap., rate | [5]
5428 | FLOAT | RD/WR | varh | Reactive energy, sum. L1..L3, cap., rate | [6]
5430 | FLOAT | RD/WR | varh | Reactive energy, sum. L1..L3, cap., rate | [7]
5432 | FLOAT | RD/WR | VAh | Apparent energy, sum. L1..L3, rate | [0]
5434 | FLOAT | RD/WR | VAh | Apparent energy, sum. L1..L3, rate | [1]
5436 | FLOAT | RD/WR | VAh | Apparent energy, sum. L1..L3, rate | [2]
5438 | FLOAT | RD/WR | VAh | Apparent energy, sum. L1..L3, rate | [3]
5440 | FLOAT | RD/WR | VAh | Apparent energy, sum. L1..L3, rate | [4]
5442 | FLOAT | RD/WR | VAh | Apparent energy, sum. L1..L3, rate | [5]
5444 | FLOAT | RD/WR | VAh | Apparent energy, sum. L1..L3, rate | [6]
5446 | FLOAT | RD/WR | VAh | Apparent energy, sum. L1..L3, rate | [7]
Fourier analysis
Address | Format | RD/WR | Unit | Note | Index
1000 | FLOAT | RD | V | Harmonic U L1 | [0]
1002 | FLOAT | RD | V | Harmonic U L1 | [1]
1004 | FLOAT | RD | V | Harmonic U L1 | [2]
1006 | FLOAT | RD | V | Harmonic U L1 | [3]
1008 | FLOAT | RD | V | Harmonic U L1 | [4]
1010 | FLOAT | RD | V | Harmonic U L1 | [5]
1012 | FLOAT | RD | V | Harmonic U L1 | [6]
1014 | FLOAT | RD | V | Harmonic U L1 | [7]
1016 | FLOAT | RD | V | Harmonic U L1 | [8]
1018 | FLOAT | RD | V | Harmonic U L1 | [9]
1020 | FLOAT | RD | V | Harmonic U L1 | [10]
1022 | FLOAT | RD | V | Harmonic U L1 | [11]
1024 | FLOAT | RD | V | Harmonic U L1 | [12]
1026 | FLOAT | RD | V | Harmonic U L1 | [13]
1028 | FLOAT | RD | V | Harmonic U L1 | [14]
1030 | FLOAT | RD | V | Harmonic U L1 | [15]
1032 | FLOAT | RD | V | Harmonic U L1 | [16]
1034 | FLOAT | RD | V | Harmonic U L1 | [17]
1036 | FLOAT | RD | V | Harmonic U L1 | [18]
1038 | FLOAT | RD | V | Harmonic U L1 | [19]
1040 | FLOAT | RD | V | Harmonic U L1 | [20]
1042 | FLOAT | RD | V | Harmonic U L1 | [21]
1044 | FLOAT | RD | V | Harmonic U L1 | [22]
1046 | FLOAT | RD | V | Harmonic U L1 | [23]
1048 | FLOAT | RD | V | Harmonic U L1 | [24]
1050 | FLOAT | RD | V | Harmonic U L1 | [25]
1052 | FLOAT | RD | V | Harmonic U L1 | [26]
1054 | FLOAT | RD | V | Harmonic U L1 | [27]
1056 | FLOAT | RD | V | Harmonic U L1 | [28]
1058 | FLOAT | RD | V | Harmonic U L1 | [29]
1060 | FLOAT | RD | V | Harmonic U L1 | [30]
1062 | FLOAT | RD | V | Harmonic U L1 | [31]
1064 | FLOAT | RD | V | Harmonic U L1 | [32]
1066 | FLOAT | RD | V | Harmonic U L1 | [33]
1068 | FLOAT | RD | V | Harmonic U L1 | [34]
1070 | FLOAT | RD | V | Harmonic U L1 | [35]
1072 | FLOAT | RD | V | Harmonic U L1 | [36]
1074 | FLOAT | RD | V | Harmonic U L1 | [37]
1076 | FLOAT | RD | V | Harmonic U L1 | [38]
1078 | FLOAT | RD | V | Harmonic U L1 | [39]
1080 | FLOAT | RD | V | Harmonic U L2 | [0]
1082 | FLOAT | RD | V | Harmonic U L2 | [1]
1084 | FLOAT | RD | V | Harmonic U L2 | [2]
1086 | FLOAT | RD | V | Harmonic U L2 | [3]
1088 | FLOAT | RD | V | Harmonic U L2 | [4]
1090 | FLOAT | RD | V | Harmonic U L2 | [5]
1092 | FLOAT | RD | V | Harmonic U L2 | [6]
1094 | FLOAT | RD | V | Harmonic U L2 | [7]
1096 | FLOAT | RD | V | Harmonic U L2 | [8]
1098 | FLOAT | RD | V | Harmonic U L2 | [9]
1100 | FLOAT | RD | V | Harmonic U L2 | [10]
1102 | FLOAT | RD | V | Harmonic U L2 | [11]
1104 | FLOAT | RD | V | Harmonic U L2 | [12]
1106 | FLOAT | RD | V | Harmonic U L2 | [13]
1108 | FLOAT | RD | V | Harmonic U L2 | [14]
1110 | FLOAT | RD | V | Harmonic U L2 | [15]
1112 | FLOAT | RD | V | Harmonic U L2 | [16]
1114 | FLOAT | RD | V | Harmonic U L2 | [17]
1116 | FLOAT | RD | V | Harmonic U L2 | [18]
1118 | FLOAT | RD | V | Harmonic U L2 | [19]
1120 | FLOAT | RD | V | Harmonic U L2 | [20]
1122 | FLOAT | RD | V | Harmonic U L2 | [21]
1124 | FLOAT | RD | V | Harmonic U L2 | [22]
1126 | FLOAT | RD | V | Harmonic U L2 | [23]
1128 | FLOAT | RD | V | Harmonic U L2 | [24]
1130 | FLOAT | RD | V | Harmonic U L2 | [25]
1132 | FLOAT | RD | V | Harmonic U L2 | [26]
1134 | FLOAT | RD | V | Harmonic U L2 | [27]
1136 | FLOAT | RD | V | Harmonic U L2 | [28]
1138 | FLOAT | RD | V | Harmonic U L2 | [29]
1140 | FLOAT | RD | V | Harmonic U L2 | [30]
1142 | FLOAT | RD | V | Harmonic U L2 | [31]
1144 | FLOAT | RD | V | Harmonic U L2 | [32]
1146 | FLOAT | RD | V | Harmonic U L2 | [33]
1148 | FLOAT | RD | V | Harmonic U L2 | [34]
1150 | FLOAT | RD | V | Harmonic U L2 | [35]
1152 | FLOAT | RD | V | Harmonic U L2 | [36]
1154 | FLOAT | RD | V | Harmonic U L2 | [37]
1156 | FLOAT | RD | V | Harmonic U L2 | [38]
1158 | FLOAT | RD | V | Harmonic U L2 | [39]
1160 | FLOAT | RD | V | Harmonic U L3 | [0]
1162 | FLOAT | RD | V | Harmonic U L3 | [1]
1164 | FLOAT | RD | V | Harmonic U L3 | [2]
1166 | FLOAT | RD | V | Harmonic U L3 | [3]
1168 | FLOAT | RD | V | Harmonic U L3 | [4]
1170 | FLOAT | RD | V | Harmonic U L3 | [5]
1172 | FLOAT | RD | V | Harmonic U L3 | [6]
1174 | FLOAT | RD | V | Harmonic U L3 | [7]
1176 | FLOAT | RD | V | Harmonic U L3 | [8]
1178 | FLOAT | RD | V | Harmonic U L3 | [9]
1180 | FLOAT | RD | V | Harmonic U L3 | [10]
1182 | FLOAT | RD | V | Harmonic U L3 | [11]
1184 | FLOAT | RD | V | Harmonic U L3 | [12]
1186 | FLOAT | RD | V | Harmonic U L3 | [13]
1188 | FLOAT | RD | V | Harmonic U L3 | [14]
1190 | FLOAT | RD | V | Harmonic U L3 | [15]
1192 | FLOAT | RD | V | Harmonic U L3 | [16]
1194 | FLOAT | RD | V | Harmonic U L3 | [17]
1196 | FLOAT | RD | V | Harmonic U L3 | [18]
1198 | FLOAT | RD | V | Harmonic U L3 | [19]
1200 | FLOAT | RD | V | Harmonic U L3 | [20]
1202 | FLOAT | RD | V | Harmonic U L3 | [21]
1204 | FLOAT | RD | V | Harmonic U L3 | [22]
1206 | FLOAT | RD | V | Harmonic U L3 | [23]
1208 | FLOAT | RD | V | Harmonic U L3 | [24]
1210 | FLOAT | RD | V | Harmonic U L3 | [25]
1212 | FLOAT | RD | V | Harmonic U L3 | [26]
1214 | FLOAT | RD | V | Harmonic U L3 | [27]
1216 | FLOAT | RD | V | Harmonic U L3 | [28]
1218 | FLOAT | RD | V | Harmonic U L3 | [29]
1220 | FLOAT | RD | V | Harmonic U L3 | [30]
1222 | FLOAT | RD | V | Harmonic U L3 | [31]
1224 | FLOAT | RD | V | Harmonic U L3 | [32]
1226 | FLOAT | RD | V | Harmonic U L3 | [33]
1228 | FLOAT | RD | V | Harmonic U L3 | [34]
1230 | FLOAT | RD | V | Harmonic U L3 | [35]
1232 | FLOAT | RD | V | Harmonic U L3 | [36]
1234 | FLOAT | RD | V | Harmonic U L3 | [37]
1236 | FLOAT | RD | V | Harmonic U L3 | [38]
1238 | FLOAT | RD | V | Harmonic U L3 | [39]
1240 | FLOAT | RD | V | Harmonic U L1-L2 | [0]
1242 | FLOAT | RD | V | Harmonic U L1-L2 | [1]
1244 | FLOAT | RD | V | Harmonic U L1-L2 | [2]
1246 | FLOAT | RD | V | Harmonic U L1-L2 | [3]
1248 | FLOAT | RD | V | Harmonic U L1-L2 | [4]
1250 | FLOAT | RD | V | Harmonic U L1-L2 | [5]
1252 | FLOAT | RD | V | Harmonic U L1-L2 | [6]
1254 | FLOAT | RD | V | Harmonic U L1-L2 | [7]
1256 | FLOAT | RD | V | Harmonic U L1-L2 | [8]
1258 | FLOAT | RD | V | Harmonic U L1-L2 | [9]
1260 | FLOAT | RD | V | Harmonic U L1-L2 | [10]
1262 | FLOAT | RD | V | Harmonic U L1-L2 | [11]
1264 | FLOAT | RD | V | Harmonic U L1-L2 | [12]
1266 | FLOAT | RD | V | Harmonic U L1-L2 | [13]
1268 | FLOAT | RD | V | Harmonic U L1-L2 | [14]
1270 | FLOAT | RD | V | Harmonic U L1-L2 | [15]
1272 | FLOAT | RD | V | Harmonic U L1-L2 | [16]
1274 | FLOAT | RD | V | Harmonic U L1-L2 | [17]
1276 | FLOAT | RD | V | Harmonic U L1-L2 | [18]
1278 | FLOAT | RD | V | Harmonic U L1-L2 | [19]
1280 | FLOAT | RD | V | Harmonic U L1-L2 | [20]
1282 | FLOAT | RD | V | Harmonic U L1-L2 | [21]
1284 | FLOAT | RD | V | Harmonic U L1-L2 | [22]
1286 | FLOAT | RD | V | Harmonic U L1-L2 | [23]
1288 | FLOAT | RD | V | Harmonic U L1-L2 | [24]
1290 | FLOAT | RD | V | Harmonic U L1-L2 | [25]
1292 | FLOAT | RD | V | Harmonic U L1-L2 | [26]
1294 | FLOAT | RD | V | Harmonic U L1-L2 | [27]
1296 | FLOAT | RD | V | Harmonic U L1-L2 | [28]
1298 | FLOAT | RD | V | Harmonic U L1-L2 | [29]
1300 | FLOAT | RD | V | Harmonic U L1-L2 | [30]
1302 | FLOAT | RD | V | Harmonic U L1-L2 | [31]
1304 | FLOAT | RD | V | Harmonic U L1-L2 | [32]
1306 | FLOAT | RD | V | Harmonic U L1-L2 | [33]
1308 | FLOAT | RD | V | Harmonic U L1-L2 | [34]
1310 | FLOAT | RD | V | Harmonic U L1-L2 | [35]
1312 | FLOAT | RD | V | Harmonic U L1-L2 | [36]
1314 | FLOAT | RD | V | Harmonic U L1-L2 | [37]
1316 | FLOAT | RD | V | Harmonic U L1-L2 | [38]
1318 | FLOAT | RD | V | Harmonic U L1-L2 | [39]
1320 | FLOAT | RD | V | Harmonic U L2-L3 | [0]
1322 | FLOAT | RD | V | Harmonic U L2-L3 | [1]
1324 | FLOAT | RD | V | Harmonic U L2-L3 | [2]
1326 | FLOAT | RD | V | Harmonic U L2-L3 | [3]
1328 | FLOAT | RD | V | Harmonic U L2-L3 | [4]
1330 | FLOAT | RD | V | Harmonic U L2-L3 | [5]
1332 | FLOAT | RD | V | Harmonic U L2-L3 | [6]
1334 | FLOAT | RD | V | Harmonic U L2-L3 | [7]
1336 | FLOAT | RD | V | Harmonic U L2-L3 | [8]
1338 | FLOAT | RD | V | Harmonic U L2-L3 | [9]
1340 | FLOAT | RD | V | Harmonic U L2-L3 | [10]
1342 | FLOAT | RD | V | Harmonic U L2-L3 | [11]
1344 | FLOAT | RD | V | Harmonic U L2-L3 | [12]
1346 | FLOAT | RD | V | Harmonic U L2-L3 | [13]
1348 | FLOAT | RD | V | Harmonic U L2-L3 | [14]
1350 | FLOAT | RD | V | Harmonic U L2-L3 | [15]
1352 | FLOAT | RD | V | Harmonic U L2-L3 | [16]
1354 | FLOAT | RD | V | Harmonic U L2-L3 | [17]
1356 | FLOAT | RD | V | Harmonic U L2-L3 | [18]
1358 | FLOAT | RD | V | Harmonic U L2-L3 | [19]
1360 | FLOAT | RD | V | Harmonic U L2-L3 | [20]
1362 | FLOAT | RD | V | Harmonic U L2-L3 | [21]
1364 | FLOAT | RD | V | Harmonic U L2-L3 | [22]
1366 | FLOAT | RD | V | Harmonic U L2-L3 | [23]
1368 | FLOAT | RD | V | Harmonic U L2-L3 | [24]
1370 | FLOAT | RD | V | Harmonic U L2-L3 | [25]
1372 | FLOAT | RD | V | Harmonic U L2-L3 | [26]
1374 | FLOAT | RD | V | Harmonic U L2-L3 | [27]
1376 | FLOAT | RD | V | Harmonic U L2-L3 | [28]
1378 | FLOAT | RD | V | Harmonic U L2-L3 | [29]
1380 | FLOAT | RD | V | Harmonic U L2-L3 | [30]
1382 | FLOAT | RD | V | Harmonic U L2-L3 | [31]
1384 | FLOAT | RD | V | Harmonic U L2-L3 | [32]
1386 | FLOAT | RD | V | Harmonic U L2-L3 | [33]
1388 | FLOAT | RD | V | Harmonic U L2-L3 | [34]
1390 | FLOAT | RD | V | Harmonic U L2-L3 | [35]
1392 | FLOAT | RD | V | Harmonic U L2-L3 | [36]
1394 | FLOAT | RD | V | Harmonic U L2-L3 | [37]
1396 | FLOAT | RD | V | Harmonic U L2-L3 | [38]
1398 | FLOAT | RD | V | Harmonic U L2-L3 | [39]
1400 | FLOAT | RD | V | Harmonic U L3-L1 | [0]
1402 | FLOAT | RD | V | Harmonic U L3-L1 | [1]
1404 | FLOAT | RD | V | Harmonic U L3-L1 | [2]
1406 | FLOAT | RD | V | Harmonic U L3-L1 | [3]
1408 | FLOAT | RD | V | Harmonic U L3-L1 | [4]
1410 | FLOAT | RD | V | Harmonic U L3-L1 | [5]
1412 | FLOAT | RD | V | Harmonic U L3-L1 | [6]
1414 | FLOAT | RD | V | Harmonic U L3-L1 | [7]
1416 | FLOAT | RD | V | Harmonic U L3-L1 | [8]
1418 | FLOAT | RD | V | Harmonic U L3-L1 | [9]
1420 | FLOAT | RD | V | Harmonic U L3-L1 | [10]
1422 | FLOAT | RD | V | Harmonic U L3-L1 | [11]
1424 | FLOAT | RD | V | Harmonic U L3-L1 | [12]
1426 | FLOAT | RD | V | Harmonic U L3-L1 | [13]
1428 | FLOAT | RD | V | Harmonic U L3-L1 | [14]
1430 | FLOAT | RD | V | Harmonic U L3-L1 | [15]
1432 | FLOAT | RD | V | Harmonic U L3-L1 | [16]
1434 | FLOAT | RD | V | Harmonic U L3-L1 | [17]
1436 | FLOAT | RD | V | Harmonic U L3-L1 | [18]
1438 | FLOAT | RD | V | Harmonic U L3-L1 | [19]
1440 | FLOAT | RD | V | Harmonic U L3-L1 | [20]
1442 | FLOAT | RD | V | Harmonic U L3-L1 | [21]
1444 | FLOAT | RD | V | Harmonic U L3-L1 | [22]
1446 | FLOAT | RD | V | Harmonic U L3-L1 | [23]
1448 | FLOAT | RD | V | Harmonic U L3-L1 | [24]
1450 | FLOAT | RD | V | Harmonic U L3-L1 | [25]
1452 | FLOAT | RD | V | Harmonic U L3-L1 | [26]
1454 | FLOAT | RD | V | Harmonic U L3-L1 | [27]
1456 | FLOAT | RD | V | Harmonic U L3-L1 | [28]
1458 | FLOAT | RD | V | Harmonic U L3-L1 | [29]
1460 | FLOAT | RD | V | Harmonic U L3-L1 | [30]
1462 | FLOAT | RD | V | Harmonic U L3-L1 | [31]
1464 | FLOAT | RD | V | Harmonic U L3-L1 | [32]
1466 | FLOAT | RD | V | Harmonic U L3-L1 | [33]
1468 | FLOAT | RD | V | Harmonic U L3-L1 | [34]
1470 | FLOAT | RD | V | Harmonic U L3-L1 | [35]
1472 | FLOAT | RD | V | Harmonic U L3-L1 | [36]
1474 | FLOAT | RD | V | Harmonic U L3-L1 | [37]
1476 | FLOAT | RD | V | Harmonic U L3-L1 | [38]
1478 | FLOAT | RD | V | Harmonic U L3-L1 | [39]
1480 | FLOAT | RD | A | Harmonic I L1 | [0]
1482 | FLOAT | RD | A | Harmonic I L1 | [1]
1484 | FLOAT | RD | A | Harmonic I L1 | [2]
1486 | FLOAT | RD | A | Harmonic I L1 | [3]
1488 | FLOAT | RD | A | Harmonic I L1 | [4]
1490 | FLOAT | RD | A | Harmonic I L1 | [5]
1492 | FLOAT | RD | A | Harmonic I L1 | [6]
1494 | FLOAT | RD | A | Harmonic I L1 | [7]
1496 | FLOAT | RD | A | Harmonic I L1 | [8]
1498 | FLOAT | RD | A | Harmonic I L1 | [9]
1500 | FLOAT | RD | A | Harmonic I L1 | [10]
1502 | FLOAT | RD | A | Harmonic I L1 | [11]
1504 | FLOAT | RD | A | Harmonic I L1 | [12]
1506 | FLOAT | RD | A | Harmonic I L1 | [13]
1508 | FLOAT | RD | A | Harmonic I L1 | [14]
1510 | FLOAT | RD | A | Harmonic I L1 | [15]
1512 | FLOAT | RD | A | Harmonic I L1 | [16]
1514 | FLOAT | RD | A | Harmonic I L1 | [17]
1516 | FLOAT | RD | A | Harmonic I L1 | [18]
1518 | FLOAT | RD | A | Harmonic I L1 | [19]
1520 | FLOAT | RD | A | Harmonic I L1 | [20]
1522 | FLOAT | RD | A | Harmonic I L1 | [21]
1524 | FLOAT | RD | A | Harmonic I L1 | [22]
1526 | FLOAT | RD | A | Harmonic I L1 | [23]
1528 | FLOAT | RD | A | Harmonic I L1 | [24]
1530 | FLOAT | RD | A | Harmonic I L1 | [25]
1532 | FLOAT | RD | A | Harmonic I L1 | [26]
1534 | FLOAT | RD | A | Harmonic I L1 | [27]
1536 | FLOAT | RD | A | Harmonic I L1 | [28]
1538 | FLOAT | RD | A | Harmonic I L1 | [29]
1540 | FLOAT | RD | A | Harmonic I L1 | [30]
1542 | FLOAT | RD | A | Harmonic I L1 | [31]
1544 | FLOAT | RD | A | Harmonic I L1 | [32]
1546 | FLOAT | RD | A | Harmonic I L1 | [33]
1548 | FLOAT | RD | A | Harmonic I L1 | [34]
1550 | FLOAT | RD | A | Harmonic I L1 | [35]
1552 | FLOAT | RD | A | Harmonic I L1 | [36]
1554 | FLOAT | RD | A | Harmonic I L1 | [37]
1556 | FLOAT | RD | A | Harmonic I L1 | [38]
1558 | FLOAT | RD | A | Harmonic I L1 | [39]
1560 | FLOAT | RD | A | Harmonic I L2 | [0]
1562 | FLOAT | RD | A | Harmonic I L2 | [1]
1564 | FLOAT | RD | A | Harmonic I L2 | [2]
1566 | FLOAT | RD | A | Harmonic I L2 | [3]
1568 | FLOAT | RD | A | Harmonic I L2 | [4]
1570 | FLOAT | RD | A | Harmonic I L2 | [5]
1572 | FLOAT | RD | A | Harmonic I L2 | [6]
1574 | FLOAT | RD | A | Harmonic I L2 | [7]
1576 | FLOAT | RD | A | Harmonic I L2 | [8]
1578 | FLOAT | RD | A | Harmonic I L2 | [9]
1580 | FLOAT | RD | A | Harmonic I L2 | [10]
1582 | FLOAT | RD | A | Harmonic I L2 | [11]
1584 | FLOAT | RD | A | Harmonic I L2 | [12]
1586 | FLOAT | RD | A | Harmonic I L2 | [13]
1588 | FLOAT | RD | A | Harmonic I L2 | [14]
1590 | FLOAT | RD | A | Harmonic I L2 | [15]
1592 | FLOAT | RD | A | Harmonic I L2 | [16]
1594 | FLOAT | RD | A | Harmonic I L2 | [17]
1596 | FLOAT | RD | A | Harmonic I L2 | [18]
1598 | FLOAT | RD | A | Harmonic I L2 | [19]
1600 | FLOAT | RD | A | Harmonic I L2 | [20]
1602 | FLOAT | RD | A | Harmonic I L2 | [21]
1604 | FLOAT | RD | A | Harmonic I L2 | [22]
1606 | FLOAT | RD | A | Harmonic I L2 | [23]
1608 | FLOAT | RD | A | Harmonic I L2 | [24]
1610 | FLOAT | RD | A | Harmonic I L2 | [25]
1612 | FLOAT | RD | A | Harmonic I L2 | [26]
1614 | FLOAT | RD | A | Harmonic I L2 | [27]
1616 | FLOAT | RD | A | Harmonic I L2 | [28]
1618 | FLOAT | RD | A | Harmonic I L2 | [29]
1620 | FLOAT | RD | A | Harmonic I L2 | [30]
1622 | FLOAT | RD | A | Harmonic I L2 | [31]
1624 | FLOAT | RD | A | Harmonic I L2 | [32]
1626 | FLOAT | RD | A | Harmonic I L2 | [33]
1628 | FLOAT | RD | A | Harmonic I L2 | [34]
1630 | FLOAT | RD | A | Harmonic I L2 | [35]
1632 | FLOAT | RD | A | Harmonic I L2 | [36]
1634 | FLOAT | RD | A | Harmonic I L2 | [37]
1636 | FLOAT | RD | A | Harmonic I L2 | [38]
1638 | FLOAT | RD | A | Harmonic I L2 | [39]
1640 | FLOAT | RD | A | Harmonic I L3 | [0]
1642 | FLOAT | RD | A | Harmonic I L3 | [1]
1644 | FLOAT | RD | A | Harmonic I L3 | [2]
1646 | FLOAT | RD | A | Harmonic I L3 | [3]
1648 | FLOAT | RD | A | Harmonic I L3 | [4]
1650 | FLOAT | RD | A | Harmonic I L3 | [5]
1652 | FLOAT | RD | A | Harmonic I L3 | [6]
1654 | FLOAT | RD | A | Harmonic I L3 | [7]
1656 | FLOAT | RD | A | Harmonic I L3 | [8]
1658 | FLOAT | RD | A | Harmonic I L3 | [9]
1660 | FLOAT | RD | A | Harmonic I L3 | [10]
1662 | FLOAT | RD | A | Harmonic I L3 | [11]
1664 | FLOAT | RD | A | Harmonic I L3 | [12]
1666 | FLOAT | RD | A | Harmonic I L3 | [13]
1668 | FLOAT | RD | A | Harmonic I L3 | [14]
1670 | FLOAT | RD | A | Harmonic I L3 | [15]
1672 | FLOAT | RD | A | Harmonic I L3 | [16]
1674 | FLOAT | RD | A | Harmonic I L3 | [17]
1676 | FLOAT | RD | A | Harmonic I L3 | [18]
1678 | FLOAT | RD | A | Harmonic I L3 | [19]
1680 | FLOAT | RD | A | Harmonic I L3 | [20]
1682 | FLOAT | RD | A | Harmonic I L3 | [21]
1684 | FLOAT | RD | A | Harmonic I L3 | [22]
1686 | FLOAT | RD | A | Harmonic I L3 | [23]
1688 | FLOAT | RD | A | Harmonic I L3 | [24]
1690 | FLOAT | RD | A | Harmonic I L3 | [25]
1692 | FLOAT | RD | A | Harmonic I L3 | [26]
1694 | FLOAT | RD | A | Harmonic I L3 | [27]
1696 | FLOAT | RD | A | Harmonic I L3 | [28]
1698 | FLOAT | RD | A | Harmonic I L3 | [29]
1700 | FLOAT | RD | A | Harmonic I L3 | [30]
1702 | FLOAT | RD | A | Harmonic I L3 | [31]
1704 | FLOAT | RD | A | Harmonic I L3 | [32]
1706 | FLOAT | RD | A | Harmonic I L3 | [33]
1708 | FLOAT | RD | A | Harmonic I L3 | [34]
1710 | FLOAT | RD | A | Harmonic I L3 | [35]
1712 | FLOAT | RD | A | Harmonic I L3 | [36]
1714 | FLOAT | RD | A | Harmonic I L3 | [37]
1716 | FLOAT | RD | A | Harmonic I L3 | [38]
1718 | FLOAT | RD | A | Harmonic I L3 | [39]
Measured values, type short, fourier analysis
Address | Format | RD/WR | Unit | Note | Index | Resolution
3536 | SHORT | RD | V | Harmonic U L1 | [0] | 0.1
3537 | SHORT | RD | V | Harmonic U L1 | [1] | 0.1
3538 | SHORT | RD | V | Harmonic U L1 | [2] | 0.1
3539 | SHORT | RD | V | Harmonic U L1 | [3] | 0.1
3540 | SHORT | RD | V | Harmonic U L1 | [4] | 0.1
3541 | SHORT | RD | V | Harmonic U L1 | [5] | 0.1
3542 | SHORT | RD | V | Harmonic U L1 | [6] | 0.1
3543 | SHORT | RD | V | Harmonic U L1 | [7] | 0.1
3544 | SHORT | RD | V | Harmonic U L1 | [8] | 0.1
3545 | SHORT | RD | V | Harmonic U L1 | [9] | 0.1
3546 | SHORT | RD | V | Harmonic U L1 | [10] | 0.1
3547 | SHORT | RD | V | Harmonic U L1 | [11] | 0.1
3548 | SHORT | RD | V | Harmonic U L1 | [12] | 0.1
3549 | SHORT | RD | V | Harmonic U L1 | [13] | 0.1
3550 | SHORT | RD | V | Harmonic U L1 | [14] | 0.1
3551 | SHORT | RD | V | Harmonic U L1 | [15] | 0.1
3552 | SHORT | RD | V | Harmonic U L1 | [16] | 0.1
3553 | SHORT | RD | V | Harmonic U L1 | [17] | 0.1
3554 | SHORT | RD | V | Harmonic U L1 | [18] | 0.1
3555 | SHORT | RD | V | Harmonic U L1 | [19] | 0.1
3556 | SHORT | RD | V | Harmonic U L1 | [20] | 0.1
3557 | SHORT | RD | V | Harmonic U L1 | [21] | 0.1
3558 | SHORT | RD | V | Harmonic U L1 | [22] | 0.1
3559 | SHORT | RD | V | Harmonic U L1 | [23] | 0.1
3560 | SHORT | RD | V | Harmonic U L1 | [24] | 0.1
3561 | SHORT | RD | V | Harmonic U L1 | [25] | 0.1
3562 | SHORT | RD | V | Harmonic U L1 | [26] | 0.1
3563 | SHORT | RD | V | Harmonic U L1 | [27] | 0.1
3564 | SHORT | RD | V | Harmonic U L1 | [28] | 0.1
3565 | SHORT | RD | V | Harmonic U L1 | [29] | 0.1
3566 | SHORT | RD | V | Harmonic U L1 | [30] | 0.1
3567 | SHORT | RD | V | Harmonic U L1 | [31] | 0.1
3568 | SHORT | RD | V | Harmonic U L1 | [32] | 0.1
3569 | SHORT | RD | V | Harmonic U L1 | [33] | 0.1
3570 | SHORT | RD | V | Harmonic U L1 | [34] | 0.1
3571 | SHORT | RD | V | Harmonic U L1 | [35] | 0.1
3572 | SHORT | RD | V | Harmonic U L1 | [36] | 0.1
3573 | SHORT | RD | V | Harmonic U L1 | [37] | 0.1
3574 | SHORT | RD | V | Harmonic U L1 | [38] | 0.1
3575 | SHORT | RD | V | Harmonic U L1 | [39] | 0.1
3576 | SHORT | RD | V | Harmonic U L2 | [0] | 0.1
3577 | SHORT | RD | V | Harmonic U L2 | [1] | 0.1
3578 | SHORT | RD | V | Harmonic U L2 | [2] | 0.1
3579 | SHORT | RD | V | Harmonic U L2 | [3] | 0.1
3580 | SHORT | RD | V | Harmonic U L2 | [4] | 0.1
3581 | SHORT | RD | V | Harmonic U L2 | [5] | 0.1
3582 | SHORT | RD | V | Harmonic U L2 | [6] | 0.1
3583 | SHORT | RD | V | Harmonic U L2 | [7] | 0.1
3584 | SHORT | RD | V | Harmonic U L2 | [8] | 0.1
3585 | SHORT | RD | V | Harmonic U L2 | [9] | 0.1
3586 | SHORT | RD | V | Harmonic U L2 | [10] | 0.1
3587 | SHORT | RD | V | Harmonic U L2 | [11] | 0.1
3588 | SHORT | RD | V | Harmonic U L2 | [12] | 0.1
3589 | SHORT | RD | V | Harmonic U L2 | [13] | 0.1
3590 | SHORT | RD | V | Harmonic U L2 | [14] | 0.1
3591 | SHORT | RD | V | Harmonic U L2 | [15] | 0.1
3592 | SHORT | RD | V | Harmonic U L2 | [16] | 0.1
3593 | SHORT | RD | V | Harmonic U L2 | [17] | 0.1
3594 | SHORT | RD | V | Harmonic U L2 | [18] | 0.1
3595 | SHORT | RD | V | Harmonic U L2 | [19] | 0.1
3596 | SHORT | RD | V | Harmonic U L2 | [20] | 0.1
3597 | SHORT | RD | V | Harmonic U L2 | [21] | 0.1
3598 | SHORT | RD | V | Harmonic U L2 | [22] | 0.1
3599 | SHORT | RD | V | Harmonic U L2 | [23] | 0.1
3600 | SHORT | RD | V | Harmonic U L2 | [24] | 0.1
3601 | SHORT | RD | V | Harmonic U L2 | [25] | 0.1
3602 | SHORT | RD | V | Harmonic U L2 | [26] | 0.1
3603 | SHORT | RD | V | Harmonic U L2 | [27] | 0.1
3604 | SHORT | RD | V | Harmonic U L2 | [28] | 0.1
3605 | SHORT | RD | V | Harmonic U L2 | [29] | 0.1
3606 | SHORT | RD | V | Harmonic U L2 | [30] | 0.1
3607 | SHORT | RD | V | Harmonic U L2 | [31] | 0.1
3608 | SHORT | RD | V | Harmonic U L2 | [32] | 0.1
3609 | SHORT | RD | V | Harmonic U L2 | [33] | 0.1
3610 | SHORT | RD | V | Harmonic U L2 | [34] | 0.1
3611 | SHORT | RD | V | Harmonic U L2 | [35] | 0.1
3612 | SHORT | RD | V | Harmonic U L2 | [36] | 0.1
3613 | SHORT | RD | V | Harmonic U L2 | [37] | 0.1
3614 | SHORT | RD | V | Harmonic U L2 | [38] | 0.1
3615 | SHORT | RD | V | Harmonic U L2 | [39] | 0.1
3616 | SHORT | RD | V | Harmonic U L3 | [0] | 0.1
3617 | SHORT | RD | V | Harmonic U L3 | [1] | 0.1
3618 | SHORT | RD | V | Harmonic U L3 | [2] | 0.1
3619 | SHORT | RD | V | Harmonic U L3 | [3] | 0.1
3620 | SHORT | RD | V | Harmonic U L3 | [4] | 0.1
3621 | SHORT | RD | V | Harmonic U L3 | [5] | 0.1
3622 | SHORT | RD | V | Harmonic U L3 | [6] | 0.1
3623 | SHORT | RD | V | Harmonic U L3 | [7] | 0.1
3624 | SHORT | RD | V | Harmonic U L3 | [8] | 0.1
3625 | SHORT | RD | V | Harmonic U L3 | [9] | 0.1
3626 | SHORT | RD | V | Harmonic U L3 | [10] | 0.1
3627 | SHORT | RD | V | Harmonic U L3 | [11] | 0.1
3628 | SHORT | RD | V | Harmonic U L3 | [12] | 0.1
3629 | SHORT | RD | V | Harmonic U L3 | [13] | 0.1
3630 | SHORT | RD | V | Harmonic U L3 | [14] | 0.1
3631 | SHORT | RD | V | Harmonic U L3 | [15] | 0.1
3632 | SHORT | RD | V | Harmonic U L3 | [16] | 0.1
3633 | SHORT | RD | V | Harmonic U L3 | [17] | 0.1
3634 | SHORT | RD | V | Harmonic U L3 | [18] | 0.1
3635 | SHORT | RD | V | Harmonic U L3 | [19] | 0.1
3636 | SHORT | RD | V | Harmonic U L3 | [20] | 0.1
3637 | SHORT | RD | V | Harmonic U L3 | [21] | 0.1
3638 | SHORT | RD | V | Harmonic U L3 | [22] | 0.1
3639 | SHORT | RD | V | Harmonic U L3 | [23] | 0.1
3640 | SHORT | RD | V | Harmonic U L3 | [24] | 0.1
3641 | SHORT | RD | V | Harmonic U L3 | [25] | 0.1
3642 | SHORT | RD | V | Harmonic U L3 | [26] | 0.1
3643 | SHORT | RD | V | Harmonic U L3 | [27] | 0.1
3644 | SHORT | RD | V | Harmonic U L3 | [28] | 0.1
3645 | SHORT | RD | V | Harmonic U L3 | [29] | 0.1
3646 | SHORT | RD | V | Harmonic U L3 | [30] | 0.1
3647 | SHORT | RD | V | Harmonic U L3 | [31] | 0.1
3648 | SHORT | RD | V | Harmonic U L3 | [32] | 0.1
3649 | SHORT | RD | V | Harmonic U L3 | [33] | 0.1
3650 | SHORT | RD | V | Harmonic U L3 | [34] | 0.1
3651 | SHORT | RD | V | Harmonic U L3 | [35] | 0.1
3652 | SHORT | RD | V | Harmonic U L3 | [36] | 0.1
3653 | SHORT | RD | V | Harmonic U L3 | [37] | 0.1
3654 | SHORT | RD | V | Harmonic U L3 | [38] | 0.1
3655 | SHORT | RD | V | Harmonic U L3 | [39] | 0.1
3656 | SHORT | RD | V | Harmonic U L1-L2 | [0] | 0.1
3657 | SHORT | RD | V | Harmonic U L1-L2 | [1] | 0.1
3658 | SHORT | RD | V | Harmonic U L1-L2 | [2] | 0.1
3659 | SHORT | RD | V | Harmonic U L1-L2 | [3] | 0.1
3660 | SHORT | RD | V | Harmonic U L1-L2 | [4] | 0.1
3661 | SHORT | RD | V | Harmonic U L1-L2 | [5] | 0.1
3662 | SHORT | RD | V | Harmonic U L1-L2 | [6] | 0.1
3663 | SHORT | RD | V | Harmonic U L1-L2 | [7] | 0.1
3664 | SHORT | RD | V | Harmonic U L1-L2 | [8] | 0.1
3665 | SHORT | RD | V | Harmonic U L1-L2 | [9] | 0.1
3666 | SHORT | RD | V | Harmonic U L1-L2 | [10] | 0.1
3667 | SHORT | RD | V | Harmonic U L1-L2 | [11] | 0.1
3668 | SHORT | RD | V | Harmonic U L1-L2 | [12] | 0.1
3669 | SHORT | RD | V | Harmonic U L1-L2 | [13] | 0.1
3670 | SHORT | RD | V | Harmonic U L1-L2 | [14] | 0.1
3671 | SHORT | RD | V | Harmonic U L1-L2 | [15] | 0.1
3672 | SHORT | RD | V | Harmonic U L1-L2 | [16] | 0.1
3673 | SHORT | RD | V | Harmonic U L1-L2 | [17] | 0.1
3674 | SHORT | RD | V | Harmonic U L1-L2 | [18] | 0.1
3675 | SHORT | RD | V | Harmonic U L1-L2 | [19] | 0.1
3676 | SHORT | RD | V | Harmonic U L1-L2 | [20] | 0.1
3677 | SHORT | RD | V | Harmonic U L1-L2 | [21] | 0.1
3678 | SHORT | RD | V | Harmonic U L1-L2 | [22] | 0.1
3679 | SHORT | RD | V | Harmonic U L1-L2 | [23] | 0.1
3680 | SHORT | RD | V | Harmonic U L1-L2 | [24] | 0.1
3681 | SHORT | RD | V | Harmonic U L1-L2 | [25] | 0.1
3682 | SHORT | RD | V | Harmonic U L1-L2 | [26] | 0.1
3683 | SHORT | RD | V | Harmonic U L1-L2 | [27] | 0.1
3684 | SHORT | RD | V | Harmonic U L1-L2 | [28] | 0.1
3685 | SHORT | RD | V | Harmonic U L1-L2 | [29] | 0.1
3686 | SHORT | RD | V | Harmonic U L1-L2 | [30] | 0.1
3687 | SHORT | RD | V | Harmonic U L1-L2 | [31] | 0.1
3688 | SHORT | RD | V | Harmonic U L1-L2 | [32] | 0.1
3689 | SHORT | RD | V | Harmonic U L1-L2 | [33] | 0.1
3690 | SHORT | RD | V | Harmonic U L1-L2 | [34] | 0.1
3691 | SHORT | RD | V | Harmonic U L1-L2 | [35] | 0.1
3692 | SHORT | RD | V | Harmonic U L1-L2 | [36] | 0.1
3693 | SHORT | RD | V | Harmonic U L1-L2 | [37] | 0.1
3694 | SHORT | RD | V | Harmonic U L1-L2 | [38] | 0.1
3695 | SHORT | RD | V | Harmonic U L1-L2 | [39] | 0.1
3696 | SHORT | RD | V | Harmonic U L2-L3 | [0] | 0.1
3697 | SHORT | RD | V | Harmonic U L2-L3 | [1] | 0.1
3698 | SHORT | RD | V | Harmonic U L2-L3 | [2] | 0.1
3699 | SHORT | RD | V | Harmonic U L2-L3 | [3] | 0.1
3700 | SHORT | RD | V | Harmonic U L2-L3 | [4] | 0.1
3701 | SHORT | RD | V | Harmonic U L2-L3 | [5] | 0.1
3702 | SHORT | RD | V | Harmonic U L2-L3 | [6] | 0.1
3703 | SHORT | RD | V | Harmonic U L2-L3 | [7] | 0.1
3704 | SHORT | RD | V | Harmonic U L2-L3 | [8] | 0.1
3705 | SHORT | RD | V | Harmonic U L2-L3 | [9] | 0.1
3706 | SHORT | RD | V | Harmonic U L2-L3 | [10] | 0.1
3707 | SHORT | RD | V | Harmonic U L2-L3 | [11] | 0.1
3708 | SHORT | RD | V | Harmonic U L2-L3 | [12] | 0.1
3709 | SHORT | RD | V | Harmonic U L2-L3 | [13] | 0.1
3710 | SHORT | RD | V | Harmonic U L2-L3 | [14] | 0.1
3711 | SHORT | RD | V | Harmonic U L2-L3 | [15] | 0.1
3712 | SHORT | RD | V | Harmonic U L2-L3 | [16] | 0.1
3713 | SHORT | RD | V | Harmonic U L2-L3 | [17] | 0.1
3714 | SHORT | RD | V | Harmonic U L2-L3 | [18] | 0.1
3715 | SHORT | RD | V | Harmonic U L2-L3 | [19] | 0.1
3716 | SHORT | RD | V | Harmonic U L2-L3 | [20] | 0.1
3717 | SHORT | RD | V | Harmonic U L2-L3 | [21] | 0.1
3718 | SHORT | RD | V | Harmonic U L2-L3 | [22] | 0.1
3719 | SHORT | RD | V | Harmonic U L2-L3 | [23] | 0.1
3720 | SHORT | RD | V | Harmonic U L2-L3 | [24] | 0.1
3721 | SHORT | RD | V | Harmonic U L2-L3 | [25] | 0.1
3722 | SHORT | RD | V | Harmonic U L2-L3 | [26] | 0.1
3723 | SHORT | RD | V | Harmonic U L2-L3 | [27] | 0.1
3724 | SHORT | RD | V | Harmonic U L2-L3 | [28] | 0.1
3725 | SHORT | RD | V | Harmonic U L2-L3 | [29] | 0.1
3726 | SHORT | RD | V | Harmonic U L2-L3 | [30] | 0.1
3727 | SHORT | RD | V | Harmonic U L2-L3 | [31] | 0.1
3728 | SHORT | RD | V | Harmonic U L2-L3 | [32] | 0.1
3729 | SHORT | RD | V | Harmonic U L2-L3 | [33] | 0.1
3730 | SHORT | RD | V | Harmonic U L2-L3 | [34] | 0.1
3731 | SHORT | RD | V | Harmonic U L2-L3 | [35] | 0.1
3732 | SHORT | RD | V | Harmonic U L2-L3 | [36] | 0.1
3733 | SHORT | RD | V | Harmonic U L2-L3 | [37] | 0.1
3734 | SHORT | RD | V | Harmonic U L2-L3 | [38] | 0.1
3735 | SHORT | RD | V | Harmonic U L2-L3 | [39] | 0.1
3736 | SHORT | RD | V | Harmonic U L3-L1 | [0] | 0.1
3737 | SHORT | RD | V | Harmonic U L3-L1 | [1] | 0.1
3738 | SHORT | RD | V | Harmonic U L3-L1 | [2] | 0.1
3739 | SHORT | RD | V | Harmonic U L3-L1 | [3] | 0.1
3740 | SHORT | RD | V | Harmonic U L3-L1 | [4] | 0.1
3741 | SHORT | RD | V | Harmonic U L3-L1 | [5] | 0.1
3742 | SHORT | RD | V | Harmonic U L3-L1 | [6] | 0.1
3743 | SHORT | RD | V | Harmonic U L3-L1 | [7] | 0.1
3744 | SHORT | RD | V | Harmonic U L3-L1 | [8] | 0.1
3745 | SHORT | RD | V | Harmonic U L3-L1 | [9] | 0.1
3746 | SHORT | RD | V | Harmonic U L3-L1 | [10] | 0.1
3747 | SHORT | RD | V | Harmonic U L3-L1 | [11] | 0.1
3748 | SHORT | RD | V | Harmonic U L3-L1 | [12] | 0.1
3749 | SHORT | RD | V | Harmonic U L3-L1 | [13] | 0.1
3750 | SHORT | RD | V | Harmonic U L3-L1 | [14] | 0.1
3751 | SHORT | RD | V | Harmonic U L3-L1 | [15] | 0.1
3752 | SHORT | RD | V | Harmonic U L3-L1 | [16] | 0.1
3753 | SHORT | RD | V | Harmonic U L3-L1 | [17] | 0.1
3754 | SHORT | RD | V | Harmonic U L3-L1 | [18] | 0.1
3755 | SHORT | RD | V | Harmonic U L3-L1 | [19] | 0.1
3756 | SHORT | RD | V | Harmonic U L3-L1 | [20] | 0.1
3757 | SHORT | RD | V | Harmonic U L3-L1 | [21] | 0.1
3758 | SHORT | RD | V | Harmonic U L3-L1 | [22] | 0.1
3759 | SHORT | RD | V | Harmonic U L3-L1 | [23] | 0.1
3760 | SHORT | RD | V | Harmonic U L3-L1 | [24] | 0.1
3761 | SHORT | RD | V | Harmonic U L3-L1 | [25] | 0.1
3762 | SHORT | RD | V | Harmonic U L3-L1 | [26] | 0.1
3763 | SHORT | RD | V | Harmonic U L3-L1 | [27] | 0.1
3764 | SHORT | RD | V | Harmonic U L3-L1 | [28] | 0.1
3765 | SHORT | RD | V | Harmonic U L3-L1 | [29] | 0.1
3766 | SHORT | RD | V | Harmonic U L3-L1 | [30] | 0.1
3767 | SHORT | RD | V | Harmonic U L3-L1 | [31] | 0.1
3768 | SHORT | RD | V | Harmonic U L3-L1 | [32] | 0.1
3769 | SHORT | RD | V | Harmonic U L3-L1 | [33] | 0.1
3770 | SHORT | RD | V | Harmonic U L3-L1 | [34] | 0.1
3771 | SHORT | RD | V | Harmonic U L3-L1 | [35] | 0.1
3772 | SHORT | RD | V | Harmonic U L3-L1 | [36] | 0.1
3773 | SHORT | RD | V | Harmonic U L3-L1 | [37] | 0.1
3774 | SHORT | RD | V | Harmonic U L3-L1 | [38] | 0.1
3775 | SHORT | RD | V | Harmonic U L3-L1 | [39] | 0.1
3796 | SHORT | RD | mA | Harmonic I L1 | [0] | 1
3797 | SHORT | RD | mA | Harmonic I L1 | [1] | 1
3798 | SHORT | RD | mA | Harmonic I L1 | [2] | 1
3799 | SHORT | RD | mA | Harmonic I L1 | [3] | 1
3800 | SHORT | RD | mA | Harmonic I L1 | [4] | 1
3801 | SHORT | RD | mA | Harmonic I L1 | [5] | 1
3802 | SHORT | RD | mA | Harmonic I L1 | [6] | 1
3803 | SHORT | RD | mA | Harmonic I L1 | [7] | 1
3804 | SHORT | RD | mA | Harmonic I L1 | [8] | 1
3805 | SHORT | RD | mA | Harmonic I L1 | [9] | 1
3806 | SHORT | RD | mA | Harmonic I L1 | [10] | 1
3807 | SHORT | RD | mA | Harmonic I L1 | [11] | 1
3808 | SHORT | RD | mA | Harmonic I L1 | [12] | 1
3809 | SHORT | RD | mA | Harmonic I L1 | [13] | 1
3810 | SHORT | RD | mA | Harmonic I L1 | [14] | 1
3811 | SHORT | RD | mA | Harmonic I L1 | [15] | 1
3812 | SHORT | RD | mA | Harmonic I L1 | [16] | 1
3813 | SHORT | RD | mA | Harmonic I L1 | [17] | 1
3814 | SHORT | RD | mA | Harmonic I L1 | [18] | 1
3815 | SHORT | RD | mA | Harmonic I L1 | [19] | 1
3816 | SHORT | RD | mA | Harmonic I L1 | [20] | 1
3817 | SHORT | RD | mA | Harmonic I L1 | [21] | 1
3818 | SHORT | RD | mA | Harmonic I L1 | [22] | 1
3819 | SHORT | RD | mA | Harmonic I L1 | [23] | 1
3820 | SHORT | RD | mA | Harmonic I L1 | [24] | 1
3821 | SHORT | RD | mA | Harmonic I L1 | [25] | 1
3822 | SHORT | RD | mA | Harmonic I L1 | [26] | 1
3823 | SHORT | RD | mA | Harmonic I L1 | [27] | 1
3824 | SHORT | RD | mA | Harmonic I L1 | [28] | 1
3825 | SHORT | RD | mA | Harmonic I L1 | [29] | 1
3826 | SHORT | RD | mA | Harmonic I L1 | [30] | 1
3827 | SHORT | RD | mA | Harmonic I L1 | [31] | 1
3828 | SHORT | RD | mA | Harmonic I L1 | [32] | 1
3829 | SHORT | RD | mA | Harmonic I L1 | [33] | 1
3830 | SHORT | RD | mA | Harmonic I L1 | [34] | 1
3831 | SHORT | RD | mA | Harmonic I L1 | [35] | 1
3832 | SHORT | RD | mA | Harmonic I L1 | [36] | 1
3833 | SHORT | RD | mA | Harmonic I L1 | [37] | 1
3834 | SHORT | RD | mA | Harmonic I L1 | [38] | 1
3835 | SHORT | RD | mA | Harmonic I L1 | [39] | 1
3836 | SHORT | RD | mA | Harmonic I L2 | [0] | 1
3837 | SHORT | RD | mA | Harmonic I L2 | [1] | 1
3838 | SHORT | RD | mA | Harmonic I L2 | [2] | 1
3839 | SHORT | RD | mA | Harmonic I L2 | [3] | 1
3840 | SHORT | RD | mA | Harmonic I L2 | [4] | 1
3841 | SHORT | RD | mA | Harmonic I L2 | [5] | 1
3842 | SHORT | RD | mA | Harmonic I L2 | [6] | 1
3843 | SHORT | RD | mA | Harmonic I L2 | [7] | 1
3844 | SHORT | RD | mA | Harmonic I L2 | [8] | 1
3845 | SHORT | RD | mA | Harmonic I L2 | [9] | 1
3846 | SHORT | RD | mA | Harmonic I L2 | [10] | 1
3847 | SHORT | RD | mA | Harmonic I L2 | [11] | 1
3848 | SHORT | RD | mA | Harmonic I L2 | [12] | 1
3849 | SHORT | RD | mA | Harmonic I L2 | [13] | 1
3850 | SHORT | RD | mA | Harmonic I L2 | [14] | 1
3851 | SHORT | RD | mA | Harmonic I L2 | [15] | 1
3852 | SHORT | RD | mA | Harmonic I L2 | [16] | 1
3853 | SHORT | RD | mA | Harmonic I L2 | [17] | 1
3854 | SHORT | RD | mA | Harmonic I L2 | [18] | 1
3855 | SHORT | RD | mA | Harmonic I L2 | [19] | 1
3856 | SHORT | RD | mA | Harmonic I L2 | [20] | 1
3857 | SHORT | RD | mA | Harmonic I L2 | [21] | 1
3858 | SHORT | RD | mA | Harmonic I L2 | [22] | 1
3859 | SHORT | RD | mA | Harmonic I L2 | [23] | 1
3860 | SHORT | RD | mA | Harmonic I L2 | [24] | 1
3861 | SHORT | RD | mA | Harmonic I L2 | [25] | 1
3862 | SHORT | RD | mA | Harmonic I L2 | [26] | 1
3863 | SHORT | RD | mA | Harmonic I L2 | [27] | 1
3864 | SHORT | RD | mA | Harmonic I L2 | [28] | 1
3865 | SHORT | RD | mA | Harmonic I L2 | [29] | 1
3866 | SHORT | RD | mA | Harmonic I L2 | [30] | 1
3867 | SHORT | RD | mA | Harmonic I L2 | [31] | 1
3868 | SHORT | RD | mA | Harmonic I L2 | [32] | 1
3869 | SHORT | RD | mA | Harmonic I L2 | [33] | 1
3870 | SHORT | RD | mA | Harmonic I L2 | [34] | 1
3871 | SHORT | RD | mA | Harmonic I L2 | [35] | 1
3872 | SHORT | RD | mA | Harmonic I L2 | [36] | 1
3873 | SHORT | RD | mA | Harmonic I L2 | [37] | 1
3874 | SHORT | RD | mA | Harmonic I L2 | [38] | 1
3875 | SHORT | RD | mA | Harmonic I L2 | [39] | 1
3876 | SHORT | RD | mA | Harmonic I L3 | [0] | 1
3877 | SHORT | RD | mA | Harmonic I L3 | [1] | 1
3878 | SHORT | RD | mA | Harmonic I L3 | [2] | 1
3879 | SHORT | RD | mA | Harmonic I L3 | [3] | 1
3880 | SHORT | RD | mA | Harmonic I L3 | [4] | 1
3881 | SHORT | RD | mA | Harmonic I L3 | [5] | 1
3882 | SHORT | RD | mA | Harmonic I L3 | [6] | 1
3883 | SHORT | RD | mA | Harmonic I L3 | [7] | 1
3884 | SHORT | RD | mA | Harmonic I L3 | [8] | 1
3885 | SHORT | RD | mA | Harmonic I L3 | [9] | 1
3886 | SHORT | RD | mA | Harmonic I L3 | [10] | 1
3887 | SHORT | RD | mA | Harmonic I L3 | [11] | 1
3888 | SHORT | RD | mA | Harmonic I L3 | [12] | 1
3889 | SHORT | RD | mA | Harmonic I L3 | [13] | 1
3890 | SHORT | RD | mA | Harmonic I L3 | [14] | 1
3891 | SHORT | RD | mA | Harmonic I L3 | [15] | 1
3892 | SHORT | RD | mA | Harmonic I L3 | [16] | 1
3893 | SHORT | RD | mA | Harmonic I L3 | [17] | 1
3894 | SHORT | RD | mA | Harmonic I L3 | [18] | 1
3895 | SHORT | RD | mA | Harmonic I L3 | [19] | 1
3896 | SHORT | RD | mA | Harmonic I L3 | [20] | 1
3897 | SHORT | RD | mA | Harmonic I L3 | [21] | 1
3898 | SHORT | RD | mA | Harmonic I L3 | [22] | 1
3899 | SHORT | RD | mA | Harmonic I L3 | [23] | 1
3900 | SHORT | RD | mA | Harmonic I L3 | [24] | 1
3901 | SHORT | RD | mA | Harmonic I L3 | [25] | 1
3902 | SHORT | RD | mA | Harmonic I L3 | [26] | 1
3903 | SHORT | RD | mA | Harmonic I L3 | [27] | 1
3904 | SHORT | RD | mA | Harmonic I L3 | [28] | 1
3905 | SHORT | RD | mA | Harmonic I L3 | [29] | 1
3906 | SHORT | RD | mA | Harmonic I L3 | [30] | 1
3907 | SHORT | RD | mA | Harmonic I L3 | [31] | 1
3908 | SHORT | RD | mA | Harmonic I L3 | [32] | 1
3909 | SHORT | RD | mA | Harmonic I L3 | [33] | 1
3910 | SHORT | RD | mA | Harmonic I L3 | [34] | 1
3911 | SHORT | RD | mA | Harmonic I L3 | [35] | 1
3912 | SHORT | RD | mA | Harmonic I L3 | [36] | 1
3913 | SHORT | RD | mA | Harmonic I L3 | [37] | 1
3914 | SHORT | RD | mA | Harmonic I L3 | [38] | 1
3915 | SHORT | RD | mA | Harmonic I L3 | [39] | 1
Mean values, type float, fourier analysis
Address | Format | RD/WR | Unit | Note | Index
1740 | FLOAT | RD | V | Average, Harmonic U L1 | [0]
1742 | FLOAT | RD | V | Average, Harmonic U L1 | [1]
1744 | FLOAT | RD | V | Average, Harmonic U L1 | [2]
1746 | FLOAT | RD | V | Average, Harmonic U L1 | [3]
1748 | FLOAT | RD | V | Average, Harmonic U L1 | [4]
1750 | FLOAT | RD | V | Average, Harmonic U L1 | [5]
1752 | FLOAT | RD | V | Average, Harmonic U L1 | [6]
1754 | FLOAT | RD | V | Average, Harmonic U L1 | [7]
1756 | FLOAT | RD | V | Average, Harmonic U L1 | [8]
1758 | FLOAT | RD | V | Average, Harmonic U L1 | [9]
1760 | FLOAT | RD | V | Average, Harmonic U L1 | [10]
1762 | FLOAT | RD | V | Average, Harmonic U L1 | [11]
1764 | FLOAT | RD | V | Average, Harmonic U L1 | [12]
1766 | FLOAT | RD | V | Average, Harmonic U L1 | [13]
1768 | FLOAT | RD | V | Average, Harmonic U L1 | [14]
1770 | FLOAT | RD | V | Average, Harmonic U L1 | [15]
1772 | FLOAT | RD | V | Average, Harmonic U L1 | [16]
1774 | FLOAT | RD | V | Average, Harmonic U L1 | [17]
1776 | FLOAT | RD | V | Average, Harmonic U L1 | [18]
1778 | FLOAT | RD | V | Average, Harmonic U L1 | [19]
1780 | FLOAT | RD | V | Average, Harmonic U L1 | [20]
1782 | FLOAT | RD | V | Average, Harmonic U L1 | [21]
1784 | FLOAT | RD | V | Average, Harmonic U L1 | [22]
1786 | FLOAT | RD | V | Average, Harmonic U L1 | [23]
1788 | FLOAT | RD | V | Average, Harmonic U L1 | [24]
1790 | FLOAT | RD | V | Average, Harmonic U L1 | [25]
1792 | FLOAT | RD | V | Average, Harmonic U L1 | [26]
1794 | FLOAT | RD | V | Average, Harmonic U L1 | [27]
1796 | FLOAT | RD | V | Average, Harmonic U L1 | [28]
1798 | FLOAT | RD | V | Average, Harmonic U L1 | [29]
1800 | FLOAT | RD | V | Average, Harmonic U L1 | [30]
1802 | FLOAT | RD | V | Average, Harmonic U L1 | [31]
1804 | FLOAT | RD | V | Average, Harmonic U L1 | [32]
1806 | FLOAT | RD | V | Average, Harmonic U L1 | [33]
1808 | FLOAT | RD | V | Average, Harmonic U L1 | [34]
1810 | FLOAT | RD | V | Average, Harmonic U L1 | [35]
1812 | FLOAT | RD | V | Average, Harmonic U L1 | [36]
1814 | FLOAT | RD | V | Average, Harmonic U L1 | [37]
1816 | FLOAT | RD | V | Average, Harmonic U L1 | [38]
1818 | FLOAT | RD | V | Average, Harmonic U L1 | [39]
1820 | FLOAT | RD | V | Average, Harmonic U L2 | [0]
1822 | FLOAT | RD | V | Average, Harmonic U L2 | [1]
1824 | FLOAT | RD | V | Average, Harmonic U L2 | [2]
1826 | FLOAT | RD | V | Average, Harmonic U L2 | [3]
1828 | FLOAT | RD | V | Average, Harmonic U L2 | [4]
1830 | FLOAT | RD | V | Average, Harmonic U L2 | [5]
1832 | FLOAT | RD | V | Average, Harmonic U L2 | [6]
1834 | FLOAT | RD | V | Average, Harmonic U L2 | [7]
1836 | FLOAT | RD | V | Average, Harmonic U L2 | [8]
1838 | FLOAT | RD | V | Average, Harmonic U L2 | [9]
1840 | FLOAT | RD | V | Average, Harmonic U L2 | [10]
1842 | FLOAT | RD | V | Average, Harmonic U L2 | [11]
1844 | FLOAT | RD | V | Average, Harmonic U L2 | [12]
1846 | FLOAT | RD | V | Average, Harmonic U L2 | [13]
1848 | FLOAT | RD | V | Average, Harmonic U L2 | [14]
1850 | FLOAT | RD | V | Average, Harmonic U L2 | [15]
1852 | FLOAT | RD | V | Average, Harmonic U L2 | [16]
1854 | FLOAT | RD | V | Average, Harmonic U L2 | [17]
1856 | FLOAT | RD | V | Average, Harmonic U L2 | [18]
1858 | FLOAT | RD | V | Average, Harmonic U L2 | [19]
1860 | FLOAT | RD | V | Average, Harmonic U L2 | [20]
1862 | FLOAT | RD | V | Average, Harmonic U L2 | [21]
1864 | FLOAT | RD | V | Average, Harmonic U L2 | [22]
1866 | FLOAT | RD | V | Average, Harmonic U L2 | [23]
1868 | FLOAT | RD | V | Average, Harmonic U L2 | [24]
1870 | FLOAT | RD | V | Average, Harmonic U L2 | [25]
1872 | FLOAT | RD | V | Average, Harmonic U L2 | [26]
1874 | FLOAT | RD | V | Average, Harmonic U L2 | [27]
1876 | FLOAT | RD | V | Average, Harmonic U L2 | [28]
1878 | FLOAT | RD | V | Average, Harmonic U L2 | [29]
1880 | FLOAT | RD | V | Average, Harmonic U L2 | [30]
1882 | FLOAT | RD | V | Average, Harmonic U L2 | [31]
1884 | FLOAT | RD | V | Average, Harmonic U L2 | [32]
1886 | FLOAT | RD | V | Average, Harmonic U L2 | [33]
1888 | FLOAT | RD | V | Average, Harmonic U L2 | [34]
1890 | FLOAT | RD | V | Average, Harmonic U L2 | [35]
1892 | FLOAT | RD | V | Average, Harmonic U L2 | [36]
1894 | FLOAT | RD | V | Average, Harmonic U L2 | [37]
1896 | FLOAT | RD | V | Average, Harmonic U L2 | [38]
1898 | FLOAT | RD | V | Average, Harmonic U L2 | [39]
1900 | FLOAT | RD | V | Average, Harmonic U L3 | [0]
1902 | FLOAT | RD | V | Average, Harmonic U L3 | [1]
1904 | FLOAT | RD | V | Average, Harmonic U L3 | [2]
1906 | FLOAT | RD | V | Average, Harmonic U L3 | [3]
1908 | FLOAT | RD | V | Average, Harmonic U L3 | [4]
1910 | FLOAT | RD | V | Average, Harmonic U L3 | [5]
1912 | FLOAT | RD | V | Average, Harmonic U L3 | [6]
1914 | FLOAT | RD | V | Average, Harmonic U L3 | [7]
1916 | FLOAT | RD | V | Average, Harmonic U L3 | [8]
1918 | FLOAT | RD | V | Average, Harmonic U L3 | [9]
1920 | FLOAT | RD | V | Average, Harmonic U L3 | [10]
1922 | FLOAT | RD | V | Average, Harmonic U L3 | [11]
1924 | FLOAT | RD | V | Average, Harmonic U L3 | [12]
1926 | FLOAT | RD | V | Average, Harmonic U L3 | [13]
1928 | FLOAT | RD | V | Average, Harmonic U L3 | [14]
1930 | FLOAT | RD | V | Average, Harmonic U L3 | [15]
1932 | FLOAT | RD | V | Average, Harmonic U L3 | [16]
1934 | FLOAT | RD | V | Average, Harmonic U L3 | [17]
1936 | FLOAT | RD | V | Average, Harmonic U L3 | [18]
1938 | FLOAT | RD | V | Average, Harmonic U L3 | [19]
1940 | FLOAT | RD | V | Average, Harmonic U L3 | [20]
1942 | FLOAT | RD | V | Average, Harmonic U L3 | [21]
1944 | FLOAT | RD | V | Average, Harmonic U L3 | [22]
1946 | FLOAT | RD | V | Average, Harmonic U L3 | [23]
1948 | FLOAT | RD | V | Average, Harmonic U L3 | [24]
1950 | FLOAT | RD | V | Average, Harmonic U L3 | [25]
1952 | FLOAT | RD | V | Average, Harmonic U L3 | [26]
1954 | FLOAT | RD | V | Average, Harmonic U L3 | [27]
1956 | FLOAT | RD | V | Average, Harmonic U L3 | [28]
1958 | FLOAT | RD | V | Average, Harmonic U L3 | [29]
1960 | FLOAT | RD | V | Average, Harmonic U L3 | [30]
1962 | FLOAT | RD | V | Average, Harmonic U L3 | [31]
1964 | FLOAT | RD | V | Average, Harmonic U L3 | [32]
1966 | FLOAT | RD | V | Average, Harmonic U L3 | [33]
1968 | FLOAT | RD | V | Average, Harmonic U L3 | [34]
1970 | FLOAT | RD | V | Average, Harmonic U L3 | [35]
1972 | FLOAT | RD | V | Average, Harmonic U L3 | [36]
1974 | FLOAT | RD | V | Average, Harmonic U L3 | [37]
1976 | FLOAT | RD | V | Average, Harmonic U L3 | [38]
1978 | FLOAT | RD | V | Average, Harmonic U L3 | [39]
1980 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [0]
1982 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [1]
1984 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [2]
1986 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [3]
1988 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [4]
1990 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [5]
1992 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [6]
1994 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [7]
1996 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [8]
1998 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [9]
2000 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [10]
2002 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [11]
2004 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [12]
2006 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [13]
2008 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [14]
2010 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [15]
2012 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [16]
2014 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [17]
2016 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [18]
2018 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [19]
2020 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [20]
2022 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [21]
2024 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [22]
2026 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [23]
2028 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [24]
2030 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [25]
2032 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [26]
2034 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [27]
2036 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [28]
2038 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [29]
2040 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [30]
2042 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [31]
2044 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [32]
2046 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [33]
2048 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [34]
2050 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [35]
2052 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [36]
2054 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [37]
2056 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [38]
2058 | FLOAT | RD | V | Average, Harmonic U L1-L2 | [39]
2060 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [0]
2062 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [1]
2064 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [2]
2066 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [3]
2068 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [4]
2070 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [5]
2072 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [6]
2074 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [7]
2076 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [8]
2078 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [9]
2080 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [10]
2082 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [11]
2084 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [12]
2086 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [13]
2088 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [14]
2090 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [15]
2092 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [16]
2094 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [17]
2096 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [18]
2098 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [19]
2100 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [20]
2102 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [21]
2104 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [22]
2106 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [23]
2108 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [24]
2110 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [25]
2112 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [26]
2114 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [27]
2116 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [28]
2118 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [29]
2120 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [30]
2122 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [31]
2124 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [32]
2126 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [33]
2128 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [34]
2130 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [35]
2132 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [36]
2134 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [37]
2136 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [38]
2138 | FLOAT | RD | V | Average, Harmonic U L2-L3 | [39]
2140 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [0]
2142 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [1]
2144 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [2]
2146 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [3]
2148 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [4]
2150 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [5]
2152 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [6]
2154 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [7]
2156 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [8]
2158 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [9]
2160 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [10]
2162 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [11]
2164 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [12]
2166 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [13]
2168 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [14]
2170 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [15]
2172 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [16]
2174 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [17]
2176 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [18]
2178 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [19]
2180 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [20]
2182 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [21]
2184 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [22]
2186 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [23]
2188 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [24]
2190 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [25]
2192 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [26]
2194 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [27]
2196 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [28]
2198 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [29]
2200 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [30]
2202 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [31]
2204 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [32]
2206 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [33]
2208 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [34]
2210 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [35]
2212 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [36]
2214 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [37]
2216 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [38]
2218 | FLOAT | RD | V | Average, Harmonic U L3-L1 | [39]
2260 | FLOAT | RD | A | Average, Harmonic I L1 | [0]
2262 | FLOAT | RD | A | Average, Harmonic I L1 | [1]
2264 | FLOAT | RD | A | Average, Harmonic I L1 | [2]
2266 | FLOAT | RD | A | Average, Harmonic I L1 | [3]
2268 | FLOAT | RD | A | Average, Harmonic I L1 | [4]
2270 | FLOAT | RD | A | Average, Harmonic I L1 | [5]
2272 | FLOAT | RD | A | Average, Harmonic I L1 | [6]
2274 | FLOAT | RD | A | Average, Harmonic I L1 | [7]
2276 | FLOAT | RD | A | Average, Harmonic I L1 | [8]
2278 | FLOAT | RD | A | Average, Harmonic I L1 | [9]
2280 | FLOAT | RD | A | Average, Harmonic I L1 | [10]
2282 | FLOAT | RD | A | Average, Harmonic I L1 | [11]
2284 | FLOAT | RD | A | Average, Harmonic I L1 | [12]
2286 | FLOAT | RD | A | Average, Harmonic I L1 | [13]
2288 | FLOAT | RD | A | Average, Harmonic I L1 | [14]
2290 | FLOAT | RD | A | Average, Harmonic I L1 | [15]
2292 | FLOAT | RD | A | Average, Harmonic I L1 | [16]
2294 | FLOAT | RD | A | Average, Harmonic I L1 | [17]
2296 | FLOAT | RD | A | Average, Harmonic I L1 | [18]
2298 | FLOAT | RD | A | Average, Harmonic I L1 | [19]
2300 | FLOAT | RD | A | Average, Harmonic I L1 | [20]
2302 | FLOAT | RD | A | Average, Harmonic I L1 | [21]
2304 | FLOAT | RD | A | Average, Harmonic I L1 | [22]
2306 | FLOAT | RD | A | Average, Harmonic I L1 | [23]
2308 | FLOAT | RD | A | Average, Harmonic I L1 | [24]
2310 | FLOAT | RD | A | Average, Harmonic I L1 | [25]
2312 | FLOAT | RD | A | Average, Harmonic I L1 | [26]
2314 | FLOAT | RD | A | Average, Harmonic I L1 | [27]
2316 | FLOAT | RD | A | Average, Harmonic I L1 | [28]
2318 | FLOAT | RD | A | Average, Harmonic I L1 | [29]
2320 | FLOAT | RD | A | Average, Harmonic I L1 | [30]
2322 | FLOAT | RD | A | Average, Harmonic I L1 | [31]
2324 | FLOAT | RD | A | Average, Harmonic I L1 | [32]
2326 | FLOAT | RD | A | Average, Harmonic I L1 | [33]
2328 | FLOAT | RD | A | Average, Harmonic I L1 | [34]
2330 | FLOAT | RD | A | Average, Harmonic I L1 | [35]
2332 | FLOAT | RD | A | Average, Harmonic I L1 | [36]
2334 | FLOAT | RD | A | Average, Harmonic I L1 | [37]
2336 | FLOAT | RD | A | Average, Harmonic I L1 | [38]
2338 | FLOAT | RD | A | Average, Harmonic I L1 | [39]
2340 | FLOAT | RD | A | Average, Harmonic I L2 | [0]
2342 | FLOAT | RD | A | Average, Harmonic I L2 | [1]
2344 | FLOAT | RD | A | Average, Harmonic I L2 | [2]
2346 | FLOAT | RD | A | Average, Harmonic I L2 | [3]
2348 | FLOAT | RD | A | Average, Harmonic I L2 | [4]
2350 | FLOAT | RD | A | Average, Harmonic I L2 | [5]
2352 | FLOAT | RD | A | Average, Harmonic I L2 | [6]
2354 | FLOAT | RD | A | Average, Harmonic I L2 | [7]
2356 | FLOAT | RD | A | Average, Harmonic I L2 | [8]
2358 | FLOAT | RD | A | Average, Harmonic I L2 | [9]
2360 | FLOAT | RD | A | Average, Harmonic I L2 | [10]
2362 | FLOAT | RD | A | Average, Harmonic I L2 | [11]
2364 | FLOAT | RD | A | Average, Harmonic I L2 | [12]
2366 | FLOAT | RD | A | Average, Harmonic I L2 | [13]
2368 | FLOAT | RD | A | Average, Harmonic I L2 | [14]
2370 | FLOAT | RD | A | Average, Harmonic I L2 | [15]
2372 | FLOAT | RD | A | Average, Harmonic I L2 | [16]
2374 | FLOAT | RD | A | Average, Harmonic I L2 | [17]
2376 | FLOAT | RD | A | Average, Harmonic I L2 | [18]
2378 | FLOAT | RD | A | Average, Harmonic I L2 | [19]
2380 | FLOAT | RD | A | Average, Harmonic I L2 | [20]
2382 | FLOAT | RD | A | Average, Harmonic I L2 | [21]
2384 | FLOAT | RD | A | Average, Harmonic I L2 | [22]
2386 | FLOAT | RD | A | Average, Harmonic I L2 | [23]
2388 | FLOAT | RD | A | Average, Harmonic I L2 | [24]
2390 | FLOAT | RD | A | Average, Harmonic I L2 | [25]
2392 | FLOAT | RD | A | Average, Harmonic I L2 | [26]
2394 | FLOAT | RD | A | Average, Harmonic I L2 | [27]
2396 | FLOAT | RD | A | Average, Harmonic I L2 | [28]
2398 | FLOAT | RD | A | Average, Harmonic I L2 | [29]
2400 | FLOAT | RD | A | Average, Harmonic I L2 | [30]
2402 | FLOAT | RD | A | Average, Harmonic I L2 | [31]
2404 | FLOAT | RD | A | Average, Harmonic I L2 | [32]
2406 | FLOAT | RD | A | Average, Harmonic I L2 | [33]
2408 | FLOAT | RD | A | Average, Harmonic I L2 | [34]
2410 | FLOAT | RD | A | Average, Harmonic I L2 | [35]
2412 | FLOAT | RD | A | Average, Harmonic I L2 | [36]
2414 | FLOAT | RD | A | Average, Harmonic I L2 | [37]
2416 | FLOAT | RD | A | Average, Harmonic I L2 | [38]
2418 | FLOAT | RD | A | Average, Harmonic I L2 | [39]
2420 | FLOAT | RD | A | Average, Harmonic I L3 | [0]
2422 | FLOAT | RD | A | Average, Harmonic I L3 | [1]
2424 | FLOAT | RD | A | Average, Harmonic I L3 | [2]
2426 | FLOAT | RD | A | Average, Harmonic I L3 | [3]
2428 | FLOAT | RD | A | Average, Harmonic I L3 | [4]
2430 | FLOAT | RD | A | Average, Harmonic I L3 | [5]
2432 | FLOAT | RD | A | Average, Harmonic I L3 | [6]
2434 | FLOAT | RD | A | Average, Harmonic I L3 | [7]
2436 | FLOAT | RD | A | Average, Harmonic I L3 | [8]
2438 | FLOAT | RD | A | Average, Harmonic I L3 | [9]
2440 | FLOAT | RD | A | Average, Harmonic I L3 | [10]
2442 | FLOAT | RD | A | Average, Harmonic I L3 | [11]
2444 | FLOAT | RD | A | Average, Harmonic I L3 | [12]
2446 | FLOAT | RD | A | Average, Harmonic I L3 | [13]
2448 | FLOAT | RD | A | Average, Harmonic I L3 | [14]
2450 | FLOAT | RD | A | Average, Harmonic I L3 | [15]
2452 | FLOAT | RD | A | Average, Harmonic I L3 | [16]
2454 | FLOAT | RD | A | Average, Harmonic I L3 | [17]
2456 | FLOAT | RD | A | Average, Harmonic I L3 | [18]
2458 | FLOAT | RD | A | Average, Harmonic I L3 | [19]
2460 | FLOAT | RD | A | Average, Harmonic I L3 | [20]
2462 | FLOAT | RD | A | Average, Harmonic I L3 | [21]
2464 | FLOAT | RD | A | Average, Harmonic I L3 | [22]
2466 | FLOAT | RD | A | Average, Harmonic I L3 | [23]
2468 | FLOAT | RD | A | Average, Harmonic I L3 | [24]
2470 | FLOAT | RD | A | Average, Harmonic I L3 | [25]
2472 | FLOAT | RD | A | Average, Harmonic I L3 | [26]
2474 | FLOAT | RD | A | Average, Harmonic I L3 | [27]
2476 | FLOAT | RD | A | Average, Harmonic I L3 | [28]
2478 | FLOAT | RD | A | Average, Harmonic I L3 | [29]
2480 | FLOAT | RD | A | Average, Harmonic I L3 | [30]
2482 | FLOAT | RD | A | Average, Harmonic I L3 | [31]
2484 | FLOAT | RD | A | Average, Harmonic I L3 | [32]
2486 | FLOAT | RD | A | Average, Harmonic I L3 | [33]
2488 | FLOAT | RD | A | Average, Harmonic I L3 | [34]
2490 | FLOAT | RD | A | Average, Harmonic I L3 | [35]
2492 | FLOAT | RD | A | Average, Harmonic I L3 | [36]
2494 | FLOAT | RD | A | Average, Harmonic I L3 | [37]
2496 | FLOAT | RD | A | Average, Harmonic I L3 | [38]
2498 | FLOAT | RD | A | Average, Harmonic I L3 | [39]
Mean values, type short, fourier analysis
Address | Format | RD/WR | Unit | Note | Index | Resolution
3966 | SHORT | RD | V | Average, Harmonic U L1 | [0] | 0.1
3967 | SHORT | RD | V | Average, Harmonic U L1 | [1] | 0.1
3968 | SHORT | RD | V | Average, Harmonic U L1 | [2] | 0.1
3969 | SHORT | RD | V | Average, Harmonic U L1 | [3] | 0.1
3970 | SHORT | RD | V | Average, Harmonic U L1 | [4] | 0.1
3971 | SHORT | RD | V | Average, Harmonic U L1 | [5] | 0.1
3972 | SHORT | RD | V | Average, Harmonic U L1 | [6] | 0.1
3973 | SHORT | RD | V | Average, Harmonic U L1 | [7] | 0.1
3974 | SHORT | RD | V | Average, Harmonic U L1 | [8] | 0.1
3975 | SHORT | RD | V | Average, Harmonic U L1 | [9] | 0.1
3976 | SHORT | RD | V | Average, Harmonic U L1 | [10] | 0.1
3977 | SHORT | RD | V | Average, Harmonic U L1 | [11] | 0.1
3978 | SHORT | RD | V | Average, Harmonic U L1 | [12] | 0.1
3979 | SHORT | RD | V | Average, Harmonic U L1 | [13] | 0.1
3980 | SHORT | RD | V | Average, Harmonic U L1 | [14] | 0.1
3981 | SHORT | RD | V | Average, Harmonic U L1 | [15] | 0.1
3982 | SHORT | RD | V | Average, Harmonic U L1 | [16] | 0.1
3983 | SHORT | RD | V | Average, Harmonic U L1 | [17] | 0.1
3984 | SHORT | RD | V | Average, Harmonic U L1 | [18] | 0.1
3985 | SHORT | RD | V | Average, Harmonic U L1 | [19] | 0.1
3986 | SHORT | RD | V | Average, Harmonic U L1 | [20] | 0.1
3987 | SHORT | RD | V | Average, Harmonic U L1 | [21] | 0.1
3988 | SHORT | RD | V | Average, Harmonic U L1 | [22] | 0.1
3989 | SHORT | RD | V | Average, Harmonic U L1 | [23] | 0.1
3990 | SHORT | RD | V | Average, Harmonic U L1 | [24] | 0.1
3991 | SHORT | RD | V | Average, Harmonic U L1 | [25] | 0.1
3992 | SHORT | RD | V | Average, Harmonic U L1 | [26] | 0.1
3993 | SHORT | RD | V | Average, Harmonic U L1 | [27] | 0.1
3994 | SHORT | RD | V | Average, Harmonic U L1 | [28] | 0.1
3995 | SHORT | RD | V | Average, Harmonic U L1 | [29] | 0.1
3996 | SHORT | RD | V | Average, Harmonic U L1 | [30] | 0.1
3997 | SHORT | RD | V | Average, Harmonic U L1 | [31] | 0.1
3998 | SHORT | RD | V | Average, Harmonic U L1 | [32] | 0.1
3999 | SHORT | RD | V | Average, Harmonic U L1 | [33] | 0.1
4000 | SHORT | RD | V | Average, Harmonic U L1 | [34] | 0.1
4001 | SHORT | RD | V | Average, Harmonic U L1 | [35] | 0.1
4002 | SHORT | RD | V | Average, Harmonic U L1 | [36] | 0.1
4003 | SHORT | RD | V | Average, Harmonic U L1 | [37] | 0.1
4004 | SHORT | RD | V | Average, Harmonic U L1 | [38] | 0.1
4005 | SHORT | RD | V | Average, Harmonic U L1 | [39] | 0.1
4006 | SHORT | RD | V | Average, Harmonic U L2 | [0] | 0.1
4007 | SHORT | RD | V | Average, Harmonic U L2 | [1] | 0.1
4008 | SHORT | RD | V | Average, Harmonic U L2 | [2] | 0.1
4009 | SHORT | RD | V | Average, Harmonic U L2 | [3] | 0.1
4010 | SHORT | RD | V | Average, Harmonic U L2 | [4] | 0.1
4011 | SHORT | RD | V | Average, Harmonic U L2 | [5] | 0.1
4012 | SHORT | RD | V | Average, Harmonic U L2 | [6] | 0.1
4013 | SHORT | RD | V | Average, Harmonic U L2 | [7] | 0.1
4014 | SHORT | RD | V | Average, Harmonic U L2 | [8] | 0.1
4015 | SHORT | RD | V | Average, Harmonic U L2 | [9] | 0.1
4016 | SHORT | RD | V | Average, Harmonic U L2 | [10] | 0.1
4017 | SHORT | RD | V | Average, Harmonic U L2 | [11] | 0.1
4018 | SHORT | RD | V | Average, Harmonic U L2 | [12] | 0.1
4019 | SHORT | RD | V | Average, Harmonic U L2 | [13] | 0.1
4020 | SHORT | RD | V | Average, Harmonic U L2 | [14] | 0.1
4021 | SHORT | RD | V | Average, Harmonic U L2 | [15] | 0.1
4022 | SHORT | RD | V | Average, Harmonic U L2 | [16] | 0.1
4023 | SHORT | RD | V | Average, Harmonic U L2 | [17] | 0.1
4024 | SHORT | RD | V | Average, Harmonic U L2 | [18] | 0.1
4025 | SHORT | RD | V | Average, Harmonic U L2 | [19] | 0.1
4026 | SHORT | RD | V | Average, Harmonic U L2 | [20] | 0.1
4027 | SHORT | RD | V | Average, Harmonic U L2 | [21] | 0.1
4028 | SHORT | RD | V | Average, Harmonic U L2 | [22] | 0.1
4029 | SHORT | RD | V | Average, Harmonic U L2 | [23] | 0.1
4030 | SHORT | RD | V | Average, Harmonic U L2 | [24] | 0.1
4031 | SHORT | RD | V | Average, Harmonic U L2 | [25] | 0.1
4032 | SHORT | RD | V | Average, Harmonic U L2 | [26] | 0.1
4033 | SHORT | RD | V | Average, Harmonic U L2 | [27] | 0.1
4034 | SHORT | RD | V | Average, Harmonic U L2 | [28] | 0.1
4035 | SHORT | RD | V | Average, Harmonic U L2 | [29] | 0.1
4036 | SHORT | RD | V | Average, Harmonic U L2 | [30] | 0.1
4037 | SHORT | RD | V | Average, Harmonic U L2 | [31] | 0.1
4038 | SHORT | RD | V | Average, Harmonic U L2 | [32] | 0.1
4039 | SHORT | RD | V | Average, Harmonic U L2 | [33] | 0.1
4040 | SHORT | RD | V | Average, Harmonic U L2 | [34] | 0.1
4041 | SHORT | RD | V | Average, Harmonic U L2 | [35] | 0.1
4042 | SHORT | RD | V | Average, Harmonic U L2 | [36] | 0.1
4043 | SHORT | RD | V | Average, Harmonic U L2 | [37] | 0.1
4044 | SHORT | RD | V | Average, Harmonic U L2 | [38] | 0.1
4045 | SHORT | RD | V | Average, Harmonic U L2 | [39] | 0.1
4046 | SHORT | RD | V | Average, Harmonic U L3 | [0] | 0.1
4047 | SHORT | RD | V | Average, Harmonic U L3 | [1] | 0.1
4048 | SHORT | RD | V | Average, Harmonic U L3 | [2] | 0.1
4049 | SHORT | RD | V | Average, Harmonic U L3 | [3] | 0.1
4050 | SHORT | RD | V | Average, Harmonic U L3 | [4] | 0.1
4051 | SHORT | RD | V | Average, Harmonic U L3 | [5] | 0.1
4052 | SHORT | RD | V | Average, Harmonic U L3 | [6] | 0.1
4053 | SHORT | RD | V | Average, Harmonic U L3 | [7] | 0.1
4054 | SHORT | RD | V | Average, Harmonic U L3 | [8] | 0.1
4055 | SHORT | RD | V | Average, Harmonic U L3 | [9] | 0.1
4056 | SHORT | RD | V | Average, Harmonic U L3 | [10] | 0.1
4057 | SHORT | RD | V | Average, Harmonic U L3 | [11] | 0.1
4058 | SHORT | RD | V | Average, Harmonic U L3 | [12] | 0.1
4059 | SHORT | RD | V | Average, Harmonic U L3 | [13] | 0.1
4060 | SHORT | RD | V | Average, Harmonic U L3 | [14] | 0.1
4061 | SHORT | RD | V | Average, Harmonic U L3 | [15] | 0.1
4062 | SHORT | RD | V | Average, Harmonic U L3 | [16] | 0.1
4063 | SHORT | RD | V | Average, Harmonic U L3 | [17] | 0.1
4064 | SHORT | RD | V | Average, Harmonic U L3 | [18] | 0.1
4065 | SHORT | RD | V | Average, Harmonic U L3 | [19] | 0.1
4066 | SHORT | RD | V | Average, Harmonic U L3 | [20] | 0.1
4067 | SHORT | RD | V | Average, Harmonic U L3 | [21] | 0.1
4068 | SHORT | RD | V | Average, Harmonic U L3 | [22] | 0.1
4069 | SHORT | RD | V | Average, Harmonic U L3 | [23] | 0.1
4070 | SHORT | RD | V | Average, Harmonic U L3 | [24] | 0.1
4071 | SHORT | RD | V | Average, Harmonic U L3 | [25] | 0.1
4072 | SHORT | RD | V | Average, Harmonic U L3 | [26] | 0.1
4073 | SHORT | RD | V | Average, Harmonic U L3 | [27] | 0.1
4074 | SHORT | RD | V | Average, Harmonic U L3 | [28] | 0.1
4075 | SHORT | RD | V | Average, Harmonic U L3 | [29] | 0.1
4076 | SHORT | RD | V | Average, Harmonic U L3 | [30] | 0.1
4077 | SHORT | RD | V | Average, Harmonic U L3 | [31] | 0.1
4078 | SHORT | RD | V | Average, Harmonic U L3 | [32] | 0.1
4079 | SHORT | RD | V | Average, Harmonic U L3 | [33] | 0.1
4080 | SHORT | RD | V | Average, Harmonic U L3 | [34] | 0.1
4081 | SHORT | RD | V | Average, Harmonic U L3 | [35] | 0.1
4082 | SHORT | RD | V | Average, Harmonic U L3 | [36] | 0.1
4083 | SHORT | RD | V | Average, Harmonic U L3 | [37] | 0.1
4084 | SHORT | RD | V | Average, Harmonic U L3 | [38] | 0.1
4085 | SHORT | RD | V | Average, Harmonic U L3 | [39] | 0.1
4086 | SHORT | RD | V | Average, Harmonic U L1-L2 | [0] | 0.1
4087 | SHORT | RD | V | Average, Harmonic U L1-L2 | [1] | 0.1
4088 | SHORT | RD | V | Average, Harmonic U L1-L2 | [2] | 0.1
4089 | SHORT | RD | V | Average, Harmonic U L1-L2 | [3] | 0.1
4090 | SHORT | RD | V | Average, Harmonic U L1-L2 | [4] | 0.1
4091 | SHORT | RD | V | Average, Harmonic U L1-L2 | [5] | 0.1
4092 | SHORT | RD | V | Average, Harmonic U L1-L2 | [6] | 0.1
4093 | SHORT | RD | V | Average, Harmonic U L1-L2 | [7] | 0.1
4094 | SHORT | RD | V | Average, Harmonic U L1-L2 | [8] | 0.1
4095 | SHORT | RD | V | Average, Harmonic U L1-L2 | [9] | 0.1
4096 | SHORT | RD | V | Average, Harmonic U L1-L2 | [10] | 0.1
4097 | SHORT | RD | V | Average, Harmonic U L1-L2 | [11] | 0.1
4098 | SHORT | RD | V | Average, Harmonic U L1-L2 | [12] | 0.1
4099 | SHORT | RD | V | Average, Harmonic U L1-L2 | [13] | 0.1
4100 | SHORT | RD | V | Average, Harmonic U L1-L2 | [14] | 0.1
4101 | SHORT | RD | V | Average, Harmonic U L1-L2 | [15] | 0.1
4102 | SHORT | RD | V | Average, Harmonic U L1-L2 | [16] | 0.1
4103 | SHORT | RD | V | Average, Harmonic U L1-L2 | [17] | 0.1
4104 | SHORT | RD | V | Average, Harmonic U L1-L2 | [18] | 0.1
4105 | SHORT | RD | V | Average, Harmonic U L1-L2 | [19] | 0.1
4106 | SHORT | RD | V | Average, Harmonic U L1-L2 | [20] | 0.1
4107 | SHORT | RD | V | Average, Harmonic U L1-L2 | [21] | 0.1
4108 | SHORT | RD | V | Average, Harmonic U L1-L2 | [22] | 0.1
4109 | SHORT | RD | V | Average, Harmonic U L1-L2 | [23] | 0.1
4110 | SHORT | RD | V | Average, Harmonic U L1-L2 | [24] | 0.1
4111 | SHORT | RD | V | Average, Harmonic U L1-L2 | [25] | 0.1
4112 | SHORT | RD | V | Average, Harmonic U L1-L2 | [26] | 0.1
4113 | SHORT | RD | V | Average, Harmonic U L1-L2 | [27] | 0.1
4114 | SHORT | RD | V | Average, Harmonic U L1-L2 | [28] | 0.1
4115 | SHORT | RD | V | Average, Harmonic U L1-L2 | [29] | 0.1
4116 | SHORT | RD | V | Average, Harmonic U L1-L2 | [30] | 0.1
4117 | SHORT | RD | V | Average, Harmonic U L1-L2 | [31] | 0.1
4118 | SHORT | RD | V | Average, Harmonic U L1-L2 | [32] | 0.1
4119 | SHORT | RD | V | Average, Harmonic U L1-L2 | [33] | 0.1
4120 | SHORT | RD | V | Average, Harmonic U L1-L2 | [34] | 0.1
4121 | SHORT | RD | V | Average, Harmonic U L1-L2 | [35] | 0.1
4122 | SHORT | RD | V | Average, Harmonic U L1-L2 | [36] | 0.1
4123 | SHORT | RD | V | Average, Harmonic U L1-L2 | [37] | 0.1
4124 | SHORT | RD | V | Average, Harmonic U L1-L2 | [38] | 0.1
4125 | SHORT | RD | V | Average, Harmonic U L1-L2 | [39] | 0.1
4126 | SHORT | RD | V | Average, Harmonic U L2-L3 | [0] | 0.1
4127 | SHORT | RD | V | Average, Harmonic U L2-L3 | [1] | 0.1
4128 | SHORT | RD | V | Average, Harmonic U L2-L3 | [2] | 0.1
4129 | SHORT | RD | V | Average, Harmonic U L2-L3 | [3] | 0.1
4130 | SHORT | RD | V | Average, Harmonic U L2-L3 | [4] | 0.1
4131 | SHORT | RD | V | Average, Harmonic U L2-L3 | [5] | 0.1
4132 | SHORT | RD | V | Average, Harmonic U L2-L3 | [6] | 0.1
4133 | SHORT | RD | V | Average, Harmonic U L2-L3 | [7] | 0.1
4134 | SHORT | RD | V | Average, Harmonic U L2-L3 | [8] | 0.1
4135 | SHORT | RD | V | Average, Harmonic U L2-L3 | [9] | 0.1
4136 | SHORT | RD | V | Average, Harmonic U L2-L3 | [10] | 0.1
4137 | SHORT | RD | V | Average, Harmonic U L2-L3 | [11] | 0.1
4138 | SHORT | RD | V | Average, Harmonic U L2-L3 | [12] | 0.1
4139 | SHORT | RD | V | Average, Harmonic U L2-L3 | [13] | 0.1
4140 | SHORT | RD | V | Average, Harmonic U L2-L3 | [14] | 0.1
4141 | SHORT | RD | V | Average, Harmonic U L2-L3 | [15] | 0.1
4142 | SHORT | RD | V | Average, Harmonic U L2-L3 | [16] | 0.1
4143 | SHORT | RD | V | Average, Harmonic U L2-L3 | [17] | 0.1
4144 | SHORT | RD | V | Average, Harmonic U L2-L3 | [18] | 0.1
4145 | SHORT | RD | V | Average, Harmonic U L2-L3 | [19] | 0.1
4146 | SHORT | RD | V | Average, Harmonic U L2-L3 | [20] | 0.1
4147 | SHORT | RD | V | Average, Harmonic U L2-L3 | [21] | 0.1
4148 | SHORT | RD | V | Average, Harmonic U L2-L3 | [22] | 0.1
4149 | SHORT | RD | V | Average, Harmonic U L2-L3 | [23] | 0.1
4150 | SHORT | RD | V | Average, Harmonic U L2-L3 | [24] | 0.1
4151 | SHORT | RD | V | Average, Harmonic U L2-L3 | [25] | 0.1
4152 | SHORT | RD | V | Average, Harmonic U L2-L3 | [26] | 0.1
4153 | SHORT | RD | V | Average, Harmonic U L2-L3 | [27] | 0.1
4154 | SHORT | RD | V | Average, Harmonic U L2-L3 | [28] | 0.1
4155 | SHORT | RD | V | Average, Harmonic U L2-L3 | [29] | 0.1
4156 | SHORT | RD | V | Average, Harmonic U L2-L3 | [30] | 0.1
4157 | SHORT | RD | V | Average, Harmonic U L2-L3 | [31] | 0.1
4158 | SHORT | RD | V | Average, Harmonic U L2-L3 | [32] | 0.1
4159 | SHORT | RD | V | Average, Harmonic U L2-L3 | [33] | 0.1
4160 | SHORT | RD | V | Average, Harmonic U L2-L3 | [34] | 0.1
4161 | SHORT | RD | V | Average, Harmonic U L2-L3 | [35] | 0.1
4162 | SHORT | RD | V | Average, Harmonic U L2-L3 | [36] | 0.1
4163 | SHORT | RD | V | Average, Harmonic U L2-L3 | [37] | 0.1
4164 | SHORT | RD | V | Average, Harmonic U L2-L3 | [38] | 0.1
4165 | SHORT | RD | V | Average, Harmonic U L2-L3 | [39] | 0.1
4166 | SHORT | RD | V | Average, Harmonic U L3-L1 | [0] | 0.1
4167 | SHORT | RD | V | Average, Harmonic U L3-L1 | [1] | 0.1
4168 | SHORT | RD | V | Average, Harmonic U L3-L1 | [2] | 0.1
4169 | SHORT | RD | V | Average, Harmonic U L3-L1 | [3] | 0.1
4170 | SHORT | RD | V | Average, Harmonic U L3-L1 | [4] | 0.1
4171 | SHORT | RD | V | Average, Harmonic U L3-L1 | [5] | 0.1
4172 | SHORT | RD | V | Average, Harmonic U L3-L1 | [6] | 0.1
4173 | SHORT | RD | V | Average, Harmonic U L3-L1 | [7] | 0.1
4174 | SHORT | RD | V | Average, Harmonic U L3-L1 | [8] | 0.1
4175 | SHORT | RD | V | Average, Harmonic U L3-L1 | [9] | 0.1
4176 | SHORT | RD | V | Average, Harmonic U L3-L1 | [10] | 0.1
4177 | SHORT | RD | V | Average, Harmonic U L3-L1 | [11] | 0.1
4178 | SHORT | RD | V | Average, Harmonic U L3-L1 | [12] | 0.1
4179 | SHORT | RD | V | Average, Harmonic U L3-L1 | [13] | 0.1
4180 | SHORT | RD | V | Average, Harmonic U L3-L1 | [14] | 0.1
4181 | SHORT | RD | V | Average, Harmonic U L3-L1 | [15] | 0.1
4182 | SHORT | RD | V | Average, Harmonic U L3-L1 | [16] | 0.1
4183 | SHORT | RD | V | Average, Harmonic U L3-L1 | [17] | 0.1
4184 | SHORT | RD | V | Average, Harmonic U L3-L1 | [18] | 0.1
4185 | SHORT | RD | V | Average, Harmonic U L3-L1 | [19] | 0.1
4186 | SHORT | RD | V | Average, Harmonic U L3-L1 | [20] | 0.1
4187 | SHORT | RD | V | Average, Harmonic U L3-L1 | [21] | 0.1
4188 | SHORT | RD | V | Average, Harmonic U L3-L1 | [22] | 0.1
4189 | SHORT | RD | V | Average, Harmonic U L3-L1 | [23] | 0.1
4190 | SHORT | RD | V | Average, Harmonic U L3-L1 | [24] | 0.1
4191 | SHORT | RD | V | Average, Harmonic U L3-L1 | [25] | 0.1
4192 | SHORT | RD | V | Average, Harmonic U L3-L1 | [26] | 0.1
4193 | SHORT | RD | V | Average, Harmonic U L3-L1 | [27] | 0.1
4194 | SHORT | RD | V | Average, Harmonic U L3-L1 | [28] | 0.1
4195 | SHORT | RD | V | Average, Harmonic U L3-L1 | [29] | 0.1
4196 | SHORT | RD | V | Average, Harmonic U L3-L1 | [30] | 0.1
4197 | SHORT | RD | V | Average, Harmonic U L3-L1 | [31] | 0.1
4198 | SHORT | RD | V | Average, Harmonic U L3-L1 | [32] | 0.1
4199 | SHORT | RD | V | Average, Harmonic U L3-L1 | [33] | 0.1
4200 | SHORT | RD | V | Average, Harmonic U L3-L1 | [34] | 0.1
4201 | SHORT | RD | V | Average, Harmonic U L3-L1 | [35] | 0.1
4202 | SHORT | RD | V | Average, Harmonic U L3-L1 | [36] | 0.1
4203 | SHORT | RD | V | Average, Harmonic U L3-L1 | [37] | 0.1
4204 | SHORT | RD | V | Average, Harmonic U L3-L1 | [38] | 0.1
4205 | SHORT | RD | V | Average, Harmonic U L3-L1 | [39] | 0.1
4226 | SHORT | RD | mA | Average, Harmonic I L1 | [0] | 1
4227 | SHORT | RD | mA | Average, Harmonic I L1 | [1] | 1
4228 | SHORT | RD | mA | Average, Harmonic I L1 | [2] | 1
4229 | SHORT | RD | mA | Average, Harmonic I L1 | [3] | 1
4230 | SHORT | RD | mA | Average, Harmonic I L1 | [4] | 1
4231 | SHORT | RD | mA | Average, Harmonic I L1 | [5] | 1
4232 | SHORT | RD | mA | Average, Harmonic I L1 | [6] | 1
4233 | SHORT | RD | mA | Average, Harmonic I L1 | [7] | 1
4234 | SHORT | RD | mA | Average, Harmonic I L1 | [8] | 1
4235 | SHORT | RD | mA | Average, Harmonic I L1 | [9] | 1
4236 | SHORT | RD | mA | Average, Harmonic I L1 | [10] | 1
4237 | SHORT | RD | mA | Average, Harmonic I L1 | [11] | 1
4238 | SHORT | RD | mA | Average, Harmonic I L1 | [12] | 1
4239 | SHORT | RD | mA | Average, Harmonic I L1 | [13] | 1
4240 | SHORT | RD | mA | Average, Harmonic I L1 | [14] | 1
4241 | SHORT | RD | mA | Average, Harmonic I L1 | [15] | 1
4242 | SHORT | RD | mA | Average, Harmonic I L1 | [16] | 1
4243 | SHORT | RD | mA | Average, Harmonic I L1 | [17] | 1
4244 | SHORT | RD | mA | Average, Harmonic I L1 | [18] | 1
4245 | SHORT | RD | mA | Average, Harmonic I L1 | [19] | 1
4246 | SHORT | RD | mA | Average, Harmonic I L1 | [20] | 1
4247 | SHORT | RD | mA | Average, Harmonic I L1 | [21] | 1
4248 | SHORT | RD | mA | Average, Harmonic I L1 | [22] | 1
4249 | SHORT | RD | mA | Average, Harmonic I L1 | [23] | 1
4250 | SHORT | RD | mA | Average, Harmonic I L1 | [24] | 1
4251 | SHORT | RD | mA | Average, Harmonic I L1 | [25] | 1
4252 | SHORT | RD | mA | Average, Harmonic I L1 | [26] | 1
4253 | SHORT | RD | mA | Average, Harmonic I L1 | [27] | 1
4254 | SHORT | RD | mA | Average, Harmonic I L1 | [28] | 1
4255 | SHORT | RD | mA | Average, Harmonic I L1 | [29] | 1
4256 | SHORT | RD | mA | Average, Harmonic I L1 | [30] | 1
4257 | SHORT | RD | mA | Average, Harmonic I L1 | [31] | 1
4258 | SHORT | RD | mA | Average, Harmonic I L1 | [32] | 1
4259 | SHORT | RD | mA | Average, Harmonic I L1 | [33] | 1
4260 | SHORT | RD | mA | Average, Harmonic I L1 | [34] | 1
4261 | SHORT | RD | mA | Average, Harmonic I L1 | [35] | 1
4262 | SHORT | RD | mA | Average, Harmonic I L1 | [36] | 1
4263 | SHORT | RD | mA | Average, Harmonic I L1 | [37] | 1
4264 | SHORT | RD | mA | Average, Harmonic I L1 | [38] | 1
4265 | SHORT | RD | mA | Average, Harmonic I L1 | [39] | 1
4266 | SHORT | RD | mA | Average, Harmonic I L2 | [0] | 1
4267 | SHORT | RD | mA | Average, Harmonic I L2 | [1] | 1
4268 | SHORT | RD | mA | Average, Harmonic I L2 | [2] | 1
4269 | SHORT | RD | mA | Average, Harmonic I L2 | [3] | 1
4270 | SHORT | RD | mA | Average, Harmonic I L2 | [4] | 1
4271 | SHORT | RD | mA | Average, Harmonic I L2 | [5] | 1
4272 | SHORT | RD | mA | Average, Harmonic I L2 | [6] | 1
4273 | SHORT | RD | mA | Average, Harmonic I L2 | [7] | 1
4274 | SHORT | RD | mA | Average, Harmonic I L2 | [8] | 1
4275 | SHORT | RD | mA | Average, Harmonic I L2 | [9] | 1
4276 | SHORT | RD | mA | Average, Harmonic I L2 | [10] | 1
4277 | SHORT | RD | mA | Average, Harmonic I L2 | [11] | 1
4278 | SHORT | RD | mA | Average, Harmonic I L2 | [12] | 1
4279 | SHORT | RD | mA | Average, Harmonic I L2 | [13] | 1
4280 | SHORT | RD | mA | Average, Harmonic I L2 | [14] | 1
4281 | SHORT | RD | mA | Average, Harmonic I L2 | [15] | 1
4282 | SHORT | RD | mA | Average, Harmonic I L2 | [16] | 1
4283 | SHORT | RD | mA | Average, Harmonic I L2 | [17] | 1
4284 | SHORT | RD | mA | Average, Harmonic I L2 | [18] | 1
4285 | SHORT | RD | mA | Average, Harmonic I L2 | [19] | 1
4286 | SHORT | RD | mA | Average, Harmonic I L2 | [20] | 1
4287 | SHORT | RD | mA | Average, Harmonic I L2 | [21] | 1
4288 | SHORT | RD | mA | Average, Harmonic I L2 | [22] | 1
4289 | SHORT | RD | mA | Average, Harmonic I L2 | [23] | 1
4290 | SHORT | RD | mA | Average, Harmonic I L2 | [24] | 1
4291 | SHORT | RD | mA | Average, Harmonic I L2 | [25] | 1
4292 | SHORT | RD | mA | Average, Harmonic I L2 | [26] | 1
4293 | SHORT | RD | mA | Average, Harmonic I L2 | [27] | 1
4294 | SHORT | RD | mA | Average, Harmonic I L2 | [28] | 1
4295 | SHORT | RD | mA | Average, Harmonic I L2 | [29] | 1
4296 | SHORT | RD | mA | Average, Harmonic I L2 | [30] | 1
4297 | SHORT | RD | mA | Average, Harmonic I L2 | [31] | 1
4298 | SHORT | RD | mA | Average, Harmonic I L2 | [32] | 1
4299 | SHORT | RD | mA | Average, Harmonic I L2 | [33] | 1
4300 | SHORT | RD | mA | Average, Harmonic I L2 | [34] | 1
4301 | SHORT | RD | mA | Average, Harmonic I L2 | [35] | 1
4302 | SHORT | RD | mA | Average, Harmonic I L2 | [36] | 1
4303 | SHORT | RD | mA | Average, Harmonic I L2 | [37] | 1
4304 | SHORT | RD | mA | Average, Harmonic I L2 | [38] | 1
4305 | SHORT | RD | mA | Average, Harmonic I L2 | [39] | 1
4306 | SHORT | RD | mA | Average, Harmonic I L3 | [0] | 1
4307 | SHORT | RD | mA | Average, Harmonic I L3 | [1] | 1
4308 | SHORT | RD | mA | Average, Harmonic I L3 | [2] | 1
4309 | SHORT | RD | mA | Average, Harmonic I L3 | [3] | 1
4310 | SHORT | RD | mA | Average, Harmonic I L3 | [4] | 1
4311 | SHORT | RD | mA | Average, Harmonic I L3 | [5] | 1
4312 | SHORT | RD | mA | Average, Harmonic I L3 | [6] | 1
4313 | SHORT | RD | mA | Average, Harmonic I L3 | [7] | 1
4314 | SHORT | RD | mA | Average, Harmonic I L3 | [8] | 1
4315 | SHORT | RD | mA | Average, Harmonic I L3 | [9] | 1
4316 | SHORT | RD | mA | Average, Harmonic I L3 | [10] | 1
4317 | SHORT | RD | mA | Average, Harmonic I L3 | [11] | 1
4318 | SHORT | RD | mA | Average, Harmonic I L3 | [12] | 1
4319 | SHORT | RD | mA | Average, Harmonic I L3 | [13] | 1
4320 | SHORT | RD | mA | Average, Harmonic I L3 | [14] | 1
4321 | SHORT | RD | mA | Average, Harmonic I L3 | [15] | 1
4322 | SHORT | RD | mA | Average, Harmonic I L3 | [16] | 1
4323 | SHORT | RD | mA | Average, Harmonic I L3 | [17] | 1
4324 | SHORT | RD | mA | Average, Harmonic I L3 | [18] | 1
4325 | SHORT | RD | mA | Average, Harmonic I L3 | [19] | 1
4326 | SHORT | RD | mA | Average, Harmonic I L3 | [20] | 1
4327 | SHORT | RD | mA | Average, Harmonic I L3 | [21] | 1
4328 | SHORT | RD | mA | Average, Harmonic I L3 | [22] | 1
4329 | SHORT | RD | mA | Average, Harmonic I L3 | [23] | 1
4330 | SHORT | RD | mA | Average, Harmonic I L3 | [24] | 1
4331 | SHORT | RD | mA | Average, Harmonic I L3 | [25] | 1
4332 | SHORT | RD | mA | Average, Harmonic I L3 | [26] | 1
4333 | SHORT | RD | mA | Average, Harmonic I L3 | [27] | 1
4334 | SHORT | RD | mA | Average, Harmonic I L3 | [28] | 1
4335 | SHORT | RD | mA | Average, Harmonic I L3 | [29] | 1
4336 | SHORT | RD | mA | Average, Harmonic I L3 | [30] | 1
4337 | SHORT | RD | mA | Average, Harmonic I L3 | [31] | 1
4338 | SHORT | RD | mA | Average, Harmonic I L3 | [32] | 1
4339 | SHORT | RD | mA | Average, Harmonic I L3 | [33] | 1
4340 | SHORT | RD | mA | Average, Harmonic I L3 | [34] | 1
4341 | SHORT | RD | mA | Average, Harmonic I L3 | [35] | 1
4342 | SHORT | RD | mA | Average, Harmonic I L3 | [36] | 1
4343 | SHORT | RD | mA | Average, Harmonic I L3 | [37] | 1
4344 | SHORT | RD | mA | Average, Harmonic I L3 | [38] | 1
4345 | SHORT | RD | mA | Average, Harmonic I L3 | [39] | 1
Maximum values, type float, fourier analysis
Address | Format | RD/WR | Unit | Note | Index
2598 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [0]
2600 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [1]
2602 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [2]
2604 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [3]
2606 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [4]
2608 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [5]
2610 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [6]
2612 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [7]
2614 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [8]
2616 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [9]
2618 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [10]
2620 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [11]
2622 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [12]
2624 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [13]
2626 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [14]
2628 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [15]
2630 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [16]
2632 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [17]
2634 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [18]
2636 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [19]
2638 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [20]
2640 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [21]
2642 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [22]
2644 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [23]
2646 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [24]
2648 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [25]
2650 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [26]
2652 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [27]
2654 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [28]
2656 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [29]
2658 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [30]
2660 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [31]
2662 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [32]
2664 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [33]
2666 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [34]
2668 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [35]
2670 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [36]
2672 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [37]
2674 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [38]
2676 | FLOAT | RD/WR | V | Maximum, Harmonic U L1 | [39]
2678 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [0]
2680 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [1]
2682 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [2]
2684 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [3]
2686 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [4]
2688 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [5]
2690 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [6]
2692 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [7]
2694 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [8]
2696 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [9]
2698 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [10]
2700 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [11]
2702 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [12]
2704 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [13]
2706 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [14]
2708 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [15]
2710 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [16]
2712 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [17]
2714 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [18]
2716 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [19]
2718 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [20]
2720 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [21]
2722 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [22]
2724 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [23]
2726 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [24]
2728 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [25]
2730 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [26]
2732 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [27]
2734 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [28]
2736 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [29]
2738 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [30]
2740 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [31]
2742 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [32]
2744 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [33]
2746 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [34]
2748 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [35]
2750 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [36]
2752 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [37]
2754 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [38]
2756 | FLOAT | RD/WR | V | Maximum, Harmonic U L2 | [39]
2758 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [0]
2760 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [1]
2762 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [2]
2764 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [3]
2766 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [4]
2768 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [5]
2770 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [6]
2772 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [7]
2774 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [8]
2776 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [9]
2778 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [10]
2780 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [11]
2782 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [12]
2784 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [13]
2786 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [14]
2788 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [15]
2790 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [16]
2792 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [17]
2794 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [18]
2796 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [19]
2798 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [20]
2800 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [21]
2802 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [22]
2804 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [23]
2806 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [24]
2808 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [25]
2810 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [26]
2812 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [27]
2814 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [28]
2816 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [29]
2818 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [30]
2820 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [31]
2822 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [32]
2824 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [33]
2826 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [34]
2828 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [35]
2830 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [36]
2832 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [37]
2834 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [38]
2836 | FLOAT | RD/WR | V | Maximum, Harmonic U L3 | [39]
2838 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [0]
2840 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [1]
2842 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [2]
2844 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [3]
2846 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [4]
2848 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [5]
2850 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [6]
2852 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [7]
2854 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [8]
2856 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [9]
2858 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [10]
2860 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [11]
2862 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [12]
2864 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [13]
2866 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [14]
2868 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [15]
2870 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [16]
2872 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [17]
2874 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [18]
2876 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [19]
2878 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [20]
2880 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [21]
2882 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [22]
2884 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [23]
2886 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [24]
2888 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [25]
2890 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [26]
2892 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [27]
2894 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [28]
2896 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [29]
2898 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [30]
2900 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [31]
2902 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [32]
2904 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [33]
2906 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [34]
2908 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [35]
2910 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [36]
2912 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [37]
2914 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [38]
2916 | FLOAT | RD/WR | V | Maximum, Harmonic U L1-L2 | [39]
2918 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [0]
2920 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [1]
2922 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [2]
2924 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [3]
2926 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [4]
2928 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [5]
2930 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [6]
2932 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [7]
2934 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [8]
2936 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [9]
2938 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [10]
2940 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [11]
2942 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [12]
2944 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [13]
2946 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [14]
2948 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [15]
2950 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [16]
2952 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [17]
2954 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [18]
2956 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [19]
2958 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [20]
2960 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [21]
2962 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [22]
2964 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [23]
2966 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [24]
2968 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [25]
2970 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [26]
2972 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [27]
2974 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [28]
2976 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [29]
2978 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [30]
2980 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [31]
2982 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [32]
2984 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [33]
2986 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [34]
2988 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [35]
2990 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [36]
2992 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [37]
2994 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [38]
2996 | FLOAT | RD/WR | V | Maximum, Harmonic U L2-L3 | [39]
2998 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [0]
3000 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [1]
3002 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [2]
3004 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [3]
3006 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [4]
3008 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [5]
3010 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [6]
3012 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [7]
3014 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [8]
3016 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [9]
3018 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [10]
3020 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [11]
3022 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [12]
3024 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [13]
3026 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [14]
3028 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [15]
3030 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [16]
3032 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [17]
3034 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [18]
3036 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [19]
3038 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [20]
3040 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [21]
3042 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [22]
3044 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [23]
3046 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [24]
3048 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [25]
3050 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [26]
3052 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [27]
3054 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [28]
3056 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [29]
3058 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [30]
3060 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [31]
3062 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [32]
3064 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [33]
3066 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [34]
3068 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [35]
3070 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [36]
3072 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [37]
3074 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [38]
3076 | FLOAT | RD/WR | V | Maximum, Harmonic U L3-L1 | [39]
3118 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [0]
3120 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [1]
3122 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [2]
3124 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [3]
3126 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [4]
3128 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [5]
3130 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [6]
3132 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [7]
3134 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [8]
3136 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [9]
3138 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [10]
3140 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [11]
3142 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [12]
3144 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [13]
3146 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [14]
3148 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [15]
3150 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [16]
3152 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [17]
3154 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [18]
3156 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [19]
3158 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [20]
3160 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [21]
3162 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [22]
3164 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [23]
3166 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [24]
3168 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [25]
3170 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [26]
3172 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [27]
3174 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [28]
3176 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [29]
3178 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [30]
3180 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [31]
3182 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [32]
3184 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [33]
3186 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [34]
3188 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [35]
3190 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [36]
3192 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [37]
3194 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [38]
3196 | FLOAT | RD/WR | A | Maximum, Harmonic I L1 | [39]
3198 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [0]
3200 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [1]
3202 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [2]
3204 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [3]
3206 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [4]
3208 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [5]
3210 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [6]
3212 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [7]
3214 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [8]
3216 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [9]
3218 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [10]
3220 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [11]
3222 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [12]
3224 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [13]
3226 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [14]
3228 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [15]
3230 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [16]
3232 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [17]
3234 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [18]
3236 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [19]
3238 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [20]
3240 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [21]
3242 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [22]
3244 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [23]
3246 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [24]
3248 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [25]
3250 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [26]
3252 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [27]
3254 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [28]
3256 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [29]
3258 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [30]
3260 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [31]
3262 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [32]
3264 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [33]
3266 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [34]
3268 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [35]
3270 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [36]
3272 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [37]
3274 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [38]
3276 | FLOAT | RD/WR | A | Maximum, Harmonic I L2 | [39]
3278 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [0]
3280 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [1]
3282 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [2]
3284 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [3]
3286 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [4]
3288 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [5]
3290 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [6]
3292 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [7]
3294 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [8]
3296 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [9]
3298 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [10]
3300 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [11]
3302 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [12]
3304 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [13]
3306 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [14]
3308 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [15]
3310 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [16]
3312 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [17]
3314 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [18]
3316 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [19]
3318 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [20]
3320 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [21]
3322 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [22]
3324 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [23]
3326 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [24]
3328 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [25]
3330 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [26]
3332 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [27]
3334 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [28]
3336 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [29]
3338 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [30]
3340 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [31]
3342 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [32]
3344 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [33]
3346 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [34]
3348 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [35]
3350 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [36]
3352 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [37]
3354 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [38]
3356 | FLOAT | RD/WR | A | Maximum, Harmonic I L3 | [39]
Maximum values, type short, fourier analysis
Address | Format | RD/WR | Unit | Note | Index | Resolution
4395 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [0] | 0.1
4396 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [1] | 0.1
4397 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [2] | 0.1
4398 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [3] | 0.1
4399 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [4] | 0.1
4400 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [5] | 0.1
4401 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [6] | 0.1
4402 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [7] | 0.1
4403 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [8] | 0.1
4404 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [9] | 0.1
4405 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [10] | 0.1
4406 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [11] | 0.1
4407 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [12] | 0.1
4408 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [13] | 0.1
4409 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [14] | 0.1
4410 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [15] | 0.1
4411 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [16] | 0.1
4412 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [17] | 0.1
4413 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [18] | 0.1
4414 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [19] | 0.1
4415 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [20] | 0.1
4416 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [21] | 0.1
4417 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [22] | 0.1
4418 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [23] | 0.1
4419 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [24] | 0.1
4420 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [25] | 0.1
4421 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [26] | 0.1
4422 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [27] | 0.1
4423 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [28] | 0.1
4424 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [29] | 0.1
4425 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [30] | 0.1
4426 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [31] | 0.1
4427 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [32] | 0.1
4428 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [33] | 0.1
4429 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [34] | 0.1
4430 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [35] | 0.1
4431 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [36] | 0.1
4432 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [37] | 0.1
4433 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [38] | 0.1
4434 | SHORT | RD/WR | V | Maximum, Harmonic U L1 | [39] | 0.1
4435 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [0] | 0.1
4436 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [1] | 0.1
4437 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [2] | 0.1
4438 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [3] | 0.1
4439 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [4] | 0.1
4440 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [5] | 0.1
4441 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [6] | 0.1
4442 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [7] | 0.1
4443 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [8] | 0.1
4444 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [9] | 0.1
4445 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [10] | 0.1
4446 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [11] | 0.1
4447 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [12] | 0.1
4448 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [13] | 0.1
4449 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [14] | 0.1
4450 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [15] | 0.1
4451 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [16] | 0.1
4452 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [17] | 0.1
4453 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [18] | 0.1
4454 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [19] | 0.1
4455 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [20] | 0.1
4456 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [21] | 0.1
4457 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [22] | 0.1
4458 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [23] | 0.1
4459 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [24] | 0.1
4460 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [25] | 0.1
4461 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [26] | 0.1
4462 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [27] | 0.1
4463 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [28] | 0.1
4464 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [29] | 0.1
4465 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [30] | 0.1
4466 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [31] | 0.1
4467 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [32] | 0.1
4468 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [33] | 0.1
4469 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [34] | 0.1
4470 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [35] | 0.1
4471 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [36] | 0.1
4472 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [37] | 0.1
4473 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [38] | 0.1
4474 | SHORT | RD/WR | V | Maximum, Harmonic U L2 | [39] | 0.1
4475 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [0] | 0.1
4476 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [1] | 0.1
4477 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [2] | 0.1
4478 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [3] | 0.1
4479 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [4] | 0.1
4480 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [5] | 0.1
4481 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [6] | 0.1
4482 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [7] | 0.1
4483 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [8] | 0.1
4484 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [9] | 0.1
4485 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [10] | 0.1
4486 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [11] | 0.1
4487 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [12] | 0.1
4488 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [13] | 0.1
4489 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [14] | 0.1
4490 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [15] | 0.1
4491 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [16] | 0.1
4492 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [17] | 0.1
4493 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [18] | 0.1
4494 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [19] | 0.1
4495 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [20] | 0.1
4496 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [21] | 0.1
4497 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [22] | 0.1
4498 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [23] | 0.1
4499 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [24] | 0.1
4500 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [25] | 0.1
4501 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [26] | 0.1
4502 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [27] | 0.1
4503 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [28] | 0.1
4504 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [29] | 0.1
4505 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [30] | 0.1
4506 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [31] | 0.1
4507 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [32] | 0.1
4508 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [33] | 0.1
4509 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [34] | 0.1
4510 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [35] | 0.1
4511 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [36] | 0.1
4512 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [37] | 0.1
4513 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [38] | 0.1
4514 | SHORT | RD/WR | V | Maximum, Harmonic U L3 | [39] | 0.1
4515 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [0] | 0.1
4516 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [1] | 0.1
4517 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [2] | 0.1
4518 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [3] | 0.1
4519 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [4] | 0.1
4520 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [5] | 0.1
4521 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [6] | 0.1
4522 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [7] | 0.1
4523 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [8] | 0.1
4524 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [9] | 0.1
4525 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [10] | 0.1
4526 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [11] | 0.1
4527 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [12] | 0.1
4528 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [13] | 0.1
4529 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [14] | 0.1
4530 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [15] | 0.1
4531 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [16] | 0.1
4532 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [17] | 0.1
4533 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [18] | 0.1
4534 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [19] | 0.1
4535 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [20] | 0.1
4536 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [21] | 0.1
4537 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [22] | 0.1
4538 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [23] | 0.1
4539 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [24] | 0.1
4540 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [25] | 0.1
4541 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [26] | 0.1
4542 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [27] | 0.1
4543 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [28] | 0.1
4544 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [29] | 0.1
4545 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [30] | 0.1
4546 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [31] | 0.1
4547 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [32] | 0.1
4548 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [33] | 0.1
4549 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [34] | 0.1
4550 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [35] | 0.1
4551 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [36] | 0.1
4552 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [37] | 0.1
4553 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [38] | 0.1
4554 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L2 | [39] | 0.1
4555 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [0] | 0.1
4556 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [1] | 0.1
4557 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [2] | 0.1
4558 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [3] | 0.1
4559 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [4] | 0.1
4560 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [5] | 0.1
4561 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [6] | 0.1
4562 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [7] | 0.1
4563 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [8] | 0.1
4564 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [9] | 0.1
4565 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [10] | 0.1
4566 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [11] | 0.1
4567 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [12] | 0.1
4568 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [13] | 0.1
4569 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [14] | 0.1
4570 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [15] | 0.1
4571 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [16] | 0.1
4572 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [17] | 0.1
4573 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [18] | 0.1
4574 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [19] | 0.1
4575 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [20] | 0.1
4576 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [21] | 0.1
4577 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [22] | 0.1
4578 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [23] | 0.1
4579 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [24] | 0.1
4580 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [25] | 0.1
4581 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [26] | 0.1
4582 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [27] | 0.1
4583 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [28] | 0.1
4584 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [29] | 0.1
4585 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [30] | 0.1
4586 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [31] | 0.1
4587 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [32] | 0.1
4588 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [33] | 0.1
4589 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [34] | 0.1
4590 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [35] | 0.1
4591 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [36] | 0.1
4592 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [37] | 0.1
4593 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [38] | 0.1
4594 | SHORT | RD/WR | V | Maximum, Harmonic U L2-L3 | [39] | 0.1
4595 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [0] | 0.1
4596 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [1] | 0.1
4597 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [2] | 0.1
4598 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [3] | 0.1
4599 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [4] | 0.1
4600 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [5] | 0.1
4601 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [6] | 0.1
4602 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [7] | 0.1
4603 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [8] | 0.1
4604 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [9] | 0.1
4605 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [10] | 0.1
4606 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [11] | 0.1
4607 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [12] | 0.1
4608 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [13] | 0.1
4609 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [14] | 0.1
4610 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [15] | 0.1
4611 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [16] | 0.1
4612 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [17] | 0.1
4613 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [18] | 0.1
4614 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [19] | 0.1
4615 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [20] | 0.1
4616 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [21] | 0.1
4617 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [22] | 0.1
4618 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [23] | 0.1
4619 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [24] | 0.1
4620 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [25] | 0.1
4621 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [26] | 0.1
4622 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [27] | 0.1
4623 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [28] | 0.1
4624 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [29] | 0.1
4625 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [30] | 0.1
4626 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [31] | 0.1
4627 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [32] | 0.1
4628 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [33] | 0.1
4629 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [34] | 0.1
4630 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [35] | 0.1
4631 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [36] | 0.1
4632 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [37] | 0.1
4633 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [38] | 0.1
4634 | SHORT | RD/WR | V | Maximum, Harmonic U L1-L3 | [39] | 0.1
4655 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [0] | 1
4656 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [1] | 1
4657 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [2] | 1
4658 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [3] | 1
4659 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [4] | 1
4660 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [5] | 1
4661 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [6] | 1
4662 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [7] | 1
4663 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [8] | 1
4664 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [9] | 1
4665 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [10] | 1
4666 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [11] | 1
4667 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [12] | 1
4668 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [13] | 1
4669 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [14] | 1
4670 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [15] | 1
4671 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [16] | 1
4672 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [17] | 1
4673 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [18] | 1
4674 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [19] | 1
4675 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [20] | 1
4676 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [21] | 1
4677 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [22] | 1
4678 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [23] | 1
4679 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [24] | 1
4680 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [25] | 1
4681 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [26] | 1
4682 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [27] | 1
4683 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [28] | 1
4684 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [29] | 1
4685 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [30] | 1
4686 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [31] | 1
4687 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [32] | 1
4688 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [33] | 1
4689 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [34] | 1
4690 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [35] | 1
4691 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [36] | 1
4692 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [37] | 1
4693 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [38] | 1
4694 | SHORT | RD/WR | mA | Maximum, Harmonic I L1 | [39] | 1
4695 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [0] | 1
4696 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [1] | 1
4697 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [2] | 1
4698 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [3] | 1
4699 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [4] | 1
4700 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [5] | 1
4701 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [6] | 1
4702 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [7] | 1
4703 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [8] | 1
4704 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [9] | 1
4705 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [10] | 1
4706 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [11] | 1
4707 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [12] | 1
4708 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [13] | 1
4709 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [14] | 1
4710 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [15] | 1
4711 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [16] | 1
4712 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [17] | 1
4713 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [18] | 1
4714 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [19] | 1
4715 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [20] | 1
4716 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [21] | 1
4717 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [22] | 1
4718 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [23] | 1
4719 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [24] | 1
4720 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [25] | 1
4721 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [26] | 1
4722 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [27] | 1
4723 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [28] | 1
4724 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [29] | 1
4725 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [30] | 1
4726 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [31] | 1
4727 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [32] | 1
4728 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [33] | 1
4729 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [34] | 1
4730 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [35] | 1
4731 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [36] | 1
4732 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [37] | 1
4733 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [38] | 1
4734 | SHORT | RD/WR | mA | Maximum, Harmonic I L2 | [39] | 1
4735 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [0] | 1
4736 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [1] | 1
4737 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [2] | 1
4738 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [3] | 1
4739 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [4] | 1
4740 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [5] | 1
4741 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [6] | 1
4742 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [7] | 1
4743 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [8] | 1
4744 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [9] | 1
4745 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [10] | 1
4746 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [11] | 1
4747 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [12] | 1
4748 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [13] | 1
4749 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [14] | 1
4750 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [15] | 1
4751 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [16] | 1
4752 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [17] | 1
4753 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [18] | 1
4754 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [19] | 1
4755 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [20] | 1
4756 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [21] | 1
4757 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [22] | 1
4758 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [23] | 1
4759 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [24] | 1
4760 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [25] | 1
4761 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [26] | 1
4762 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [27] | 1
4763 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [28] | 1
4764 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [29] | 1
4765 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [30] | 1
4766 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [31] | 1
4767 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [32] | 1
4768 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [33] | 1
4769 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [34] | 1
4770 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [35] | 1
4771 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [36] | 1
4772 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [37] | 1
4773 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [38] | 1
4774 | SHORT | RD/WR | mA | Maximum, Harmonic I L3 | [39] | 1
Extension UMG96 RM-PN
Additional parameters and address list for the
extensions UMG96RM-PN
Parameter
Address | Format | RD/WR | Unit | Note | Adjustment Area | Default
520 | SHORT | RD/WR |  | Modbus Timeout: Time (in ms) after | 0-10000 | 200
a Modbus request over the module is
discarded to the base
521 | SHORT | RD/WR |  | Changeover of the digital IOs of the module | 0, 1 | 0
0=output, 1=input
524 | SHORT | RD/WR |  | Inverting digital output 3 | 0, 1 | 0
525 | SHORT | RD/WR |  | Inverting digital output 4 | 0, 1 | 0
526 | SHORT | RD/WR |  | Inverting digital output 5 | 0, 1 | 0
527 | SHORT | RD/WR |  | Digital out 1, source Profinet: Source for | 0, 1 | 0
base outputs (selection by Addr. 200 = 5)
528 | SHORT | RD/WR |  | Digital out 2, source Profinet: Source for | 0, 1 | 0
base outputs (selection by Addr. 202 = 5)
530 | FLOAT | RD/WR |  | I4, current transformer, primary | 0-1000000 | 5
532 | FLOAT | RD/WR |  | I4, current transformer, secondary | 1.0-5.0 | 5
534 | FLOAT | RD/WR |  | I5, current transformer, primary | 0.0-1000000.0 | 1
536 | FLOAT | RD/WR |  | I5, current transformer, secondary | 1.0-5.0 | 1
538 | FLOAT | RD/WR |  | I6, current transformer, primary | 0.0-1000000.0 | 1
540 | FLOAT | RD/WR |  | I6, current transformer, secondary | 1.0-5.0 | 1
542 | SHORT | RD/WR |  | Type I5: 0=residual current, 1=temperature | 0, 1 | 0
543 | SHORT | RD/WR |  | Type I6: 0=residual current, 1=temperature | 0, 1 | 0
544 | FLOAT | RD/WR |  | Temperature offset, Temp1 | -1000.0 - 1000.0 | 0
546 | FLOAT | RD/WR |  | Temperature offset, Temp2 | -1000.0 - 1000.0 | 0
548 | SHORT | RD/WR |  | Temperature sensor, Temp1 | 0-4 | 0
(0=PT100, 1=PT1000, 2=KTY83, 3=KTY84,
4=resistor in ohm)
549 | SHORT | RD/WR |  | Temperature sensor, Temp2 | 0-4 | 0
(0=PT100, 1=PT1000, 2=KTY83, 3=KTY84,
4=resistor in ohm)
550 | SHORT | RD/WR |  | Tariff configuration input 1; if Input 1 is set, | 0-127 | 0
configurable counters are set in tariff 1 *
551 | SHORT | RD/WR |  | Tariff configuration input 2; if Input 2 is set, | 0-127 | 0
configurable counters are set in tariff 2 *
552 | SHORT | RD/WR |  | Tariff configuration input 3; if Input 3 is set, | 0-127 | 0
configurable counters are set in tariff 3 *
553 | SHORT | RD/WR |  | Enable transformer connection ckeck channel I5 | 0.1 | 0
554 | SHORT | RD/WR |  | Enable transformer connection ckeck channel I6 | 0.1 | 0
20010 | UINT |  |  | Device IP address | 0, 0xFFFFFFFF | 0xA0A0AC8
(10.10.10.200)
20012 | UINT |  |  | Device netmask | 0, 0xFFFFFFFF | 0xFFFFFF00
(255.255.255.0)
20014 | UINT |  |  | Device gateway IP address | 0, 0xFFFFFFFF | 0xA0A0A01
(10.10.10.1)
25436 | STRING | RD/WR |  | Device name
UMG96RM-PN-2500-xxxx
26000 | UINT | RD |  | Serial number **
26002 | UINT | RD |  | Item number **
26004 | SHORT | RD |  | Release Base **
26005 | SHORT | RD |  | Modbus Adresse **
26006 | UINT | RD |  | Modbus RTU Baudrate **
26008 | SHORT | RD |  | Hardware Index **
Measured values
Address | Format | RD/WR | Unit | Note | Index | Resolution
20050 | SHORT |  |  | Digital-Out 3 | 0.1
20051 | SHORT |  |  | Digital-Out 4 | 0.1
20052 | SHORT |  |  | Digital-Out 5 | 0.1
10000 | FLOAT |  | A | I4 current |  | 1
10002 | FLOAT |  | A | I5 current |  | 1
10004 | FLOAT |  | A | I6 current |  | 1
10006 | FLOAT |  | °C | Temperature input 1
10008 | FLOAT |  | °C | Temperature input 2
10010 | SHORT |  |  | Digital-In 1 | 0.1
10011 | SHORT |  |  | Digital-In 2 | 0.1
10012 | SHORT |  |  | Digital-In 3 | 0.1
10013 | SHORT |  |  | Digital In Binary | 0-7
10014 | SHORT |  |  | Transformer I5 not connected | 0.1
0 = converter realised
1 = no converter realised
10015 | SHORT |  |  | Transformer I6 not connected | 0.1
0 = converter realised
1 = no converter realised
Extension UMG96 RM-P / -CBM
Additional parameters and address list for the
extensions UMG96RM-P and UMG 96RM-CBM
Parameter
Address | Format | RD/WR | Unit | Note | Adjustment Area | Default
10082 | SHORT | RD |  | Condition digital output 3
10083 | SHORT | RD |  | Condition digital output 4
10084 | SHORT | RD |  | Condition digital output 5
10085 | SHORT | RD |  | Condition digital output 6
10132 | SHORT | RD |  | Status, digital input 1
10133 | SHORT | RD |  | Status, digital input 2
10134 | SHORT | RD |  | Status, digital input 3
10135 | SHORT | RD |  | Status, digital input 4
10136 | SHORT | RD |  | Status, overrange, I4
10138 | SHORT | RD |  | Status digital inputs 3-6
(Bit1=input 1,....)
20001 | UINT | RD/WR |  | Address of reading, UTC system time
20003 | UINT | RD/WR |  | Address of writing, UTC system time | 0 .. 0xFFFFFFFF | 0
20020 | FLOAT | RD/WR |  | I4, nominal current | 1 .. 1000000 | 150
20022 | FLOAT | RD/WR |  | I4, current transformer, primary | 0 .. 1000000 | 5
20024 | FLOAT | RD/WR |  | I4, current transformer, secondary | 1 .. 5 | 5
21992 | FLOAT | RD/WR |  | S0 pulse valence, input 1 | 0 .. 1000000 | 0
21994 | FLOAT | RD/WR |  | S0 pulse valence, input 2 | 0 .. 1000000 | 0
21996 | FLOAT | RD/WR |  | S0 pulse valence, input 3 | 0 .. 1000000 | 0
21998 | FLOAT | RD/WR |  | S0 pulse valence, input 4 | 0 .. 1000000 | 0
22000 | SHORT | RD/WR |  | Measured value address output 3 | 0 .. 32000 | 0
22001 | SHORT | RD/WR |  | Measured value address output 4 | 0 .. 32000 | 0
22002 | SHORT | RD/WR |  | Measured value address output 5 | 0 .. 32000 | 0
22003 | SHORT | RD/WR |  | Measured value address output 6 | 0 .. 32000 | 0
22004 | FLOAT | RD/WR |  | Pulse valence, output 3 | -1000000 .. +1000000 | 0
22006 | FLOAT | RD/WR |  | Pulse valence, output 4 | -1000000 .. +1000000 | 0
22008 | FLOAT | RD/WR |  | Pulse valence, output 5 | -1000000 .. +1000000 | 0
22010 | FLOAT | RD/WR |  | Pulse valence, output 6 | -1000000 .. +1000000 | 0
22096 | SHORT | RD/WR |  | Output 3, Modbus remote, address | 0, 1 | 0
22097 | SHORT | RD/WR |  | Output 3, Profibus remote, address | 0, 1 | 0
22098 | SHORT | RD/WR |  | Output 4, Modbus remote, address | 0, 1 | 0
22099 | SHORT | RD/WR |  | Output 3, Profibus remote, address | 0, 1 | 0
22100 | SHORT | RD/WR |  | Output 5, Modbus remote, address | 0, 1 | 0
22101 | SHORT | RD/WR |  | Output 5, Profibus remote, address | 0, 1 | 0
22102 | SHORT | RD/WR |  | Output 6, Modbus remote, address | 0, 1 | 0
22103 | SHORT | RD/WR |  | Output 6, Profibus remote, address | 0, 1 | 0
22500 | CHAR | RD/WR |  | Rate 1, active energy, if input 1 is active | 0.1 | 0
22501 | CHAR | RD/WR |  | Rate 2, active energy, if input 2 is active | 0.1 | 0
22502 | CHAR | RD/WR |  | Rate 3, active energy, if input 3 is active | 0.1 | 0
22503 | CHAR | RD/WR |  | Rate 4, active energy, if input 4 is active | 0.1 | 0
22507 | CHAR | RD/WR |  | Rate 1, active energy, consumed, if input 1 is active | 0.1 | 0
22508 | CHAR | RD/WR |  | Rate 2, active energy, consumed, if input 2 is active | 0.1 | 0
22509 | CHAR | RD/WR |  | Rate 3, active energy, consumed, if input 3 is active | 0.1 | 0
22510 | CHAR | RD/WR |  | Rate 4, active energy, consumed, if input 4 is active | 0.1 | 0
22514 | CHAR | RD/WR |  | Rate 1, active energy, delivered, if input 1 is active | 0.1 | 0
22515 | CHAR | RD/WR |  | Rate 2, active energy, delivered, if input 2 is active | 0.1 | 0
22516 | CHAR | RD/WR |  | Rate 3, active energy, delivered, if input 3 is active | 0.1 | 0
22517 | CHAR | RD/WR |  | Rate 4, active energy, delivered, if input 4 is active | 0.1 | 0
22521 | CHAR | RD/WR |  | Rate 1, reactive energy, without reverse running stop, if input 1 is active | 0.1 | 0
22522 | CHAR | RD/WR |  | Rate 2, reactive energy, without reverse running stop, if input 2 is active | 0.1 | 0
22523 | CHAR | RD/WR |  | Rate 3, reactive energy, without reverse running stop, if input 3 is active | 0.1 | 0
22524 | CHAR | RD/WR |  | Rate 4, reactive energy, without reverse running stop, if input 4 is active | 0.1 | 0
22528 | CHAR | RD/WR |  | Rate 1, reactive energy induktiv, if input 1 is active | 0.1 | 0
22529 | CHAR | RD/WR |  | Rate 2, reactive energy induktiv, if input 2 is active | 0.1 | 0
22530 | CHAR | RD/WR |  | Rate 3, reactive energy induktiv, if input 3 is active | 0.1 | 0
22531 | CHAR | RD/WR |  | Rate 4, reactive energy induktiv, if input 4 is active | 0.1 | 0
22535 | CHAR | RD/WR |  | Rate 1, reactive energy kapazitiv, if input 1 is active | 0.1 | 0
22536 | CHAR | RD/WR |  | Rate 2, reactive energy kapazitiv, if input 2 is active | 0.1 | 0
22537 | CHAR | RD/WR |  | Rate 3, reactive energy kapazitiv, if input 3 is active | 0.1 | 0
22538 | CHAR | RD/WR |  | Rate 4, reactive energy kapazitiv, if input 4 is active | 0.1 | 0
22542 | CHAR | RD/WR |  | Rate 1, apparent energy, if input 1 is active | 0.1 | 0
22543 | CHAR | RD/WR |  | Rate 2, apparent energy, if input 2 is active | 0.1 | 0
22544 | CHAR | RD/WR |  | Rate 3, apparent energy, if input 3 is active | 0.1 | 0
22545 | CHAR | RD/WR |  | Rate 4, apparent energy, if input 4 is active | 0.1 | 0
25010 | SHORT | RD |  | Software release | - | -
25011 | USHORT | RD |  | Hardware release | - | -
25012 | SERNR | RD |  | Serial number | - | -
Limit value monitoring
Address | Format | RD/WR | Unit | Note | Adjustment Area | Default
10086 | SHORT | RD |  | Results of the comparator A, comparator group 3
10087 | SHORT | RD |  | Results of the comparator B, comparator group 3
10088 | SHORT | RD |  | Results of the comparator C, comparator group 3
10089 | SHORT | RD |  | Results of the comparator A, comparator group 4
10090 | SHORT | RD |  | Results of the comparator B, comparator group 4
10091 | SHORT | RD |  | Results of the comparator C, comparator group 4
10092 | SHORT | RD |  | Results of the comparator A, comparator group 5
10093 | SHORT | RD |  | Results of the comparator B, comparator group 5
10094 | SHORT | RD |  | Results of the comparator C, comparator group 5
10095 | SHORT | RD |  | Results of the comparator A, comparator group 6
10096 | SHORT | RD |  | Results of the comparator B, comparator group 6
10097 | SHORT | RD |  | Results of the comparator C, comparator group 6
10098 | SHORT | RD | - | Comparator group 3, Linkage result of comparator group
10099 | SHORT | RD | - | Comparator group 4, Linkage result of comparator group
10100 | SHORT | RD | - | Comparator group 5, Linkage result of comparator group
10101 | SHORT | RD | - | Comparator group 6, Linkage result of comparator group
10154 | CONF_DB | RD | sec | Total running time, comparator A, comparator group 3
10156 | CONF_DB | RD | sec | Total running time, comparator B, comparator group 3
10158 | CONF_DB | RD | sec | Total running time, comparator C, comparator group 3
10160 | CONF_DB | RD | sec | Total running time, comparator A, comparator group 4
10162 | CONF_DB | RD | sec | Total running time, comparator B, comparator group 4
10164 | CONF_DB | RD | sec | Total running time, comparator C, comparator group 4
10166 | CONF_DB | RD | sec | Total running time, comparator A, comparator group 5
10168 | CONF_DB | RD | sec | Total running time, comparator B, comparator group 5
10170 | CONF_DB | RD | sec | Total running time, comparator C, comparator group 5
10172 | CONF_DB | RD | sec | Total running time, comparator A, comparator group 6
10174 | CONF_DB | RD | sec | Total running time, comparator B, comparator group 6
10176 | CONF_DB | RD | sec | Total running time, comparator C, comparator group 6
10178 | INT | RD | sec | Total running time, comparator A, comparator group 3
10180 | INT | RD | sec | Total running time, comparator B, comparator group 3
10182 | INT | RD | sec | Total running time, comparator C, comparator group 3
10184 | INT | RD | sec | Total running time, comparator A, comparator group 4
10186 | INT | RD | sec | Total running time, comparator B, comparator group 4
10188 | INT | RD | sec | Total running time, comparator C, comparator group 4
10190 | INT | RD | sec | Total running time, comparator A, comparator group 5
10192 | INT | RD | sec | Total running time, comparator B, comparator group 5
10194 | INT | RD | sec | Total running time, comparator C, comparator group 5
10196 | INT | RD | sec | Total running time, comparator A, comparator group 6
10198 | INT | RD | sec | Total running time, comparator B, comparator group 6
10200 | INT | RD | sec | Total running time, comparator C, comparator group 6
22012 | SHORT | RD/WR |  | Results of the comparator group 3, Combine A, B, C | 0, 1 | 0
22013 | FLOAT | RD/WR |  | Comparator 3A, limit | -1012-1..+1012-1 | 0
22015 | SHORT | RD/WR |  | Comparator 3A, Address of measurement value | 0 .. 32000 | 0
22016 | SHORT | RD/WR |  | Comparator 3A, min. on time | 0 .. 32000 | 0
22017 | SHORT | RD/WR |  | Comparator 3A, lead time | 0 .. 32000 | 0
22018 | SHORT | RD/WR |  | Comparator 3A, inverted | 0, 1 | 0
22019 | FLOAT | RD/WR |  | Comparator 3B, limit | -1012-1..+1012-1 | 0
22021 | SHORT | RD/WR |  | Comparator 3B, Address of measurement value | 0 .. 32000 | 0
22022 | SHORT | RD/WR |  | Comparator 3B, min. on time | 0 .. 32000 | 0
22023 | SHORT | RD/WR |  | Comparator 3B, lead time | 0 .. 32000 | 0
22024 | SHORT | RD/WR |  | Comparator 3B, inverted | 0, 1 | 0
22025 | FLOAT | RD/WR |  | Comparator 3C, limit | -1012-1..+1012-1 | 0
22027 | SHORT | RD/WR |  | Comparator 3C, Address of measurement value | 0 .. 32000 | 0
22028 | SHORT | RD/WR |  | Comparator 3C, min. on time | 0 .. 32000 | 0
22029 | SHORT | RD/WR |  | Comparator 3C, lead time | 0 .. 32000 | 0
22030 | SHORT | RD/WR |  | Comparator 3C, inverted | 0, 1 | 0
22031 | SHORT | RD/WR |  | Results of the comparator group 4, Combine A, B, C | 0, 1 | 0
22032 | FLOAT | RD/WR |  | Comparator 4A, limit | -1012-1..+1012-1 | 0
22034 | SHORT | RD/WR |  | Comparator 4A, Address of measurement value | 0 .. 32000 | 0
22035 | SHORT | RD/WR |  | Comparator 4A, min. on time | 0 .. 32000 | 0
22036 | SHORT | RD/WR |  | Comparator 4A, lead time | 0 .. 32000 | 0
22037 | SHORT | RD/WR |  | Comparator 4A, inverted | 0, 1 | 0
22038 | FLOAT | RD/WR |  | Comparator 4B, limit | -1012-1..+1012-1 | 0
22040 | SHORT | RD/WR |  | Comparator 4B, Address of measurement value | 0 .. 32000 | 0
22041 | SHORT | RD/WR |  | Comparator 4B, min. on time | 0 .. 32000 | 0
22042 | SHORT | RD/WR |  | Comparator 4B, lead time | 0 .. 32000 | 0
22043 | SHORT | RD/WR |  | Comparator 4B, inverted | 0, 1 | 0
22044 | FLOAT | RD/WR |  | Comparator 4C, limit | -1012-1..+1012-1 | 0
22046 | SHORT | RD/WR |  | Comparator 4C, Address of measurement value | 0 .. 32000 | 0
22047 | SHORT | RD/WR |  | Comparator 4C, min. on time | 0 .. 32000 | 0
22048 | SHORT | RD/WR |  | Comparator 4C, lead time | 0 .. 32000 | 0
22049 | SHORT | RD/WR |  | Comparator 4C, inverted | 0, 1 | 0
22050 | SHORT | RD/WR |  | Results of the comparator group 5, Combine A, B, C | 0, 1 | 0
22051 | FLOAT | RD/WR |  | Comparator 5A, limit | -1012-1..+1012-1 | 0
22053 | SHORT | RD/WR |  | Comparator 5A, Address of measurement value | 0 .. 32000 | 0
22054 | SHORT | RD/WR |  | Comparator 5A, min. on time | 0 .. 32000 | 0
22055 | SHORT | RD/WR |  | Comparator 5A, lead time | 0 .. 32000 | 0
22056 | SHORT | RD/WR |  | Comparator 5A, inverted | 0, 1 | 0
22057 | FLOAT | RD/WR |  | Comparator 5B, limit | -1012-1..+1012-1 | 0
22059 | SHORT | RD/WR |  | Comparator 5B, Address of measurement value | 0 .. 32000 | 0
22060 | SHORT | RD/WR |  | Comparator 5B, min. on time | 0 .. 32000 | 0
22061 | SHORT | RD/WR |  | Comparator 5B, lead time | 0 .. 32000 | 0
22062 | SHORT | RD/WR |  | Comparator 5B, inverted | 0, 1 | 0
22063 | FLOAT | RD/WR |  | Comparator 5C, limit | -1012-1..+1012-1 | 0
22065 | SHORT | RD/WR |  | Comparator 5C, Address of measurement value | 0 .. 32000 | 0
22066 | SHORT | RD/WR |  | Comparator 5C, min. on time | 0 .. 32000 | 0
22067 | SHORT | RD/WR |  | Comparator 5C, lead time | 0 .. 32000 | 0
22068 | SHORT | RD/WR |  | Comparator 5C, inverted | 0, 1 | 0
22069 | SHORT | RD/WR |  | Results of the comparator group 6, Combine A, B, C | 0, 1 | 0
22070 | FLOAT | RD/WR |  | Comparator 6A, limit | -1012-1..+1012-1 | 0
22072 | SHORT | RD/WR |  | Comparator 6A, Address of measurement value | 0 .. 32000 | 0
22073 | SHORT | RD/WR |  | Comparator 6A, min. on time | 0 .. 32000 | 0
22074 | SHORT | RD/WR |  | Comparator 6A, lead time | 0 .. 32000 | 0
22075 | SHORT | RD/WR |  | Comparator 6A, inverted | 0, 1 | 0
22076 | FLOAT | RD/WR |  | Comparator 6B, limit | -1012-1..+1012-1 | 0
22078 | SHORT | RD/WR |  | Comparator 6B, Address of measurement value | 0 .. 32000 | 0
22079 | SHORT | RD/WR |  | Comparator 6B, min. on time | 0 .. 32000 | 0
22080 | SHORT | RD/WR |  | Comparator 6B, lead time | 0 .. 32000 | 0
22081 | SHORT | RD/WR |  | Comparator 6B, inverted | 0, 1 | 0
22082 | FLOAT | RD/WR |  | Comparator 6C, limit | -1012-1..+1012-1 | 0
22084 | SHORT | RD/WR |  | Comparator 6C, Address of measurement value | 0 .. 32000 | 0
22085 | SHORT | RD/WR |  | Comparator 6C, min. on time | 0 .. 32000 | 0
22086 | SHORT | RD/WR |  | Comparator 6C, lead time | 0 .. 32000 | 0
22087 | SHORT | RD/WR |  | Comparator 6C, inverted | 0, 1 | 0
22088 | SHORT | RD/WR |  | Source selection for digital output 3 | 0 .. 4 | 0
0 = Comparator 3
1 = Pulse output (S0)
2 = External source - Modbus
3 = External source - Profibus (option)
4 = External source - Ethernet (option)
22089 | SHORT | RD/WR |  | Output 3 inverted | 0, 1 | 0
22090 | SHORT | RD/WR |  | Source selection for digital output 4 | 0 .. 4 | 0
0 = Comparator 3
1 = Pulse output (S0)
2 = External source - Modbus
3 = External source - Profibus (option)
4 = External source - Ethernet (option)
22091 | SHORT | RD/WR |  | Output 4 inverted | 0, 1 | 0
22092 | SHORT | RD/WR |  | Source selection for digital output 5 | 0 .. 4 | 0
0 = Comparator 3
1 = Pulse output (S0)
2 = External source - Modbus
3 = External source - Profibus (option)
4 = External source - Ethernet (option)
22093 | SHORT | RD/WR |  | Output 5 inverted | 0, 1 | 0
22094 | SHORT | RD/WR |  | Source selection for digital output 6 | 0 .. 4 | 0
0 = Comparator 3
1 = Pulse output (S0)
2 = External source - Modbus
3 = External source - Profibus (option)
4 = External source - Ethernet (option)
22095 | SHORT | RD/WR |  | Output 6 inverted | 0, 1 | 0
Measured values, type float
Address | Format | RD/WR | Unit | Note | Index
10102 | FLOAT | RD | A | I4, effective value
10104 | FLOAT | RD | % | I4, THD
10106 | FLOAT | RD | % | I4, TDD
10108 | FLOAT | RD |  | Pulse input 1, power
10110 | FLOAT | RD |  | Pulse input 2, power
10112 | FLOAT | RD |  | Pulse input 3, power
10114 | FLOAT | RD |  | Pulse input 4, power
Measured values, type short
Address | Format | RD/WR | Unit | Note | Index | Resolution
10620 | SHORT | RD | mA | I4 current |  | 1
10621 | SHORT | RD | % | I4 current, THD |  | 0.1
10622 | SHORT | RD | % | I4 current, TDD |  | 0.1
10623 | SHORT | RD |  | Pulse input 1, power
10624 | SHORT | RD |  | Pulse input 2, power
10625 | SHORT | RD |  | Pulse input 3, power
10626 | SHORT | RD |  | Pulse input 4, power
Measured values, type integer
Address | Format | RD/WR | Unit | Note | Index
10202 | UINT | RD | n | Meter reading, pulse meter, digital input 1
10204 | UINT | RD | n | Meter reading, pulse meter, digital input 2
10206 | UINT | RD | n | Meter reading, pulse meter, digital input 3
10208 | UINT | RD | n | Meter reading, pulse meter, digital input 4
Mean values, type float
Address | Format | RD/WR | Unit | Note | Index
10116 | FLOAT | RD |  | Pulse input 1, power, average
10118 | FLOAT | RD |  | Pulse input 2, power, average
10120 | FLOAT | RD |  | Pulse input 3, power, average
10122 | FLOAT | RD |  | Pulse input 4, power, average
10140 | FLOAT | RD | A | I4 current, average
10142 | FLOAT | RD | % | I4 current, average, THD
10144 | FLOAT | RD | % | I4 current, average, TDD
Mean values, type short
Address | Format | RD/WR | Unit | Note | Index | Resolution
10667 | SHORT | RD | mA | I4 current, average |  | 1
10668 | SHORT | RD | % | I4 current, average, THD |  | 0.1
10669 | SHORT | RD | % | I4 current, average, TDD |  | 0.1
10670 | SHORT | RD |  | Pulse input 1, power, average
10671 | SHORT | RD |  | Pulse input 2, power, average
10672 | SHORT | RD |  | Pulse input 3, power, average
10673 | SHORT | RD |  | Pulse input 4, power, average
Maximum values, type float
Adresse | Format | RD/WR | Einheit | Bemerkung | Index
10124 | FLOAT | RD |  | Pulse input 1, power, max. value
10126 | FLOAT | RD |  | Pulse input 2, power, max. value
10128 | FLOAT | RD |  | Pulse input 3, power, max. value
10130 | FLOAT | RD |  | Pulse input 4, power, max. value
10146 | FLOAT | RD | A | I4, max. value
10148 | FLOAT | RD | % | I4, THD, max. value
10150 | FLOAT | RD | % | I4, TDD, max. value
10152 | FLOAT | RD | A | I4, max. value of average value
Maximum values, type short
Adresse | Format | RD/WR | Einheit | Bemerkung | Index | Resolution
10714 | SHORT | RD | mA | I4 current, max. value |  | 1
10715 | SHORT | RD | % | I4 current, THD, max. value |  | 0.1
10716 | SHORT | RD | % | I4 current, TDD, max. value |  | 0.1
10717 | SHORT | RD |  | Pulse input 1, power, max. value
10718 | SHORT | RD |  | Pulse input 2, power, max. value
10719 | SHORT | RD |  | Pulse input 3, power, max. value
10720 | SHORT | RD |  | Pulse input 4, power, max. value
10761 | SHORT | RD | A | I4 current, max. value of average value
Minimum values, time stamp
Adresse | Format | RD/WR | Einheit | Bemerkung | Index
10398 | INT | RD | s | Time of min. value (UTC), frequency
10400 | INT | RD | s | Time of min. value (UTC), Voltage zero sequence
10402 | INT | RD | s | Time of min. value (UTC), Voltage negative sequence
10404 | INT | RD | s | Time of min. value (UTC), Voltage positive sequence
10406 | INT | RD | s | Time of min. value (UTC), voltage U L1-N
10408 | INT | RD | s | Time of min. value (UTC), voltage U L2-N
10410 | INT | RD | s | Time of min. value (UTC), voltage U L3-N
10412 | INT | RD | s | Time of min. value (UTC), voltage U L1-L2
10414 | INT | RD | s | Time of min. value (UTC), voltage U L2-L3
10416 | INT | RD | s | Time of min. value (UTC), voltage U L3-12
10418 | INT | RD | s | Time of min. value (UTC), powerfactor fund. L1
10420 | INT | RD | s | Time of min. value (UTC), powerfactor fund. L2
10422 | INT | RD | s | Time of min. value (UTC), powerfactor fund. L3
10424 | INT | RD | s | Time of min. value (UTC), powerfactor fund. Summe
10426 | INT | RD | s | Time of min. value (UTC), powerfactor L1
10428 | INT | RD | s | Time of min. value (UTC), powerfactor L2
10430 | INT | RD | s | Time of min. value (UTC), powerfactor L3
10432 | INT | RD | s | Time of min. value (UTC), powerfactor Summe
10434 | INT | RD | s | Time of min. value (UTC), THD U L1-N
10436 | INT | RD | s | Time of min. value (UTC), THD U L2-N
10438 | INT | RD | s | Time of min. value (UTC), THD U L3-N
10440 | INT | RD | s | Time of min. value (UTC), THD U L1-UL2
10442 | INT | RD | s | Time of min. value (UTC), THD U L2-UL3
10444 | INT | RD | s | Time of min. value (UTC), THD U L3-UL1
10446 | INT | RD | s | Time of min. value (UTC), voltage U L1-N
10448 | INT | RD | s | Time of min. value (UTC), voltage U L2-N
10450 | INT | RD | s | Time of min. value (UTC), voltage U L3-N
10452 | INT | RD | s | Time of min. value (UTC), voltage U L1-L2
10454 | INT | RD | s | Time of min. value (UTC), voltage U L2-L3
10456 | INT | RD | s | Time of min. value (UTC), voltage U L3-12
Maximum values, time stamp
Adresse | Format | RD/WR | Einheit | Bemerkung | Index
10210 | INT | RD | s | Time of max. value (UTC), I4
10212 | INT | RD | s | Time of max. value (UTC), I4 THD
10214 | INT | RD | s | Time of max. value (UTC), I4 TDD
10216 | INT | RD | s | Time of max. value (UTC) of average value, I4
10218 | INT | RD | s | Time of max. value (UTC), pulse input 3
10220 | INT | RD | s | Time of max. value (UTC), pulse input 4
10222 | INT | RD | s | Time of max. value (UTC), pulse input 5
10224 | INT | RD | s | Time of max. value (UTC), pulse input 6
10226 | INT | RD | s | Time of max. value (UTC), frequency
10228 | INT | RD | s | Time of max. value (UTC), Voltage zero sequence
10230 | INT | RD | s | Time of max. value (UTC), Voltage negative sequence
10232 | INT | RD | s | Time of max. value (UTC), Voltage positive sequence
10234 | INT | RD | s | Time of max. value (UTC), voltage U L1-N
10236 | INT | RD | s | Time of max. value (UTC), voltage U L2-N
10238 | INT | RD | s | Time of max. value (UTC), voltage U L3-N
10240 | INT | RD | s | Time of max. value (UTC), voltage U L1-L2
10242 | INT | RD | s | Time of max. value (UTC), voltage U L2-L3
10244 | INT | RD | s | Time of max. value (UTC), voltage U L3-12
10246 | INT | RD | s | Time of max. value (UTC), powerfactor fund. L1
10248 | INT | RD | s | Time of max. value (UTC), powerfactor fund. L2
10250 | INT | RD | s | Time of max. value (UTC), powerfactor fund. L3
10252 | INT | RD | s | Time of max. value (UTC), powerfactor fund. sum
10254 | INT | RD | s | Time of max. value (UTC), powerfactor L1
10256 | INT | RD | s | Time of max. value (UTC), powerfactor L2
10258 | INT | RD | s | Time of max. value (UTC), powerfactor L3
10260 | INT | RD | s | Time of max. value (UTC), powerfactor sum
10262 | INT | RD | s | Time of max. value (UTC), THD U L1-N
10264 | INT | RD | s | Time of max. value (UTC), THD U L2-N
10266 | INT | RD | s | Time of max. value (UTC), THD U L3-N
10268 | INT | RD | s | Time of max. value (UTC), THD U L1-UL2
10270 | INT | RD | s | Time of max. value (UTC), THD U L2-UL3
10272 | INT | RD | s | Time of max. value (UTC), THD U L3-UL1
10292 | INT | RD | s | Time of max. value (UTC)e, real part, U L1-N
10294 | INT | RD | s | Time of max. value (UTC)e, real part, U L2-N
10296 | INT | RD | s | Time of max. value (UTC)e, real part, U L3-N
10298 | INT | RD | s | Time of max. value (UTC)e, imaginary part, U L1-N
10300 | INT | RD | s | Time of max. value (UTC)e, imaginary part, U L2-N
10302 | INT | RD | s | Time of max. value (UTC)e, imaginary part, U L3-N
10304 | INT | RD | s | Time of max. value (UTC)e, current, I1
10306 | INT | RD | s | Time of max. value (UTC)e, current, I2
10308 | INT | RD | s | Time of max. value (UTC)e, current, I3
10310 | INT | RD | s | Time of max. value (UTC)e, current N (sum I1..I3)
10312 | INT | RD | s | Time of max. value (UTC)e, active power, P1
10314 | INT | RD | s | Time of max. value (UTC)e, active power, P2
10316 | INT | RD | s | Time of max. value (UTC)e, active power, P3
10318 | INT | RD | s | Time of max. value (UTC)e, active power, P sum
10320 | INT | RD | s | Time of max. value (UTC)e, reactive power, Q1
10322 | INT | RD | s | Time of max. value (UTC)e, reactive power, Q1
10324 | INT | RD | s | Time of max. value (UTC)e, reactive power, Q1
10326 | INT | RD | s | Time of max. value (UTC)e, reactive power, Q sum
10328 | INT | RD | s | Time of max. value (UTC)e, apparent power, Q1
10330 | INT | RD | s | Time of max. value (UTC)e, apparent power, Q1
10332 | INT | RD | s | Time of max. value (UTC)e, apparent power, Q1
10334 | INT | RD | s | Time of max. value (UTC)e, apparent power, Q sum
10336 | INT | RD | s | Time of max. value (UTC)e, active power, fund., P1
10338 | INT | RD | s | Time of max. value (UTC)e, active power, fund., P2
10340 | INT | RD | s | Time of max. value (UTC)e, active power, fund., P3
10342 | INT | RD | s | Time of max. value (UTC)e, active power, fund., P sum
10344 | INT | RD | s | Time of max. value (UTC), harmonic distortion power D L1-N
10346 | INT | RD | s | Time of max. value (UTC), harmonic distortion power D L2-N
10348 | INT | RD | s | Time of max. value (UTC), harmonic distortion power D L3-N
10350 | INT | RD | s | Time of max. value (UTC), sum; Dsum3=D1+D2+D3
10352 | INT | RD | s | Time of max. value (UTC), THD I1
10354 | INT | RD | s | Time of max. value (UTC), THD I2
10356 | INT | RD | s | Time of max. value (UTC), THD I3
10358 | INT | RD | s | Time of max. value (UTC), TDD I1
10360 | INT | RD | s | Time of max. value (UTC), TDD I2
10362 | INT | RD | s | Time of max. value (UTC), TDD I3
10364 | INT | RD | s | Time of max. value (UTC), Current zero sequence
10366 | INT | RD | s | Time of max. value (UTC), Current negative sequence
10368 | INT | RD | s | Time of max. value (UTC), Current positive sequence
10370 | INT | RD | s | Time of max. value (UTC), real part I1
10372 | INT | RD | s | Time of max. value (UTC), real part I2
10374 | INT | RD | s | Time of max. value (UTC), real part I3
10376 | INT | RD | s | Time of max. value (UTC), imaginary part I1
10378 | INT | RD | s | Time of max. value (UTC), imaginary part I2
10380 | INT | RD | s | Time of max. value (UTC), imaginary part I3
10382 | INT | RD | s | Time of max. value (UTC) of average value I1
10384 | INT | RD | s | Time of max. value (UTC) of average value I2
10386 | INT | RD | s | Time of max. value (UTC) of average value I3
10388 | INT | RD | s | Time of max. value (UTC) of average value N (sum I1..I3)
10390 | INT | RD | s | Time of max. value (UTC) of average value P1
10392 | INT | RD | s | Time of max. value (UTC) of average value P2
10394 | INT | RD | s | Time of max. value (UTC) of average value P3
10396 | INT | RD | s | Time of max. value (UTC) of average value P sum
Peak indicator (drag indicator)
Adresse | Format | RD/WR | Einheit | Bemerkung | Index
5974 | FLOAT | RD | Current I L1; highest value
5976 | FLOAT | RD | Current I L2; highest value
5978 | FLOAT | RD | Current I L3; highest value
5986 | FLOAT | RD | Apparent power S1 L1N; highest value
5988 | FLOAT | RD | Apparent power S2 L2N; highest value
5990 | FLOAT | RD | Apparent power S3 L3N; highest value
5992 | FLOAT | RD | Apparent power; Sum; Ssum3=S1+S2+S3; highest value
6002 | FLOAT | RD | Real power P1 L1N (positiv); highest value
6004 | FLOAT | RD | Real power P2 L2N (positiv); highest value
6006 | FLOAT | RD | Real power P3 L3N (positiv); highest value
6008 | FLOAT | RD | Real power (positiv); Sum; Psum3=P1+P2+P3; highest value
6018 | FLOAT | RD | Real power P1 L1N (negative); highest value
6020 | FLOAT | RD | Real power P2 L2N (negative); highest value
6022 | FLOAT | RD | Real power P3 L3N (negative); highest value
6024 | FLOAT | RD | Real power (negative) Sum; Psum3=P1+P2+P3; highest value
6034 | FLOAT | RD | Current I L1; second highest value
6036 | FLOAT | RD | Current I L2; second highest value
6038 | FLOAT | RD | Current I L3; second highest value
6046 | FLOAT | RD | Apparent power S1 L1N; second highest value
6048 | FLOAT | RD | Apparent power S2 L2N; second highest value
6050 | FLOAT | RD | Apparent power S3 L3N; second highest value
6052 | FLOAT | RD | Apparent power; Sum; Ssum3=S1+S2+S3; second highest value
6062 | FLOAT | RD | Real power P1 L1N (positiv); second highest value
6064 | FLOAT | RD | Real power P2 L2N (positiv); second highest value
6066 | FLOAT | RD | Real power P3 L3N (positiv); second highest value
6068 | FLOAT | RD | Real power (positiv); Sum; Psum3=P1+P2+P3; second highest value
6078 | FLOAT | RD | Real power P1 L1N (negative); second highest value
6080 | FLOAT | RD | Real power P2 L2N (negative); second highest value
6082 | FLOAT | RD | Real power P3 L3N (negative); second highest value
6084 | FLOAT | RD | Real power (negative) Sum; Psum3=P1+P2+P3; second highest value
6094 | FLOAT | RD | Current I L1; third highest value
6096 | FLOAT | RD | Current I L2; third highest value
6098 | FLOAT | RD | Current I L3; third highest value
6106 | FLOAT | RD | Apparent power S1 L1N; third highest value
6108 | FLOAT | RD | Apparent power S2 L2N; third highest value
6110 | FLOAT | RD | Apparent power S3 L3N; third highest value
6112 | FLOAT | RD | Apparent power; Sum; Ssum3=S1+S2+S3; third highest value
6122 | FLOAT | RD | Real power P1 L1N (positiv); third highest value
6124 | FLOAT | RD | Real power P2 L2N (positiv); third highest value
6126 | FLOAT | RD | Real power P3 L3N (positiv); third highest value
6128 | FLOAT | RD | Real power (positiv); Sum; Psum3=P1+P2+P3; third highest value
6138 | FLOAT | RD | Real power P1 L1N (negative); third highest value
6140 | FLOAT | RD | Real power P2 L2N (negative); third highest value
6142 | FLOAT | RD | Real power P3 L3N (negative); third highest value
6144 | FLOAT | RD | Real power (negative) Sum; Psum3=P1+P2+P3; third highest value
5980 | UINT | RD | Time of Current I L1; highest value
5982 | UINT | RD | Time of Current I L2; highest value
5984 | UINT | RD | Time of Current I L3; highest value
5994 | UINT | RD | Time of Apparent power S1 L1N; highest value
5996 | UINT | RD | Time of Apparent power S2 L2N; highest value
5998 | UINT | RD | Time of Apparent power S3 L3N; highest value
6000 | UINT | RD | Time of Apparent power; Sum; Ssum3=S1+S2+S3; highest value
6010 | UINT | RD | Time of Real power P1 L1N (positiv); highest value
6012 | UINT | RD | Time of Real power P2 L2N (positiv); highest value
6014 | UINT | RD | Time of Real power P3 L3N (positiv); highest value
6016 | UINT | RD | Time of Real power (positiv); Sum; Psum3=P1+P2+P3; highest value
6026 | UINT | RD | Time of Real power P1 L1N (negative); highest value
6028 | UINT | RD | Time of Real power P2 L2N (negative); highest value
6030 | UINT | RD | Time of Real power P3 L3N (negative); highest value
6032 | UINT | RD | Time of Real power (negative) Sum; Psum3=P1+P2+P3; highest value
6040 | UINT | RD | Time of Current I L1; second highest value
6042 | UINT | RD | Time of Current I L2; second highest value
6044 | UINT | RD | Time of Current I L3; second highest value
6054 | UINT | RD | Time of Apparent power S1 L1N; second highest value
6056 | UINT | RD | Time of Apparent power S2 L2N; second highest value
6058 | UINT | RD | Time of Apparent power S3 L3N; second highest value
6060 | UINT | RD | Time of Apparent power; Sum; Ssum3=S1+S2+S3; second highest value
6070 | UINT | RD | Time of Real power P1 L1N (positiv); second highest value
6072 | UINT | RD | Time of Real power P2 L2N (positiv); second highest value
6074 | UINT | RD | Time of Real power P3 L3N (positiv); second highest value
6076 | UINT | RD | Time of Real power (positiv); Sum; Psum3=P1+P2+P3; second highest value
6086 | UINT | RD | Time of Real power P1 L1N (negative); second highest value
6088 | UINT | RD | Time of Real power P2 L2N (negative); second highest value
6090 | UINT | RD | Time of Real power P3 L3N (negative); second highest value
6092 | UINT | RD | Time of Real power (negative) Sum; Psum3=P1+P2+P3; second highest value
6100 | UINT | RD | Time of Current I L1; third highest value
6102 | UINT | RD | Time of Current I L2; third highest value
6104 | UINT | RD | Time of Current I L3; third highest value
6114 | UINT | RD | Time of Apparent power S1 L1N; third highest value
6116 | UINT | RD | Time of Apparent power S2 L2N; third highest value
6118 | UINT | RD | Time of Apparent power S3 L3N; third highest value
6120 | UINT | RD | Time of Apparent power; Sum; Ssum3=S1+S2+S3; third highest value
6130 | UINT | RD | Time of Real power P1 L1N (positiv); third highest value
6132 | UINT | RD | Time of Real power P2 L2N (positiv); third highest value
6134 | UINT | RD | Time of Real power P3 L3N (positiv); third highest value
6136 | UINT | RD | Time of Real power (positiv); Sum; Psum3=P1+P2+P3; third highest value
6146 | UINT | RD | Time of Real power P1 L1N (negative); third highest value
6148 | UINT | RD | Time of Real power P2 L2N (negative); third highest value
6150 | UINT | RD | Time of Real power P3 L3N (negative); third highest value
6152 | UINT | RD | Time of Real power (negative) Sum; Psum3=P1+P2+P3; third highest value
Fourier analysis
Measured values, typ float, fourier analysis
Adresse | Format | RD/WR | Einheit | Bemerkung | Index
10000 | FLOAT | RD | A | Harmonic I L4 | [0]
10002 | FLOAT | RD | A | Harmonic I L4 | [1]
10004 | FLOAT | RD | A | Harmonic I L4 | [2]
10006 | FLOAT | RD | A | Harmonic I L4 | [3]
10008 | FLOAT | RD | A | Harmonic I L4 | [4]
10010 | FLOAT | RD | A | Harmonic I L4 | [5]
10012 | FLOAT | RD | A | Harmonic I L4 | [6]
10014 | FLOAT | RD | A | Harmonic I L4 | [7]
10016 | FLOAT | RD | A | Harmonic I L4 | [8]
10018 | FLOAT | RD | A | Harmonic I L4 | [9]
10020 | FLOAT | RD | A | Harmonic I L4 | [10]
10022 | FLOAT | RD | A | Harmonic I L4 | [11]
10024 | FLOAT | RD | A | Harmonic I L4 | [12]
10026 | FLOAT | RD | A | Harmonic I L4 | [13]
10028 | FLOAT | RD | A | Harmonic I L4 | [14]
10030 | FLOAT | RD | A | Harmonic I L4 | [15]
10032 | FLOAT | RD | A | Harmonic I L4 | [16]
10034 | FLOAT | RD | A | Harmonic I L4 | [17]
10036 | FLOAT | RD | A | Harmonic I L4 | [18]
10038 | FLOAT | RD | A | Harmonic I L4 | [19]
10040 | FLOAT | RD | A | Harmonic I L4 | [20]
10042 | FLOAT | RD | A | Harmonic I L4 | [21]
10044 | FLOAT | RD | A | Harmonic I L4 | [22]
10046 | FLOAT | RD | A | Harmonic I L4 | [23]
10048 | FLOAT | RD | A | Harmonic I L4 | [24]
10050 | FLOAT | RD | A | Harmonic I L4 | [25]
10052 | FLOAT | RD | A | Harmonic I L4 | [26]
10054 | FLOAT | RD | A | Harmonic I L4 | [27]
10056 | FLOAT | RD | A | Harmonic I L4 | [28]
10058 | FLOAT | RD | A | Harmonic I L4 | [29]
10060 | FLOAT | RD | A | Harmonic I L4 | [30]
10062 | FLOAT | RD | A | Harmonic I L4 | [31]
10064 | FLOAT | RD | A | Harmonic I L4 | [32]
10066 | FLOAT | RD | A | Harmonic I L4 | [33]
10068 | FLOAT | RD | A | Harmonic I L4 | [34]
10070 | FLOAT | RD | A | Harmonic I L4 | [35]
10072 | FLOAT | RD | A | Harmonic I L4 | [36]
10074 | FLOAT | RD | A | Harmonic I L4 | [37]
10076 | FLOAT | RD | A | Harmonic I L4 | [38]
10078 | FLOAT | RD | A | Harmonic I L4 | [39]
Fourier analysis
Measured values, typ short, fourier analysis
Adresse | Format | RD/WR | Einheit | Bemerkung | Index | Resolution
10627 | SHORT | RD | mA | Harmonic I L4 | [0] | 1
10628 | SHORT | RD | mA | Harmonic I L4 | [1] | 1
10629 | SHORT | RD | mA | Harmonic I L4 | [2] | 1
10630 | SHORT | RD | mA | Harmonic I L4 | [3] | 1
10631 | SHORT | RD | mA | Harmonic I L4 | [4] | 1
10632 | SHORT | RD | mA | Harmonic I L4 | [5] | 1
10633 | SHORT | RD | mA | Harmonic I L4 | [6] | 1
10634 | SHORT | RD | mA | Harmonic I L4 | [7] | 1
10635 | SHORT | RD | mA | Harmonic I L4 | [8] | 1
10636 | SHORT | RD | mA | Harmonic I L4 | [9] | 1
10637 | SHORT | RD | mA | Harmonic I L4 | [10] | 1
10638 | SHORT | RD | mA | Harmonic I L4 | [11] | 1
10639 | SHORT | RD | mA | Harmonic I L4 | [12] | 1
10640 | SHORT | RD | mA | Harmonic I L4 | [13] | 1
10641 | SHORT | RD | mA | Harmonic I L4 | [14] | 1
10642 | SHORT | RD | mA | Harmonic I L4 | [15] | 1
10643 | SHORT | RD | mA | Harmonic I L4 | [16] | 1
10644 | SHORT | RD | mA | Harmonic I L4 | [17] | 1
10645 | SHORT | RD | mA | Harmonic I L4 | [18] | 1
10646 | SHORT | RD | mA | Harmonic I L4 | [19] | 1
10647 | SHORT | RD | mA | Harmonic I L4 | [20] | 1
10648 | SHORT | RD | mA | Harmonic I L4 | [21] | 1
10649 | SHORT | RD | mA | Harmonic I L4 | [22] | 1
10650 | SHORT | RD | mA | Harmonic I L4 | [23] | 1
10651 | SHORT | RD | mA | Harmonic I L4 | [24] | 1
10652 | SHORT | RD | mA | Harmonic I L4 | [25] | 1
10653 | SHORT | RD | mA | Harmonic I L4 | [26] | 1
10654 | SHORT | RD | mA | Harmonic I L4 | [27] | 1
10655 | SHORT | RD | mA | Harmonic I L4 | [28] | 1
10656 | SHORT | RD | mA | Harmonic I L4 | [29] | 1
10657 | SHORT | RD | mA | Harmonic I L4 | [30] | 1
10658 | SHORT | RD | mA | Harmonic I L4 | [31] | 1
10659 | SHORT | RD | mA | Harmonic I L4 | [32] | 1
10660 | SHORT | RD | mA | Harmonic I L4 | [33] | 1
10661 | SHORT | RD | mA | Harmonic I L4 | [34] | 1
10662 | SHORT | RD | mA | Harmonic I L4 | [35] | 1
10663 | SHORT | RD | mA | Harmonic I L4 | [36] | 1
10664 | SHORT | RD | mA | Harmonic I L4 | [37] | 1
10665 | SHORT | RD | mA | Harmonic I L4 | [38] | 1
10666 | SHORT | RD | mA | Harmonic I L4 | [39] | 1
Mean values, typ float, fourier analysis
Adresse | Format | RD/WR | Einheit | Bemerkung | Index
10540 | FLOAT | RD | A | Average, Harmonic I L4 | [0]
10542 | FLOAT | RD | A | Average, Harmonic I L4 | [1]
10544 | FLOAT | RD | A | Average, Harmonic I L4 | [2]
10546 | FLOAT | RD | A | Average, Harmonic I L4 | [3]
10548 | FLOAT | RD | A | Average, Harmonic I L4 | [4]
10550 | FLOAT | RD | A | Average, Harmonic I L4 | [5]
10552 | FLOAT | RD | A | Average, Harmonic I L4 | [6]
10554 | FLOAT | RD | A | Average, Harmonic I L4 | [7]
10556 | FLOAT | RD | A | Average, Harmonic I L4 | [8]
10558 | FLOAT | RD | A | Average, Harmonic I L4 | [9]
10560 | FLOAT | RD | A | Average, Harmonic I L4 | [10]
10562 | FLOAT | RD | A | Average, Harmonic I L4 | [11]
10564 | FLOAT | RD | A | Average, Harmonic I L4 | [12]
10566 | FLOAT | RD | A | Average, Harmonic I L4 | [13]
10568 | FLOAT | RD | A | Average, Harmonic I L4 | [14]
10570 | FLOAT | RD | A | Average, Harmonic I L4 | [15]
10572 | FLOAT | RD | A | Average, Harmonic I L4 | [16]
10574 | FLOAT | RD | A | Average, Harmonic I L4 | [17]
10576 | FLOAT | RD | A | Average, Harmonic I L4 | [18]
10578 | FLOAT | RD | A | Average, Harmonic I L4 | [19]
10580 | FLOAT | RD | A | Average, Harmonic I L4 | [20]
10582 | FLOAT | RD | A | Average, Harmonic I L4 | [21]
10584 | FLOAT | RD | A | Average, Harmonic I L4 | [22]
10586 | FLOAT | RD | A | Average, Harmonic I L4 | [23]
10588 | FLOAT | RD | A | Average, Harmonic I L4 | [24]
10590 | FLOAT | RD | A | Average, Harmonic I L4 | [25]
10592 | FLOAT | RD | A | Average, Harmonic I L4 | [26]
10594 | FLOAT | RD | A | Average, Harmonic I L4 | [27]
10596 | FLOAT | RD | A | Average, Harmonic I L4 | [28]
10598 | FLOAT | RD | A | Average, Harmonic I L4 | [29]
10600 | FLOAT | RD | A | Average, Harmonic I L4 | [30]
10602 | FLOAT | RD | A | Average, Harmonic I L4 | [31]
10604 | FLOAT | RD | A | Average, Harmonic I L4 | [32]
10606 | FLOAT | RD | A | Average, Harmonic I L4 | [33]
10608 | FLOAT | RD | A | Average, Harmonic I L4 | [34]
10610 | FLOAT | RD | A | Average, Harmonic I L4 | [35]
10612 | FLOAT | RD | A | Average, Harmonic I L4 | [36]
10614 | FLOAT | RD | A | Average, Harmonic I L4 | [37]
10616 | FLOAT | RD | A | Average, Harmonic I L4 | [38]
10618 | FLOAT | RD | A | Average, Harmonic I L4 | [39]
Mean values, typ short, fourier analysis
Adresse | Format | RD/WR | Einheit | Bemerkung | Index | Resolution
10674 | SHORT | RD | mA | Average, Harmonic I L4 | [0] | 1
10675 | SHORT | RD | mA | Average, Harmonic I L4 | [1] | 1
10676 | SHORT | RD | mA | Average, Harmonic I L4 | [2] | 1
10677 | SHORT | RD | mA | Average, Harmonic I L4 | [3] | 1
10678 | SHORT | RD | mA | Average, Harmonic I L4 | [4] | 1
10679 | SHORT | RD | mA | Average, Harmonic I L4 | [5] | 1
10680 | SHORT | RD | mA | Average, Harmonic I L4 | [6] | 1
10681 | SHORT | RD | mA | Average, Harmonic I L4 | [7] | 1
10682 | SHORT | RD | mA | Average, Harmonic I L4 | [8] | 1
10683 | SHORT | RD | mA | Average, Harmonic I L4 | [9] | 1
10684 | SHORT | RD | mA | Average, Harmonic I L4 | [10] | 1
10685 | SHORT | RD | mA | Average, Harmonic I L4 | [11] | 1
10686 | SHORT | RD | mA | Average, Harmonic I L4 | [12] | 1
10687 | SHORT | RD | mA | Average, Harmonic I L4 | [13] | 1
10688 | SHORT | RD | mA | Average, Harmonic I L4 | [14] | 1
10689 | SHORT | RD | mA | Average, Harmonic I L4 | [15] | 1
10690 | SHORT | RD | mA | Average, Harmonic I L4 | [16] | 1
10691 | SHORT | RD | mA | Average, Harmonic I L4 | [17] | 1
10692 | SHORT | RD | mA | Average, Harmonic I L4 | [18] | 1
10693 | SHORT | RD | mA | Average, Harmonic I L4 | [19] | 1
10694 | SHORT | RD | mA | Average, Harmonic I L4 | [20] | 1
10695 | SHORT | RD | mA | Average, Harmonic I L4 | [21] | 1
10696 | SHORT | RD | mA | Average, Harmonic I L4 | [22] | 1
10697 | SHORT | RD | mA | Average, Harmonic I L4 | [23] | 1
10698 | SHORT | RD | mA | Average, Harmonic I L4 | [24] | 1
10699 | SHORT | RD | mA | Average, Harmonic I L4 | [25] | 1
10700 | SHORT | RD | mA | Average, Harmonic I L4 | [26] | 1
10701 | SHORT | RD | mA | Average, Harmonic I L4 | [27] | 1
10702 | SHORT | RD | mA | Average, Harmonic I L4 | [28] | 1
10703 | SHORT | RD | mA | Average, Harmonic I L4 | [29] | 1
10704 | SHORT | RD | mA | Average, Harmonic I L4 | [30] | 1
10705 | SHORT | RD | mA | Average, Harmonic I L4 | [31] | 1
10706 | SHORT | RD | mA | Average, Harmonic I L4 | [32] | 1
10707 | SHORT | RD | mA | Average, Harmonic I L4 | [33] | 1
10708 | SHORT | RD | mA | Average, Harmonic I L4 | [34] | 1
10709 | SHORT | RD | mA | Average, Harmonic I L4 | [35] | 1
10710 | SHORT | RD | mA | Average, Harmonic I L4 | [36] | 1
10711 | SHORT | RD | mA | Average, Harmonic I L4 | [37] | 1
10712 | SHORT | RD | mA | Average, Harmonic I L4 | [38] | 1
10713 | SHORT | RD | mA | Average, Harmonic I L4 | [39] | 1
Maximum values, typ float, fourier analysis
Adresse | Format | RD/WR | Einheit | Bemerkung | Index
10460 | FLOAT | RD | A | Maximum, Harmonic I L4 | [0]
10462 | FLOAT | RD | A | Maximum, Harmonic I L4 | [1]
10464 | FLOAT | RD | A | Maximum, Harmonic I L4 | [2]
10466 | FLOAT | RD | A | Maximum, Harmonic I L4 | [3]
10468 | FLOAT | RD | A | Maximum, Harmonic I L4 | [4]
10470 | FLOAT | RD | A | Maximum, Harmonic I L4 | [5]
10472 | FLOAT | RD | A | Maximum, Harmonic I L4 | [6]
10474 | FLOAT | RD | A | Maximum, Harmonic I L4 | [7]
10476 | FLOAT | RD | A | Maximum, Harmonic I L4 | [8]
10478 | FLOAT | RD | A | Maximum, Harmonic I L4 | [9]
10480 | FLOAT | RD | A | Maximum, Harmonic I L4 | [10]
10482 | FLOAT | RD | A | Maximum, Harmonic I L4 | [11]
10484 | FLOAT | RD | A | Maximum, Harmonic I L4 | [12]
10486 | FLOAT | RD | A | Maximum, Harmonic I L4 | [13]
10488 | FLOAT | RD | A | Maximum, Harmonic I L4 | [14]
10490 | FLOAT | RD | A | Maximum, Harmonic I L4 | [15]
10492 | FLOAT | RD | A | Maximum, Harmonic I L4 | [16]
10494 | FLOAT | RD | A | Maximum, Harmonic I L4 | [17]
10496 | FLOAT | RD | A | Maximum, Harmonic I L4 | [18]
10498 | FLOAT | RD | A | Maximum, Harmonic I L4 | [19]
10500 | FLOAT | RD | A | Maximum, Harmonic I L4 | [20]
10502 | FLOAT | RD | A | Maximum, Harmonic I L4 | [21]
10504 | FLOAT | RD | A | Maximum, Harmonic I L4 | [22]
10506 | FLOAT | RD | A | Maximum, Harmonic I L4 | [23]
10508 | FLOAT | RD | A | Maximum, Harmonic I L4 | [24]
10510 | FLOAT | RD | A | Maximum, Harmonic I L4 | [25]
10512 | FLOAT | RD | A | Maximum, Harmonic I L4 | [26]
10514 | FLOAT | RD | A | Maximum, Harmonic I L4 | [27]
10516 | FLOAT | RD | A | Maximum, Harmonic I L4 | [28]
10518 | FLOAT | RD | A | Maximum, Harmonic I L4 | [29]
10520 | FLOAT | RD | A | Maximum, Harmonic I L4 | [30]
10522 | FLOAT | RD | A | Maximum, Harmonic I L4 | [31]
10524 | FLOAT | RD | A | Maximum, Harmonic I L4 | [32]
10526 | FLOAT | RD | A | Maximum, Harmonic I L4 | [33]
10528 | FLOAT | RD | A | Maximum, Harmonic I L4 | [34]
10530 | FLOAT | RD | A | Maximum, Harmonic I L4 | [35]
10532 | FLOAT | RD | A | Maximum, Harmonic I L4 | [36]
10534 | FLOAT | RD | A | Maximum, Harmonic I L4 | [37]
10536 | FLOAT | RD | A | Maximum, Harmonic I L4 | [38]
10538 | FLOAT | RD | A | Maximum, Harmonic I L4 | [39]
Maximum values, typ short, fourier analysis
Adresse | Format | RD/WR | Einheit | Bemerkung | Index | Resolution
10721 | SHORT | RD | mA | Maximum, Harmonic I L4 | [0] | 1
10722 | SHORT | RD | mA | Maximum, Harmonic I L4 | [1] | 1
10723 | SHORT | RD | mA | Maximum, Harmonic I L4 | [2] | 1
10724 | SHORT | RD | mA | Maximum, Harmonic I L4 | [3] | 1
10725 | SHORT | RD | mA | Maximum, Harmonic I L4 | [4] | 1
10726 | SHORT | RD | mA | Maximum, Harmonic I L4 | [5] | 1
10727 | SHORT | RD | mA | Maximum, Harmonic I L4 | [6] | 1
10728 | SHORT | RD | mA | Maximum, Harmonic I L4 | [7] | 1
10729 | SHORT | RD | mA | Maximum, Harmonic I L4 | [8] | 1
10730 | SHORT | RD | mA | Maximum, Harmonic I L4 | [9] | 1
10731 | SHORT | RD | mA | Maximum, Harmonic I L4 | [10] | 1
10732 | SHORT | RD | mA | Maximum, Harmonic I L4 | [11] | 1
10733 | SHORT | RD | mA | Maximum, Harmonic I L4 | [12] | 1
10734 | SHORT | RD | mA | Maximum, Harmonic I L4 | [13] | 1
10735 | SHORT | RD | mA | Maximum, Harmonic I L4 | [14] | 1
10736 | SHORT | RD | mA | Maximum, Harmonic I L4 | [15] | 1
10737 | SHORT | RD | mA | Maximum, Harmonic I L4 | [16] | 1
10738 | SHORT | RD | mA | Maximum, Harmonic I L4 | [17] | 1
10739 | SHORT | RD | mA | Maximum, Harmonic I L4 | [18] | 1
10740 | SHORT | RD | mA | Maximum, Harmonic I L4 | [19] | 1
10741 | SHORT | RD | mA | Maximum, Harmonic I L4 | [20] | 1
10742 | SHORT | RD | mA | Maximum, Harmonic I L4 | [21] | 1
10743 | SHORT | RD | mA | Maximum, Harmonic I L4 | [22] | 1
10744 | SHORT | RD | mA | Maximum, Harmonic I L4 | [23] | 1
10745 | SHORT | RD | mA | Maximum, Harmonic I L4 | [24] | 1
10746 | SHORT | RD | mA | Maximum, Harmonic I L4 | [25] | 1
10747 | SHORT | RD | mA | Maximum, Harmonic I L4 | [26] | 1
10748 | SHORT | RD | mA | Maximum, Harmonic I L4 | [27] | 1
10749 | SHORT | RD | mA | Maximum, Harmonic I L4 | [28] | 1
10750 | SHORT | RD | mA | Maximum, Harmonic I L4 | [29] | 1
10751 | SHORT | RD | mA | Maximum, Harmonic I L4 | [30] | 1
10752 | SHORT | RD | mA | Maximum, Harmonic I L4 | [31] | 1
10753 | SHORT | RD | mA | Maximum, Harmonic I L4 | [32] | 1
10754 | SHORT | RD | mA | Maximum, Harmonic I L4 | [33] | 1
10755 | SHORT | RD | mA | Maximum, Harmonic I L4 | [34] | 1
10756 | SHORT | RD | mA | Maximum, Harmonic I L4 | [35] | 1
10757 | SHORT | RD | mA | Maximum, Harmonic I L4 | [36] | 1
10758 | SHORT | RD | mA | Maximum, Harmonic I L4 | [37] | 1
10759 | SHORT | RD | mA | Maximum, Harmonic I L4 | [38] | 1
10760 | SHORT | RD | mA | Maximum, Harmonic I L4 | [39] | 1