## Hold Register
Holding Registers, Function code 03/10
Address Register | Parameter | Modbus Protocol Start Address(Hex) |  | Valid Range | Mode
|  | Hi Byte | Lo Byte
40003 | Demand Period | 00 | 02 | Write demand period: 0~60 minutes.Default 60. Setting the period to 0 will cause the “Phase # current demand” parameters to show the “Phase # current values”; and “Max. phase # current demand” to show the maximum value of the “Phase # current” parameter since last demand reset. Length : 4 byte Data Format : Float | r/w
40013 | Pulse 1 Width | 00 | OC | Write pulse on period in milliseconds: 60, 100 or 200, default 200. Length : 4 byte Data Format : Float | r/w
40019 | Parity and Stop bits | 00 | 12 | Write the network port parity/stop bits for MODBUS Protocol, where: 0 = One stop bit and no parity, default. 1 = One stop bit and even parity. 2 = One stop bit and odd parity.3 = Two stop bits and no parity. Length : 4 byte Data Format : Float | r/w
40021 | Modbus Address | 00 | 14 | Write the network port node Address: 1 to 247 for MODBUS Protocol, default 1. Length : 4 byte Data Format : Float | r/w
40029 | Network Baud Rate | 00 | 1C | Write the network port baud rate for MODBUS Protocol, where: 0= 2400 baud. 1 = 4800 baud. 2= 9600 baud, (default) 3= 19200 baud. 4 = 38400 baud 5= 1200 band Length : 4 byte Data Format : Float | r/w
40087 | Pulse 1 Energy Type | 00 | 56 | Write MODBUS Protocol input parameter for pulse output 1： 1: import active energy 2: total active energy 4: export active energy, (default) 5: import reactive energy 6: total reactive energy 8: export reactive energy Length : 4 byte Data Format : Float | r/w
461457 | Reset | F0 | 10 | 00 00 : reset the demand informaiton 00 03 : reset energy information Length : 2 byte Data Format:Hex | wo
463745 | Time of scroll display | F9 | 00 | 0-30s Default 0: does not display in turns Length: 2 bytes Data Format:BCD | r/w
463761 | Pulse 1 output | F9 | 10 | 0000:0.001kWh/imp(default) 0001:0.01kWh/imp 0002:0.1kWh/imp 0003:1kWh/imp Length : 2 byte Data Format:Hex | r/w
464513 | Serial number | FC | 00 | Serial number Length: 4 bytes Data Format:Unsigned Int 32 | ro

## Input Register
Input Registers, Function code 04
Address (Register) | Input Register Parameter |  |  |  | Modbus Protocol Start Address(Hex)
| Description | Length （byte） | Data Format | Units | Hi byte | Lo byte
30001 | Line to neutral volts | 4 | Float | V | 00 | 00
30007 | Current | 4 | Float | A | 00 | 06
30013 | Active power | 4 | Float | W | 00 | 0C
30019 | Apparent power | 4 | Float | VA | 00 | 12
30025 | Reactive power | 4 | Float | VAr | 00 | 18
30031 | Power factor(1) | 4 | Float | None | 00 | 1E
30071 | Frequency of supply voltages | 4 | Float | Hz | 00 | 46
30073 | Import Wh since last reset | 4 | Float | kWh | 00 | 48
30075 | Export Wh since last reset | 4 | Float | kWH | 00 | 4A
30077 | Import VArh since last reset | 4 | Float | kVArh | 00 | 4C
30079 | Export VArh since last reset | 4 | Float | kVArh | 00 | 4E
30085 | Total system power demand(2) | 4 | Float | W | 00 | 54
30087 | Maximum total system power demand(2) | 4 | Float | W | 00 | 56
30089 | Import active power demand | 4 | Float | W | 00 | 58
30091 | Import active power max. demand | 4 | Float | W | 00 | 5A
30093 | Export active power demand | 4 | Float | W | 00 | 5C
30095 | Export active power max. demand | 4 | Float | W | 00 | 5E
30259 | Current demand | 4 | Float | A | 01 | 02
30265 | Maximum phase 1 current demand | 4 | Float | A | 01 | 08
30343 | Total kwh(3) | 4 | Float | kWh | 01 | 56
30345 | Total kvarh(3) | 4 | Float | kVArh | 01 | 58
Notes:
1. The power factor has its sign adjusted to indicate the direction of the current. Positive refers to forward current, negative refers to reverse current.
2. The power sum demand calculation is for import – export.
3.Total kWh / kVarh equals to Import + export.