## Hold Register
Holding Registers, Function code 03/10
Address Register | Parameter | Modbus Protocol Start Address(Hex) |  | Valid Range | Mode
|  | Hi Byte | Lo Byte
40001 | Demand Time | 00 | 00 | Read minutes into first demand calculation. When the Demand Time reaches the Demand Period then the demand values are valid. Length : 4 byte Data Format : Float | ro
40003 | Demand Period | 00 | 02 | Write demand period: 0~60 minutes.Default 60. Setting the period to 0 will cause the “Phase # current demand” parameters to show the “Phase # current values”; and “Max. phase # current demand” to show the maximum value of the “Phase # current” parameter since last demand reset. Length : 4 byte Data Format : Float | r/w
40005 | Slide time | 00 | 04 | Default 1, min. Range ：1 ~ (Demand Period -1). Length : 4 byte Data Format : Float | r/w
40007 | Demand Calculation Method | 00 | 06 | Default 0, 0 = Slide time; 1 = Fixed time Length : 4 byte Data Format : Float | r/w
40011 | System Type | 00 | 0A | Write system type: 3p4w = 3, 3p3w = 2 &1p2w= 1 Default, 3 Length : 4 byte Data Format : Float (KPPA is asked) | r/w
40015 | Key Parameter Programming Authorization (KPPA) | 00 | 0E | Read: to get the status of the KPPA 0 = not authorized；1 = authorized Write the correct password to get KPPA,enable to program key parameters. Length : 4 byte Data Format : Float | r/w
40019 | Parity and Stop bits | 00 | 12 | Write the network port parity/stop bits for MODBUS Protocol, where: 0 = One stop bit and no parity, default. 1 = One stop bit and even parity. 2 = One stop bit and odd parity.3 = Two stop bits and no parity. Length : 4 byte Data Format : Float | r/w
40021 | Modbus Address | 00 | 14 | Write the network port node Address: 1 to 247 for MODBUS Protocol, default 1. Length : 4 byte Data Format : Float | r/w
40025 | Password | 00 | 18 | Read: to get the password of the meter Write: to program the new password of the meter Default 1000 Length : 4 byte Data Format : Float | r/w
40029 | Network Baud Rate | 00 | 1C | Write the network port baud rate for MODBUS Protocol, where: 0= 2400 baud. 1 = 4800 baud. 2= 9600 baud, (default) 3= 19200 baud. 4 = 38400 baud 5= 1200 band Length : 4 byte Data Format : Float | r/w
40047 | PT1 | 00 | 2E | PT1 Range 174- 500000V, Default 400 Length : 4 byte Data Format : Float (KPPA is asked) | r/w
40049 | PT2 | 00 | 30 | PT2 Range 174- 480V, Default 400 Length : 4 byte Data Format : Float (KPPA is asked) | r/w
40051 | CT1 | 00 | 32 | CT1 Range 1-9999A，Default 5， Length : 4 byte Data Format : Float (KPPA is asked) | r/w
40053 | CT2 | 00 | 34 | CT2 Default 5A Range: 1A or 5A Length : 4 byte Data Format : Float (KPPA is asked) | r/w
40057 | Current Direction correction(when theexternal CT is connected reversely） | 00 | 38 | Default 0 0= A Frd，B Frd，C Frd 1= A Rev，B Frd ，C Frd 2= A Frd ，B Rev，C Frd 3= A Rev，B Rev，C Frd 4= A Frd ，B Frd ，C Rev 5= A Rev，B Frd ，C Rev 6= A Frd ，B Rev ，C Rev 7= A Rev ，B Rev ，C Rev Length : 4 byte Data Format :Float (KPPA is asked) | r/w
40059 | Automatic Scroll Display Time | 00 | 3A | Default 5，second Range 1~255 Length : 4 byte Data Format : Float | r/w
40061 | Backlit time | 00 | 3C | Default 0, min Range 0~120，0 means backlit always on Length : 4byte Data Format : Float | r/w
40513 | DO-1 mode | 02 | 00 | DO-1 output mode 00 00: level 00 01: pulse Length: 2 byte Data Format: Hex | r/w
40514 | DO-2 mode | 02 | 01 | DO-2 output mode 00 00: level 00 01: pulse Length: 2 byte Data Format: Hex | r/w
40521 | DO-1 pulse duration | 02 | 08 | DO-1 pulse duration (1000ms: 50 ~ 3000) Length: 2 byte Data Format: unsigned int16 | r/w
40522 | DO-2 pulse duration | 02 | 09 | DO-2 pulse duration (1000ms: 50 ~ 3000) Length: 2 byte Data Format: unsigned int16 | r/w
40769 | DI filter time | 03 | 00 | DI filter time (0ms: 0~255) , Default 100ms Length: 2 byte Data Format: unsigned int16 | r/w
40770 | DI-1 count | 03 | 01 | DI-1 count Write 0 to reset the count. No response if write other value Length: 4 byte Data Format: unsigned int32 | r/w
40772 | DI-2 count | 03 | 03 | DI-2 count Write 0 to reset the count. No response if write other value Length: 4 byte Data Format: unsigned int32 | r/w
40774 | DI-3 count | 03 | 05 | DI-3 count Write 0 to reset the count. No response if write other value Length: 4 byte Data Format: unsigned int32 | r/w
40776 | DI-4 count | 03 | 07 | DI-4 count Write 0 to reset the count. No response if write other value Length: 4 byte Data Format: unsigned int32 | r/w
41025 | DO-1 Alarm Parameter(1) | 04 | 00 | DO-1 Alarm parameter Range: 0~29，and 255； Default: 255 = null Length: 2 byte Data Format: unsigned int16 | r/w
41026 | DO-1 Action delay time | 04 | 01 | DO-1 Action delay time, unit: ms Range:0~9999；default: 200ms Length : 2 byte Data Format: unsigned int16 | r/w
41027 | DO-1 HC value(2) | 04 | 02 | DO-1 High value to close Length: 4 byte Data Format: Float | r/w
41029 | DO-1 HO value(2) | 04 | 04 | DO-1 High value to open Length: 4 byte Data Format: Float | r/w
41031 | DO-1 LO value(2) | 04 | 06 | DO-1 Low value to open Length: 4 byte Data Format: Float | r/w
41033 | DO-1 LC value(2) | 04 | 08 | DO-1 Low value to close Length: 4 byte Data Format: Float | r/w
41035 | DO-2 Alarm Parameter(1) | 04 | 0A | DO-2 Alarm parameter Range: 0~29，and 255； Default: 255 = null Length: 2 byte Data Format: unsigned int16 | r/w
41036 | DO-2 Action delay time | 04 | 0B | DO-2 Action delay time, unit: ms Range:0~9999；default: 200ms Length : 2 byte Data Format: unsigned int16 | r/w
41037 | DO-2 HC value(2) | 04 | 0C | DO-2 High value to close Length: 4 byte Data Format: Float | r/w
41039 | DO-2 HO value(2) | 04 | 0E | DO-2 High value to open Length: 4 byte Data Format: Float | r/w
41041 | DO-2 LO value(2) | 04 | 10 | DO-2 Low value to open Length: 4 byte Data Format: Float | r/w
41043 | DO-2 LC value(2) | 04 | 12 | DO-2 Low value to close Length: 4 byte Data Format: Float | r/w
41105 | DO-1 Status | 04 | 50 | DO-1 Status 0 = Open (HO or LO) 1 = HC 2 = LC Length: 2 byte Data Format: unsigned int16 | ro
41106 | DO-2 Status | 04 | 51 | DO-2 Status 0 = Open (HO or LO) 1 = HC 2 = LC Length: 2 byte Data Format: unsigned int16 | ro
41281 | SOE-01(3) | 05 | 00 | SOE-01 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41285 | SOE-02(3) | 05 | 04 | SOE-02 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41289 | SOE-03(3) | 05 | 08 | SOE-03 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41293 | SOE-04(3) | 05 | 0C | SOE-04 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41297 | SOE-05(3) | 05 | 10 | SOE-05 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41301 | SOE-06(3) | 05 | 14 | SOE-06 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41305 | SOE-07(3) | 05 | 18 | SOE-07 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41309 | SOE-08(3) | 05 | 1C | SOE-08 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41313 | SOE-09(3) | 05 | 20 | SOE-09 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41317 | SOE-10(3) | 05 | 24 | SOE-10 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41321 | SOE-11(3) | 05 | 28 | SOE-11 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41325 | SOE-12(3) | 05 | 2C | SOE-12 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41329 | SOE-13(3) | 05 | 30 | SOE-13 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41333 | SOE-14(3) | 05 | 34 | SOE-14 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41337 | SOE-15(3) | 05 | 38 | SOE-15 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41341 | SOE-16(3) | 05 | 3C | SOE-16 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41345 | SOE-17(3) | 05 | 40 | SOE-17 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41349 | SOE-18(3) | 05 | 44 | SOE-18 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41353 | SOE-19(3) | 05 | 48 | SOE-19 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41357 | SOE-20(3) | 05 | 4C | SOE-20 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41361 | SOE-21(3) | 05 | 50 | SOE-21 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41365 | SOE-22(3) | 05 | 54 | SOE-22 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41369 | SOE-23(3) | 05 | 58 | SOE-23 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41373 | SOE-24(3) | 05 | 5C | SOE-24 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41377 | SOE-25(3) | 05 | 60 | SOE-25 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41381 | SOE-26(3) | 05 | 64 | SOE-26 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41385 | SOE-27(3) | 05 | 68 | SOE-27 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41389 | SOE-28(3) | 05 | 6C | SOE-28 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41393 | SOE-29(3) | 05 | 70 | SOE-29 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
41397 | SOE-30(3) | 05 | 74 | SOE-30 information; the format is: type-event cause-year-month-date-hour-min-second Length: 8 byte Data Format : BCD | ro
461441 | Time | F0 | 00 | s-min-hour-week-Date-Month-Year-20 Length: 8 byte Data Format: BCD | r/w
461445 | Running time | F0 | 04 | Day-hour-minute, day = 2byte; hour = 1byte; minute=1byte For example: 04 23 21 57 refer to Running time=423 day+21 hour+57 min Write 00 00 00 00 to reset the running hour Length: 4 byte Data Format: BCD | r/w
461447 | Ethernet communication Parameter | F0 | 06 | Ethernet communication parameter includes: IP address (4byte)，subnet mask (4byte)， default gateway (4byte)，IP port(2 byte) Data format ： IP Address-Subnet mask- default gateway- IP port，High byte first. Default：IP Address = 192-168-1-200 Subnet mask = 255-255-255-0 Gate way = 192-168-1-1 IP Port = 502 Length : 14byte Data Format: Hex | r/w
461454 | Ethernet TCP/IP working mode | F0 | 0D | Ethernet TCP/IP working mode 00 00 = slave mode (the Ethernet port is only used for TCP/IP communication for this meter); 00 01 = master mode (the meter can be worked as an RS485-TCP/IP gateway. Via the Ethernet port, it can read the devices connected to its RS485 port on the same Bus line.) Length : 2byte Data Format: Hex (KPPA is asked) | r/w
461457 | Reset | F0 | 10 | 00 00 : reset the demand informaiton 00 03 : reset energy information Length : 2 byte Data Format:Hex | wo
461697 | Meter Info | F1 | 00 | Meter identity code：meter model and software version Length : 16 byte Data Format: AscII（Character ASCII） | ro
463233 | Tariff | F7 | 00 | Tariff number-Min-Hour Tariff number：01，02，03，04 Min：00-59 Hour：00-23 Length : 30 byte Data Format : BCD | r/w
463793 | Running time | F9 | 30 | Continuous working period--hour Length : 4 byte Data Format : Float | r/w
464513 | Serial number | FC | 00 | Serial number Length: 4 bytes Data Format:Unsigned Int 32 | ro
Note:
(1) Table 1 Alarm Parameter
Number | Alarm parameter
0 | Phase 1 line to neutral volts
1 | Phase 2 line to neutral volts
2 | Phase 3 line to neutral volts
3 | Average line to neutral volts
4 | Line 1 to Line 2 volts
5 | Line 2 to Line 3 volts
6 | Line 3 to Line 1 volts
7 | Average line to line volts
8 | Phase 1 current
9 | Phase 2 current
10 | Phase 3 current
11 | Average line current
12 | Neutral current
13 | Phase 1 active power
14 | Phase 2 active power
15 | Phase 3 active power
16 | Total system power
17 | Phase 1 reactive power
18 | Phase 2 reactive power
19 | Phase 3 reactive power
20 | Total system Var
21 | Phase 1 apparent power
22 | Phase 2 apparent power
23 | Phase 3 apparent power
24 | Total system volt amps
25 | Phase 1 power factor
26 | Phase 2 power factor
27 | Phase 3 power factor
28 | Total system power factor
29 | Frequency of supply voltages
(2) Please make sure during the setting: HC>HO >LO >LC
(3) SOE information format: type-status-year-month-date-hour-min-second
Type: 0~67 and 99 (4 table-2)
Event cause: 0 = null; 1 and 2 refer to the cause of event. 1 = HC alarm caused event; 2 = LC alarm caused event
Year: the year when event happened. For example: 2017, year=17
Month: the month when event happened
Date: the date when event happened
Hour: the hour when event happened
Min: The Minute when event happened
Second: the second when event happened
(4) Table-2 Event descriptions
Number | Event description
0 | L1 Voltage alarm
1 | L2 Voltage alarm
2 | L3 Voltage alarm
3 | L-N Average voltage alarm
4 | L1-2 Voltage alarm
5 | L2-3 Voltage alarm
6 | L3-1 Voltage alarm
7 | L-L Average voltage alarm
8 | L1 Current alarm
9 | L2 Current alarm
10 | L3 Current alarm
11 | Average current alarm
12 | Neutral current alarm
13 | L1 active power alarm
14 | L2 active power alarm
15 | L3 active power alarm
16 | Total active power alarm
17 | L1 reactive power alarm
18 | L2 reactive power alarm
19 | L3 reactive power alarm
20 | Total reactive power alarm
21 | L1 apparent power alarm
22 | L2 apparent power alarm
23 | L3 apparent power alarm
24 | Total apparent power alarm
25 | L1 PF alarm
26 | L2 PF alarm
27 | L3 PF alarm
28 | Total PF alarm
29 | Frequency alarm
60 | Power on
61 | Power off
62 | CT2 change
63 | CT1 change
64 | PT2 change
65 | PT1 change
66 | Energy reset
67 | Demand info reset
99 | Null

## Input Register
Input Registers, Function code 04
Address (Register) | Input Register Parameter |  |  |  | Modbus Protocol Start Address(Hex) |  | 3Ø | 3Ø | 1Ø
| Description | Length （byte） | Data Format | Units | Hi byte | Lo byte | 4W | 3W | 2W
30001 | Phase 1 line to neutral volts | 4 | Float | V | 00 | 00 | ● | - | ●
30003 | Phase 2 line to neutral volts | 4 | Float | V | 00 | 02 | ● | - | -
30005 | Phase 3 line to neutral volts | 4 | Float | V | 00 | 04 | ● | - | -
30007 | Phase 1 current | 4 | Float | A | 00 | 06 | ● | ● | ●
30009 | Phase 2 current | 4 | Float | A | 00 | 08 | ● | ● | -
30011 | Phase 3 current | 4 | Float | A | 00 | 0A | ● | ● | -
30013 | Phase 1 active power | 4 | Float | W | 00 | 0C | ● | - | ●
30015 | Phase 2 active power | 4 | Float | W | 00 | 0E | ● | - | -
30017 | Phase 3 active power | 4 | Float | W | 00 | 10 | ● | - | -
30019 | Phase 1 apparent power | 4 | Float | VA | 00 | 12 | ● | - | ●
30021 | Phase 2 apparent power | 4 | Float | VA | 00 | 14 | ● | - | -
30023 | Phase 3 apparent power | 4 | Float | VA | 00 | 16 | ● | - | -
30025 | Phase 1 reactive power | 4 | Float | VAr | 00 | 18 | ● | - | ●
30027 | Phase 2 reactive power | 4 | Float | VAr | 00 | 1A | ● | - | -
30029 | Phase 3 reactive power | 4 | Float | VAr | 00 | 1C | ● | - | -
30031 | Phase 1 power factor (1) | 4 | Float | None | 00 | 1E | ● | - | ●
30033 | Phase 2 power factor (1) | 4 | Float | None | 00 | 20 | ● | - | -
30035 | Phase 3 power factor (1) | 4 | Float | None | 00 | 22 | ● | - | -
30037 | Phase 1 phase angle | 4 | Float | Degrees | 00 | 24 | ● | - | ●
30039 | Phase 2 phase angle | 4 | Float | Degrees | 00 | 26 | ● | - | -
30041 | Phase 3 phase angle | 4 | Float | Degrees | 00 | 28 | ● | - | -
30043 | Average line to neutral volts | 4 | Float | V | 00 | 2A | ● | - | -
30047 | Average line current | 4 | Float | A | 00 | 2E | ● | ● | ●
30049 | Sum of line currents | 4 | Float | A | 00 | 30 | ● | ● | ●
30053 | Total system power | 4 | Float | W | 00 | 34 | ● | ● | ●
30057 | Total system volt amps | 4 | Float | VA | 00 | 38 | ● | ● | ●
30061 | Total system Var | 4 | Float | VAr | 00 | 3C | ● | ● | ●
30063 | Total system power factor (1) | 4 | Float | None | 00 | 3E | ● | ● | ●
30067 | Total system phase angle | 4 | Float | Degrees | 00 | 42 | ● | ● | ●
30071 | Frequency of supply voltages | 4 | Float | Hz | 00 | 46 | ● | ● | ●
30073 | Import Wh since last reset | 4 | Float | kWh | 00 | 48 | ● | ● | ●
30075 | E-port Wh since last reset | 4 | Float | kWH | 00 | 4A | ● | ● | ●
30077 | Import VArh since last reset | 4 | Float | kVArh | 00 | 4C | ● | ● | ●
30079 | E-port VArh since last reset | 4 | Float | kVArh | 00 | 4E | ● | ● | ●
30081 | VAh since last reset | 4 | Float | kVAh | 00 | 50 | ● | ● | ●
30083 | Ah since last reset | 4 | Float | Ah | 00 | 52 | ● | ● | ●
30085 | Total system power demand (2) | 4 | Float | W | 00 | 54 | ● | ● | ●
30087 | Ma-imum total system power demand (2) | 4 | Float | W | 00 | 56 | ● | ● | ●
30089 | Import active power demand | 4 | Float | W | 00 | 58 | ● | ● | ●
30091 | Import active power ma-. demand | 4 | Float | W | 00 | 5A | ● | ● | ●
30093 | E-port active power demand | 4 | Float | W | 00 | 5C | ● | ● | ●
30095 | E-port active power ma-. demand | 4 | Float | W | 00 | 5E | ● | ● | ●
30101 | Total system VA demand | 4 | Float | VA | 00 | 64 | ● | ● | ●
30103 | Ma-imum total system VA demand | 4 | Float | VA | 00 | 66 | ● | ● | ●
30105 | Neutral current demand | 4 | Float | Amps | 00 | 68 | ● | - | -
30107 | Ma-imum neutral current demand | 4 | Float | Amps | 00 | 6A | ● | - | -
30109 | Total system reactive power demand(2) | 4 | Float | VAr | 00 | 6C | ● | - | ●
30111 | Ma-imum total system reactive power demand(2) | 4 | Float | VAr | 00 | 6E | ● | - | ●
30161 | Voltage phase sequence（normal=1、reverse=2） | 4 | Float | None | 00 | A0 | ● | ● | -
30163 | Current phase sequence（normal=1、reverse=2） | 4 | Float | None | 00 | A2 | ● | ● | -
30193 | Nature of the load（Resistive =1、inductive=2、capacitive =3） | 4 | Float | None | 00 | C0 | ● | ● | ●
30195 | Nature of L1 load（Resistive=1、inductive=2、capacitive =3） | 4 | Float | None | 00 | C2 | ● | ● | ●
30197 | Nature of L2 load（Resistive =1、inductive=2、capacitive =3） | 4 | Float | None | 00 | C4 | ● | ● | -
30199 | Nature of L3 load（Resistive =1、inductive=2、capacitive =3） | 4 | Float | None | 00 | C6 | ● | ● | -
30201 | Line 1 to Line 2 volts | 4 | Float | V | 00 | C8 | ● | ● | -
30203 | Line 2 to Line 3 volts | 4 | Float | V | 00 | CA | ● | ● | -
30205 | Line 3 to Line 1 volts | 4 | Float | V | 00 | CC | ● | ● | -
30207 | Average line to line volts | 4 | Float | V | 00 | CE | ● | ● | -
30225 | Neutral current | 4 | Float | A | 00 | E0 | ● | - | -
30235 | Phase 1 L/N volts THD | 4 | Float | % | 00 | EA | ● | - | ●
30237 | Phase 2 L/N volts THD | 4 | Float | % | 00 | EC | ● | - | -
30239 | Phase 3 L/N volts THD | 4 | Float | % | 00 | EE | ● | - | -
30241 | Phase 1 Current THD | 4 | Float | % | 00 | F0 | ● | ● | ●
30243 | Phase 2 Current THD | 4 | Float | % | 00 | F2 | ● | ● | -
30245 | Phase 3 Current THD | 4 | Float | % | 00 | F4 | ● | ● | -
30249 | Average line to neutral volts THD | 4 | Float | % | 00 | F8 | ● | - | ●
30251 | Average line current THD | 4 | Float | % | 00 | FA | ● | ● | ●
30259 | Phase 1 current demand | 4 | Float | A | 01 | 02 | ● | ● | ●
30261 | Phase 2 current demand | 4 | Float | A | 01 | 04 | ● | ● | -
30263 | Phase 3 current demand | 4 | Float | A | 01 | 06 | ● | ● | -
30265 | Ma-imum phase 1 current demand | 4 | Float | A | 01 | 08 | ● | ● | ●
30267 | Ma-imum phase 2 current demand | 4 | Float | A | 01 | 0A | ● | ● | -
30269 | Ma-imum phase 3 current demand | 4 | Float | A | 01 | 0C | ● | ● | -
30335 | Line 1 to line 2 volts THD | 4 | Float | ％ | 01 | 4E | ● | ● | -
30337 | Line 2 to line 3 volts THD | 4 | Float | ％ | 01 | 50 | ● | ● | -
30339 | Line 3 to line 1 volts THD | 4 | Float | ％ | 01 | 52 | ● | ● | -
30341 | Average line to line volts THD | 4 | Float | ％ | 01 | 54 | ● | ● | -
30343 | Total kwh(3) | 4 | Float | kWh | 01 | 56 | ● | ● | ●
30345 | Total kvarh(3) | 4 | Float | kVArh | 01 | 58 | ● | ● | ●
30347 | L1 import kwh | 4 | Float | kWh | 01 | 5A | ● | ● | ●
30349 | L2 import kwh | 4 | Float | kWh | 01 | 5C | ● | ● | -
30351 | L3 import kWh | 4 | Float | kWh | 01 | 5E | ● | ● | -
30353 | L1 e-port kWh | 4 | Float | kWh | 01 | 60 | ● | ● | ●
30355 | L2 e-port kwh | 4 | Float | kWh | 01 | 62 | ● | ● | -
30357 | L3 e-port kWh | 4 | Float | kWh | 01 | 64 | ● | ● | -
30359 | L1 total kwh | 4 | Float | kWh | 01 | 66 | ● | ● | ●
30361 | L2 total kWh | 4 | Float | kWh | 01 | 68 | ● | ● | -
30363 | L3 total kwh | 4 | Float | kWh | 01 | 6A | ● | ● | -
30365 | L1 import kvarh | 4 | Float | kVArh | 01 | 6C | ● | ● | ●
30367 | L2 import kvarh | 4 | Float | kVArh | 01 | 6E | ● | ● | -
30369 | L3 import kvarh | 4 | Float | kVArh | 01 | 70 | ● | ● | -
30371 | L1 e-port kvarh | 4 | Float | kVArh | 01 | 72 | ● | ● | ●
30373 | L2 e-port kvarh | 4 | Float | kVArh | 01 | 74 | ● | ● | -
30375 | L3 e-port kvarh | 4 | Float | kVArh | 01 | 76 | ● | ● | -
30377 | L1 total kvarh | 4 | Float | kVArh | 01 | 78 | ● | ● | ●
30379 | L2 total kvarh | 4 | Float | kVArh | 01 | 7A | ● | ● | -
30381 | L3 total kvarh | 4 | Float | kVArh | 01 | 7C | ● | ● | -
30403 | Voltage 2st~63st Harmonic L1 | 248 | Float | % | 01 | 92 | ● | ● | ●
30527 | Voltage 2st~63st Harmonic L2 | 248 | Float | % | 02 | 0E | ● | ● | -
30651 | Voltage 2st~63st Harmonic L3 | 248 | Float | % | 02 | 8A | ● | ● | -
30775 | Current 2st~63st Harmonic L1 | 248 | Float | % | 03 | 06 | ● | ● | ●
30899 | Current 2st~63st Harmonic L2 | 248 | Float | % | 03 | 82 | ● | ● | -
31023 | Current 2st~63st Harmonic L3 | 248 | Float | % | 03 | FE | ● | ● | -
31147 | Voltage Total Harmonic L1 | 4 | Float | % | 04 | 7A | ● | ● | ●
31149 | Voltage Total Harmonic L2 | 4 | Float | % | 04 | 7C | ● | ● | -
31151 | Voltage Total Harmonic L3 | 4 | Float | % | 04 | 7E | ● | ● | -
31153 | Current Total Harmonic L1 | 4 | Float | % | 04 | 80 | ● | ● | ●
31155 | Current Total Harmonic L2 | 4 | Float | % | 04 | 82 | ● | ● | -
31157 | Current Total Harmonic L3 | 4 | Float | % | 04 | 84 | ● | ● | -
Notes:
1. The power factor has its sign adjusted to indicate the direction of the current. Positive refers to forward current, negative refers to reverse current.
2. The power sum demand calculation is for import – export.
3.Total kWh / kVarh equals to Import + export.

## Input Status
Input Status, Function code 02
Address Register | Parameter | Modbus Protocol Start Address(Hex) |  | Valid Range | Mode
|  | Hi Byte | Lo Byte
10001 | DI-1 status | 00 | 00 | DI-1 status, 1=ON, 0=OFF Length : 1 bit Data Format :Binary | ro
10002 | DI-2 status | 00 | 01 | DI-2 status, 1=ON, 0=OFF Length : 1 bit Data Format :Binary | ro
10003 | DI-3 status | 00 | 02 | DI-3 status, 1=ON, 0=OFF Length : 1 bit Data Format :Binary | ro
10004 | DI-4 status | 00 | 03 | DI-4 status, 1=ON, 0=OFF Length : 1 bit Data Format :Binary | ro

## Coll Status
Coll Status, Function code 01
Address Register | Parameter | Modbus Protocol Start Address(Hex) |  | Valid Range | Mode
|  | Hi Byte | Lo Byte
00001 | DO-1 status | 00 | 00 | DO-1 status, 1=ON, 0=OFF Length : 1 bit Data Format :Binary | rw
00002 | DO-2 status | 00 | 01 | DO-2 status, 1=ON, 0=OFF Length : 1 bit Data Format :Binary | rw
Coll Status, Function code 05
Address Register | Parameter | Modbus Protocol Start Address(Hex) |  | Valid Range | Mode
|  | Hi Byte | Lo Byte
00001 | Control DO-1 | 00 | 00 | 0xFF00=ON, 0x0000=OFF Length :2 byte Data Format: Hex | rw
00002 | Control DO-2 | 00 | 01 | 0xFF00=ON, 0x0000=OFF Length :2 byte Data Format: Hex | rw