## Tabelle1
Address list
Frequently required readings
Address | Format | RD/WR | Designation | Unit | Note
19000 | float | RD | _G_ULN[0] | V | Voltage L1-N
19002 | float | RD | _G_ULN[1] | V | Voltage L2-N
19004 | float | RD | _G_ULN[2] | V | Voltage L3-N
19006 | float | RD | _G_ULL[0] | V | Voltage L1-L2
19008 | float | RD | _G_ULL[1] | V | Voltage L2-L3
19010 | float | RD | _G_ULL[2] | V | Voltage L3-L1
19012 | float | RD | _G_ILN[0] | A | Apparent current, L1-N
19014 | float | RD | _G_ILN[1] | A | Apparent current, L2-N
19016 | float | RD | _G_ILN[2] | A | Apparent current, L3-N
19018 | float | RD | _G_I_SUM3 | A | Vector sum; IN=I1+I2+I3
19020 | float | RD | _G_PLN[0] | W | Real power L1-N
19022 | float | RD | _G_PLN[1] | W | Real power L2-N
19024 | float | RD | _G_PLN[2] | W | Real power L3-N
19026 | float | RD | _G_P_SUM3 | W | Psum3=P1+P2+P3
19028 | float | RD | _G_SLN[0] | VA | Apparent power L1-N
19030 | float | RD | _G_SLN[1] | VA | Apparent power L2-N
19032 | float | RD | _G_SLN[2] | VA | Apparent power L3-N
19034 | float | RD | _G_S_SUM3 | VA | Sum; Ssum3=S1+S2+S3
19036 | float | RD | _G_QLN[0] | var | Reactive power L1 (fundamental comp.)
19038 | float | RD | _G_QLN[1] | var | Reactive power L2 (fundamental comp.)
19040 | float | RD | _G_QLN[2] | var | Reactive power L3 (fundamental comp.)
19042 | float | RD | _G_Q_SUM3 | var | Qsum3=Q1+Q2+Q3 (fundamental comp.)
19044 | float | RD | _G_COS_PHI[0] | - | CosPhi; UL1 IL1 (fundamental comp.)
19046 | float | RD | _G_COS_PHI[1] | - | CosPhi; UL2 IL2 (fundamental comp.)
19048 | float | RD | _G_COS_PHI[2] | - | CosPhi; UL3 IL3 (fundamental comp.)
19050 | float | RD | _G_FREQ | Hz | Measured frequency
19052 | float | RD | _G_PHASE_SEQ | - | Rotation field; 1=right, 0=none, -1=left
19054 | float | RD | _G_WH[0] | Wh | Real energy L1
19056 | float | RD | _G_WH[1] | Wh | Real energy L2
19058 | float | RD | _G_WH[2] | Wh | Real energy L3
19060 | float | RD | _G_WH_SUML13 | Wh | Real energy L1..L3
19062 | float | RD | _G_WH_V[0] | Wh | Real energy L1, consumed
19064 | float | RD | _G_WH_V[1] | Wh | Real energy L2, consumed
19066 | float | RD | _G_WH_V[2] | Wh | Real energy L3, consumed
19068 | float | RD | _G_WH_V_HT_SUML13 | Wh | Real energy L1..L3, consumed, rate 1
19070 | float | RD | _G_WH_Z[0] | Wh | Real energy L1, delivered
19072 | float | RD | _G_WH_Z[1] | Wh | Real energy L2, delivered
19074 | float | RD | _G_WH_Z[2] | Wh | Real energy L3, delivered
19076 | float | RD | _G_WH_Z_SUML13 | Wh | Real energy L1..L3, delivered
19078 | float | RD | _G_WH_S[0] | VAh | Apparent energy L1
19080 | float | RD | _G_WH_S[1] | VAh | Apparent energy L2
19082 | float | RD | _G_WH_S[2] | VAh | Apparent energy L3
19084 | float | RD | _G_WH_S_SUML13 | VAh | Apparent energy L1..L3
19086 | float | RD | _G_QH[0] | varh | Reaktive energy L1 (fundamental comp.)
19088 | float | RD | _G_QH[1] | varh | Reaktive energy L2 (fundamental comp.)
19090 | float | RD | _G_QH[2] | varh | Reaktive energy L3 (fundamental comp.)
19092 | float | RD | _G_QH_SUML13 | varh | Reaktive energy L1..L3 (fundamental comp.)
19094 | float | RD | _G_IQH[0] | varh | Reactive energy, inductive, L1 (fundamental comp.)
19096 | float | RD | _G_IQH[1] | varh | Reactive energy, inductive, L2 (fundamental comp.)
19098 | float | RD | _G_IQH[2] | varh | Reactive energy, inductive, L3 (fundamental comp.)
19100 | float | RD | _G_IQH_SUML13 | varh | Reactive energy L1..L3, ind. (fundamental comp.)
19102 | float | RD | _G_CQH[0] | varh | Reactive energy, capacitive, L1 (fundamental comp.)
19104 | float | RD | _G_CQH[1] | varh | Reactive energy, capacitive, L2 (fundamental comp.)
19106 | float | RD | _G_CQH[2] | varh | Reactive energy, capacitive, L3 (fundamental comp.)
19108 | float | RD | _G_CQH_SUML13 | varh | Reactive energy L1..L3, cap. (fundamental comp.)
19110 | float | RD | _G_THD_ULN[0] | % | Harmonic, THD,U L1-N
19112 | float | RD | _G_THD_ULN[1] | % | Harmonic, THD,U L2-N
19114 | float | RD | _G_THD_ULN[2] | % | Harmonic, THD,U L3-N
19116 | float | RD | _G_THD_ILN[0] | % | Harmonic, THD,I L1
19118 | float | RD | _G_THD_ILN[1] | % | Harmonic, THD,I L2
19120 | float | RD | _G_THD_ILN[2] | % | Harmonic, THD,I L3
Date and time
Address | Format | RD/WR | Designation | Unit | Note
0 | long64 | RD | _REALTIME | 2 ns | time (UTC)
4 | int | RD/WR | _SYSTIME | sec | time (UTC)
6 | short | RD | _DAY | - | Day (1..31)
7 | short | RD | _MONTH | - | Month (0=Jan, .. 11=Dec)
8 | short | RD | _YEAR | - | Year
9 | short | RD | _HOUR | h | Hour (1..24)
10 | short | RD | _MIN | min | Minute (1..59)
11 | short | RD | _SEC | s | Second (1..59)
12 | short | RD | _WEEKDAY | - | Weekday (0=Sun, .. 6=Sat)
Measured values (200ms measuring window)
Address | Format | RD/WR | Designation | Unit | Note
3793 | float | RD | _THD_ULL[0] | % | Harmonic, THD,U L1-L2
3795 | float | RD | _THD_ULL[1] | % | Harmonic, THD,U L2-L3
3797 | float | RD | _THD_ULL[2] | % | Harmonic, THD,U L1-L3
3799 | float | RD | _ZHD_ULL[0] | % | Interharmonics, U L1-L2
3801 | float | RD | _ZHD_ULL[1] | % | Interharmonics, U L2-L3
3803 | float | RD | _ZHD_ULL[2] | % | Interharmonics, U L1-L3
3805 | float | RD | _THD_ULN[0] | % | Harmonic, THD,U L1-N
3807 | float | RD | _THD_ULN[1] | % | Harmonic, THD,U L2-N
3809 | float | RD | _THD_ULN[2] | % | Harmonic, THD,U L3-N
3811 | float | RD | _THD_ULN[3] | % | Harmonic, THD,U L4-N
3813 | float | RD | _THD_IL[0] | % | Harmonic, THD,I1 L1
3815 | float | RD | _THD_IL[1] | % | Harmonic, THD,I2 L2
3817 | float | RD | _THD_IL[2] | % | Harmonic, THD,I3 L3
3819 | float | RD | _THD_IL[3] | % | Harmonic, THD,I4 L4
3821 | float | RD | _ZHD_ULN[0] | % | Interharmonics, ZHD, U, L1
3823 | float | RD | _ZHD_ULN[1] | % | Interharmonics, ZHD, U, L2
3825 | float | RD | _ZHD_ULN[2] | % | Interharmonics, ZHD, U, L3
3827 | float | RD | _ZHD_ULN[3] | % | Interharmonics, ZHD, U, L4
3829 | float | RD | _ZHD_ILN[0] | % | Interharmonics, ZHD, I, L1
3831 | float | RD | _ZHD_ILN[1] | % | Interharmonics, ZHD, I, L2
3833 | float | RD | _ZHD_ILN[2] | % | Interharmonics, ZHD, I, L3
3835 | float | RD | _ZHD_ILN[3] | % | Interharmonics, ZHD, I, L4
3837 | float | RD | _KFACT[0] |  | K-Factor, L1
3839 | float | RD | _KFACT[1] |  | K-Factor, L2
3841 | float | RD | _KFACT[2] |  | K-Factor, L3
3843 | float | RD | _KFACT[3] |  | K-Factor, L4
3845 | float | RD | _ULN[0] | V | Voltage L1-N
3847 | float | RD | _ULN[1] | V | Voltage L2-N
3849 | float | RD | _ULN[2] | V | Voltage L3-N
3851 | float | RD | _ULN[3] | V | Voltage L4-N
3853 | float | RD | _ILN[0] | A | Apparent current, L1
3855 | float | RD | _ILN[1] | A | Apparent current, L2
3857 | float | RD | _ILN[2] | A | Apparent current, L3
3859 | float | RD | _ILN[3] | A | Apparent current, L4
3861 | float | RD | _PLN[0] | W | Real power L1
3863 | float | RD | _PLN[1] | W | Real power L2
3865 | float | RD | _PLN[2] | W | Real power L3
3867 | float | RD | _PLN[3] | W | Real power L4
3869 | float | RD | _QLN[0] | var | Reactive power L1 (fundamental comp.)
3871 | float | RD | _QLN[1] | var | Reactive power L2 (fundamental comp.)
3873 | float | RD | _QLN[2] | var | Reactive power L3 (fundamental comp.)
3875 | float | RD | _QLN[3] | var | Reactive power L4 (fundamental comp.)
3877 | float | RD | _SLN[0] | VA | Apparent power L1
3879 | float | RD | _SLN[1] | VA | Apparent power L2
3881 | float | RD | _SLN[2] | VA | Apparent power L3
3883 | float | RD | _SLN[3] | VA | Apparent power L4
3885 | float | RD | _DLN[0] | var | Distortion power factor; L1
3887 | float | RD | _DLN[1] | var | Distortion power factor; L2
3889 | float | RD | _DLN[2] | var | Distortion power factor; L3
3891 | float | RD | _DLN[3] | var | Distortion power factor; L4
3893 | float | RD | _PFLN[0] |  | Power factor; L1
3895 | float | RD | _PFLN[1] |  | Power factor; L2
3897 | float | RD | _PFLN[2] |  | Power factor; L3
3899 | float | RD | _PFLN[3] |  | Power factor; L4
3901 | float | RD | _ULL[0] | V | Phase conductor voltage; L1-L2
3903 | float | RD | _ULL[1] | V | Phase conductor voltage; L2-L3
3905 | float | RD | _ULL[2] | V | Phase conductor voltage; L1-L3
3907 | float | RD | _ULL_RE[0] | V | Phase conductor voltage real part; L1-L2
3909 | float | RD | _ULL_RE[1] | V | Phase conductor voltage real part; L2-L3
3911 | float | RD | _ULL_RE[2] | V | Phase conductor voltage real part; L1-L3
3913 | float | RD | _ULL_IM[0] | V | Phase conductor voltage imaginary part; L1-L2
3915 | float | RD | _ULL_IM[1] | V | Phase conductor voltage imaginary part; L2-L3
3917 | float | RD | _ULL_IM[2] | V | Phase conductor voltage imaginary part; L1-L3
3919 | float | RD | _I_SUM3 | A | Vector sum; IN = I1 + I2 + I3
3921 | float | RD | _I_SUM | A | Vector sum; I1 + I2 + I3 + I4
3923 | float | RD | _S_SUM3 | VA | Sum; S = S1 + S2 + S3
3925 | float | RD | _P_SUM3 | W | Sum; P = P1 + P2 + P3
3927 | float | RD | _Q_SUM3 | var | Mains frequency reactive power
Sum; Q = Q1 + Q2 + Q3
3929 | float | RD | _COS_SUM3 |  | CosPhi of mains frequency
Calculated from Psum3 and Qsum3
3931 | float | RD | _S_SUM | VA | Sum; S = S1 + S2 + S3 + S4
3933 | float | RD | _P_SUM | W | Sum; P = P1 + P2 + P3 + P4
3935 | float | RD | _Q_SUM | var | Mains frequency reactive power
Sum; Q = Q1 + Q2 + Q3 + Q4
3937 | float | RD | _COS_SUM |  | CosPhi of mains frequency
Calculated from Psum and Qsum
3939 | float | RD | _ULN_RE[0] | V | Voltage, real part, L1-N
3941 | float | RD | _ULN_RE[1] | V | Voltage, real part, L2-N
3943 | float | RD | _ULN_RE[2] | V | Voltage, real part, L3-N
3945 | float | RD | _ULN_RE[3] | V | Voltage, real part, L4-N
3947 | float | RD | _ULN_IM[0] | V | Voltage, imaginary part, L1-N
3949 | float | RD | _ULN_IM[1] | V | Voltage, imaginary part, L2-N
3951 | float | RD | _ULN_IM[2] | V | Voltage, imaginary part, L3-N
3953 | float | RD | _ULN_IM[3] | V | Voltage, imaginary part, L4-N
3955 | float | RD | _IL_RE[0] | A | Current, real part, L1
3957 | float | RD | _IL_RE[1] | A | Current, real part, L2
3959 | float | RD | _IL_RE[2] | A | Current, real part, L3
3961 | float | RD | _IL_RE[3] | A | Current, real part, L4
3963 | float | RD | _IL_IM[0] | A | Current, imaginary part, L1
3965 | float | RD | _IL_IM[1] | A | Current, imaginary part, L2
3967 | float | RD | _IL_IM[2] | A | Current, imaginary part, L3
3969 | float | RD | _IL_IM[3] | A | Current, imaginary part, L4
3971 | float | RD | _PHASE[0] | ° | Phase; UL1 IL1
3973 | float | RD | _PHASE[1] | ° | Phase; UL2 IL2
3975 | float | RD | _PHASE[2] | ° | Phase; UL3 IL3
3977 | float | RD | _PHASE[3] | ° | Phase; UL4 IL4
3979 | float | RD | _COS_PHI[0] |  | Fund. power factor, CosPhi; UL1 IL1
3981 | float | RD | _COS_PHI[1] |  | Fund. power factor, CosPhi; UL2 IL2
3983 | float | RD | _COS_PHI[2] |  | Fund. power factor, CosPhi; UL3 IL3
3985 | float | RD | _COS_PHI[3] |  | Fund. power factor, CosPhi; UL4 IL4
3987 | float | RD | _IND_CAP[0] |  | Sign; Q L1, +1 = ind., -1 = cap.
3989 | float | RD | _IND_CAP[1] |  | Sign; Q L2, +1 = ind., -1 = cap.
3991 | float | RD | _IND_CAP[2] |  | Sign; Q L3, +1 = ind., -1 = cap.
3993 | float | RD | _IND_CAP[3] |  | Sign; Q L4, +1 = ind., -1 = cap.
3995 | float | RD | _FREQ | Hz | Measured frequency
3997 | float | RD | _NORM_FREQ | Hz | Nominal frequency
3999 | float | RD | _UN | V | Zero sequence, voltage
4001 | float | RD | _UM | V | Positive sequence, voltage
4003 | float | RD | _UG | V | Negative sequence, voltage
4005 | float | RD | _U_SYM | % | Unsymmetrical, voltage
4007 | float | RD | _I_SYM | % | Unsymmetrical, current
4009 | float | RD | _PHASE_SEQ |  | Rotation field; 1=right, 0=none, -1=left
4011 | float | RD | _IN | A | Zero sequence, current
4013 | float | RD | _IM | A | Positive sequence, current
4015 | float | RD | _IG | A | Negative sequence, current
4021 | float | RD | _IL_CF[0] |  | Crest factor, I L1
4023 | float | RD | _IL_CF[1] |  | Crest factor, I L2
4025 | float | RD | _IL_CF[2] |  | Crest factor, I L3
4027 | float | RD | _IL_CF[3] |  | Crest factor, I L4
4029 | float | RD | _ULN_CF[0] |  | Crest factor, U L1-N
4031 | float | RD | _ULN_CF[1] |  | Crest factor, U L2-N
4033 | float | RD | _ULN_CF[2] |  | Crest factor, U L3-N
4035 | float | RD | _ULN_CF[3] |  | Crest factor, U L4-N
4037 | float | RD | _ULL_CF[0] |  | Crest factor, U L1-L2
4039 | float | RD | _ULL_CF[1] |  | Crest factor, U L2-L3
4041 | float | RD | _ULL_CF[2] |  | Crest factor, U L1-L3
4043 | float | RD | _IL_NEG_PEAK[0] | A | Peak value negative, I L1
4045 | float | RD | _IL_NEG_PEAK[1] | A | Peak value negative, I L2
4047 | float | RD | _IL_NEG_PEAK[2] | A | Peak value negative, I L3
4049 | float | RD | _IL_NEG_PEAK[3] | A | Peak value negative, I L4
4051 | float | RD | _ULN_NEG_PEAK[0] | V | Peak value negative, U L1-N
4053 | float | RD | _ULN_NEG_PEAK[1] | V | Peak value negative, U L2-N
4055 | float | RD | _ULN_NEG_PEAK[2] | V | Peak value negative, U L3-N
4057 | float | RD | _ULN_NEG_PEAK[3] | V | Peak value negative, U L4-N
4059 | float | RD | _IL_POS_PEAK[0] | A | Peak value positive, I L1
4061 | float | RD | _IL_POS_PEAK[1] | A | Peak value positive, I L2
4063 | float | RD | _IL_POS_PEAK[2] | A | Peak value positive, I L3
4065 | float | RD | _IL_POS_PEAK[3] | A | Peak value positive, I L4
4067 | float | RD | _ULN_POS_PEAK[0] | V | Peak value positive, U L1-N
4069 | float | RD | _ULN_POS_PEAK[1] | V | Peak value positive, U L2-N
4071 | float | RD | _ULN_POS_PEAK[2] | V | Peak value positive, U L3-N
4073 | float | RD | _ULN_POS_PEAK[3] | V | Peak value positive, U L4-N
4075 | float | RD | _IL_PEAK_PEAK[0] | A | Peak-peak value, I L1
4077 | float | RD | _IL_PEAK_PEAK[1] | A | Peak-peak value, I L2
4079 | float | RD | _IL_PEAK_PEAK[2] | A | Peak-peak value, I L3
4081 | float | RD | _IL_PEAK_PEAK[3] | A | Peak-peak value, I L4
4083 | float | RD | _ULN_PEAK_PEAK[0] | V | Peak-peak value, U L1-N
4085 | float | RD | _ULN_PEAK_PEAK[1] | V | Peak-peak value, U L2-N
4087 | float | RD | _ULN_PEAK_PEAK[2] | V | Peak-peak value, U L3-N
4089 | float | RD | _ULN_PEAK_PEAK[3] | V | Peak-peak value, U L4-N
4091 | float | RD | _IL_UNDER[0] | % | Under difference, I L1
4093 | float | RD | _IL_UNDER[1] | % | Under difference, I L2
4095 | float | RD | _IL_UNDER[2] | % | Under difference, I L3
4097 | float | RD | _IL_UNDER[3] | % | Under difference, I L4
4099 | float | RD | _ULN_UNDER[0] | % | Under difference, U L1 (61000-4-30)
4101 | float | RD | _ULN_UNDER[1] | % | Under difference, U L2 (61000-4-30)
4103 | float | RD | _ULN_UNDER[2] | % | Under difference, U L3 (61000-4-30)
4105 | float | RD | _ULN_UNDER[3] | % | Under difference, U L4 (61000-4-30)
4107 | float | RD | _IL_OVER[0] | % | Over difference, I L1
4109 | float | RD | _IL_OVER[1] | % | Over difference, I L2
4111 | float | RD | _IL_OVER[2] | % | Over difference, I L3
4113 | float | RD | _IL_OVER[3] | % | Over difference, I L4
4115 | float | RD | _ULN_OVER[0] | % | Over difference, U L1 (61000-4-30)
4117 | float | RD | _ULN_OVER[1] | % | Over difference, U L2 (61000-4-30)
4119 | float | RD | _ULN_OVER[2] | % | Over difference, U L3 (61000-4-30)
4121 | float | RD | _ULN_OVER[3] | % | Over difference, U L4 (61000-4-30)
4123 | float | RD | _ULL_NEG_PEAK[0] | V | Peak value negative, U L1-L2
4125 | float | RD | _ULL_NEG_PEAK[1] | V | Peak value negative, U L2-L3
4127 | float | RD | _ULL_NEG_PEAK[2] | V | Peak value negative, U L3-L1
4129 | float | RD | _ULL_POS_PEAK[0] | V | Peak value positive, U L1-L2
4131 | float | RD | _ULL_POS_PEAK[1] | V | Peak value positive, U L2-L3
4133 | float | RD | _ULL_POS_PEAK[2] | V | Peak value positive, U L3-L1
4135 | float | RD | _ULL_PEAK_PEAK[0] | V | Peak-peak value, U L1-L2
4137 | float | RD | _ULL_PEAK_PEAK[1] | V | Peak-peak value, U L2-L3
4139 | float | RD | _ULL_PEAK_PEAK[2] | V | Peak-peak value, U L3-L1
4141 | float | RD | _ULL_UNDER[0] | % | Under difference, U L1-L2 (61000-4-30)
4143 | float | RD | _ULL_UNDER[1] | % | Under difference, U L2-L3 (61000-4-30)
4145 | float | RD | _ULL_UNDER[2] | % | Under difference, U L3-L1 (61000-4-30)
4147 | float | RD | _ULL_OVER[0] | % | Over difference, U L1-L2 (61000-4-30)
4149 | float | RD | _ULL_OVER[1] | % | Over difference, U L2-L3 (61000-4-30)
4151 | float | RD | _ULL_OVER[2] | % | Over difference, U L3-L1 (61000-4-30)
4153 | float | RD | _FLI_PF5[0] |  | Current flicker Pf5, L1-N
4155 | float | RD | _FLI_PF5[1] |  | Current flicker Pf5, L2-N
4157 | float | RD | _FLI_PF5[2] |  | Current flicker Pf5, L3-N
4159 | float | RD | _FLI_PF5[3] |  | Current flicker Pf5, L4-N
4161 | float | RD | _FLI_SHORT_TERM[0] |  | Short-term flicker level, Pst (10m), L1-N
4163 | float | RD | _FLI_SHORT_TERM[1] |  | Short-term flicker level, Pst (10m), L2-N
4165 | float | RD | _FLI_SHORT_TERM[2] |  | Short-term flicker level, Pst (10m), L3-N
4167 | float | RD | _FLI_SHORT_TERM[3] |  | Short-term flicker level, Pst (10m), L4-N
4169 | float | RD | _FLI_LONG_TERM[0] |  | Long-term flicker level, Plt (2h), L1-N
4171 | float | RD | _FLI_LONG_TERM[1] |  | Long-term flicker level, Plt (2h), L2-N
4173 | float | RD | _FLI_LONG_TERM[2] |  | Long-term flicker level, Plt (2h), L3-N
4175 | float | RD | _FLI_LONG_TERM[3] |  | Long-term flicker level, Plt (2h), L4-N
4177 | float | RD | _URC[0] | V | Ripple control signal, U L1-N (61000-4-30)
4179 | float | RD | _URC[1] | V | Ripple control signal, U L2-N (61000-4-30)
4181 | float | RD | _URC[2] | V | Ripple control signal, U L3-N (61000-4-30)
4183 | float | RD | _URC[3] | V | Ripple control signal, U L4-N (61000-4-30)
4185 | float | RD | _IRC[0] | A | Ripple control signal, I L1
4187 | float | RD | _IRC[1] | A | Ripple control signal, I L2
4189 | float | RD | _IRC[2] | A | Ripple control signal, I L3
4191 | float | RD | _IRC[3] | A | Ripple control signal, I L4
4193 | float | RD | _ULL_RC[0] | V | Ripple control signal, U L1-L2, (61000-4-30)
4195 | float | RD | _ULL_RC[1] | V | Ripple control signal, U L2-L3, (61000-4-30)
4197 | float | RD | _ULL_RC[2] | V | Ripple control signal, U L3-L1, (61000-4-30)
4209 | float | RD | _TEMPERATUR | °C | Internal temperature
13097 | float | RD/WR | _IRATED_TDD[0] | A | Maximum demand load current, L1..L3
13099 | float | RD/WR | _IRATED_TDD[1] | A | Maximum demand load current, L4
13101 | float | RD | _TDD_IL[0] | % | TDD, total demand distortion, IL1
13103 | float | RD | _TDD_IL[1] | % | TDD, total demand distortion, IL2
13105 | float | RD | _TDD_IL[2] | % | TDD, total demand distortion, IL3
13107 | float | RD | _TDD_IL[3] | % | TDD, total demand distortion, IL4
13109 | float | RD | _U_SYM_U0 | % | Unsymmetrical, voltage U0
19122 | float | RD | _IND_CAP_SUM3 | - | Sign, Q1 + Q2 + Q3
19124 | float | RD | _IND_CAP_SUM | - | Sign, Q1 + Q2 + Q3 + Q4
Mean values (float type)
Address | Format | RD/WR | Designation | Unit | Note
4211 | float | RD/WR | _ULN_AVG[0] | V | Mean value, voltage U L1-N
4213 | float | RD/WR | _ULN_AVG[1] | V | Mean value, voltage U L2-N
4215 | float | RD/WR | _ULN_AVG[2] | V | Mean value, voltage U L3-N
4217 | float | RD/WR | _ULN_AVG[3] | V | Mean value, voltage U L4-N
4219 | float | RD/WR | _ULL_AVG[0] | V | Mean value, voltage U L1-L2
4221 | float | RD/WR | _ULL_AVG[1] | V | Mean value, voltage U L2-L3
4223 | float | RD/WR | _ULL_AVG[2] | V | Mean value, voltage U L3-L1
4225 | float | RD/WR | _ULN_CF_AVG[0] |  | Mean value, crest factor of the Voltage U L1-N
4227 | float | RD/WR | _ULN_CF_AVG[1] |  | Mean value, crest factor of the Voltage U L2-N
4229 | float | RD/WR | _ULN_CF_AVG[2] |  | Mean value, crest factor of the Voltage U L3-N
4231 | float | RD/WR | _ULN_CF_AVG[3] |  | Mean value, crest factor of the Voltage U L4-N
4233 | float | RD/WR | _ULL_CF_AVG[0] |  | Mean value, crest factor of the Voltage U L1-L2
4235 | float | RD/WR | _ULL_CF_AVG[1] |  | Mean value, crest factor of the Voltage U L2-L3
4237 | float | RD/WR | _ULL_CF_AVG[2] |  | Mean value, crest factor of the Voltage U L3-L1
4239 | float | RD/WR | _UN_AVG | V | Mean value, zero sequence
4241 | float | RD/WR | _UM_AVG | V | Mean value, positive sequence
4243 | float | RD/WR | _UG_AVG | V | Mean value, negative sequence
4245 | float | RD/WR | _THD_ULN_AVG[0] | % | Mean value, harmonic, THD,U L1-N
4247 | float | RD/WR | _THD_ULN_AVG[1] | % | Mean value, harmonic, THD,U L2-N
4249 | float | RD/WR | _THD_ULN_AVG[2] | % | Mean value, harmonic, THD,U L3-N
4251 | float | RD/WR | _THD_ULN_AVG[3] | % | Mean value, harmonic, THD,U L4-N
4253 | float | RD/WR | _THD_ZLN_AVG[0] | % | Mean value, interharmonics, ZHD, U, L1
4255 | float | RD/WR | _THD_ZLN_AVG[1] | % | Mean value, interharmonics, ZHD, U, L2
4257 | float | RD/WR | _THD_ZLN_AVG[2] | % | Mean value, interharmonics, ZHD, U, L3
4259 | float | RD/WR | _THD_ZLN_AVG[3] | % | Mean value, interharmonics, ZHD, U, L4
4261 | float | RD/WR | _ULN_OVER_AVG[0] | % | Mean value, over difference, U L1 (61000-4-30)
4263 | float | RD/WR | _ULN_OVER_AVG[1] | % | Mean value, over difference, U L2 (61000-4-30)
4265 | float | RD/WR | _ULN_OVER_AVG[2] | % | Mean value, over difference, U L3 (61000-4-30)
4267 | float | RD/WR | _ULN_OVER_AVG[3] | % | Mean value, over difference, U L4 (61000-4-30)
4269 | float | RD/WR | _ULN_UNDER_AVG[0] | % | Mean value, under difference, U L1 (61000-4-30)
4271 | float | RD/WR | _ULN_UNDER_AVG[1] | % | Mean value, under difference, U L1 (61000-4-30)
4273 | float | RD/WR | _ULN_UNDER_AVG[2] | % | Mean value, under difference, U L1 (61000-4-30)
4275 | float | RD/WR | _ULN_UNDER_AVG[3] | % | Mean value, under difference, U L1 (61000-4-30)
4277 | float | RD/WR | _ULN_NEG_PEAK_AVG[0] | V | Mean value, peak value negative, U L1-N
4279 | float | RD/WR | _ULN_NEG_PEAK_AVG[1] | V | Mean value, peak value negative, U L2-N
4281 | float | RD/WR | _ULN_NEG_PEAK_AVG[2] | V | Mean value, peak value negative, U L3-N
4283 | float | RD/WR | _ULN_NEG_PEAK_AVG[3] | V | Mean value, peak value negative, U L4-N
4285 | float | RD/WR | _ULN_POS_PEAK_AVG[0] | V | Mean value, peak value positive, U L1-N
4287 | float | RD/WR | _ULN_POS_PEAK_AVG[1] | V | Mean value, peak value positive, U L2-N
4289 | float | RD/WR | _ULN_POS_PEAK_AVG[2] | V | Mean value, peak value positive, U L3-N
4291 | float | RD/WR | _ULN_POS_PEAK_AVG[3] | V | Mean value, peak value positive, U L4-N
4293 | float | RD/WR | _ULN_PEAK_PEAK_AVG[0] | V | Mean value, peak-peak value, U L1-N
4295 | float | RD/WR | _ULN_PEAK_PEAK_AVG[1] | V | Mean value, peak-peak value, U L2-N
4297 | float | RD/WR | _ULN_PEAK_PEAK_AVG[2] | V | Mean value, peak-peak value, U L3-N
4299 | float | RD/WR | _ULN_PEAK_PEAK_AVG[3] | V | Mean value, peak-peak value, U L4-N
4301 | float | RD/WR | _THD_ULL_AVG[0] | % | Mean value, harmonic, THD,U L1-L2
4303 | float | RD/WR | _THD_ULL_AVG[1] | % | Mean value, harmonic, THD,U L2-L3
4305 | float | RD/WR | _THD_ULL_AVG[2] | % | Mean value, harmonic, THD,U L3-L1
4307 | float | RD/WR | _THD_ZLL_AVG[0] | % | Mean value, interharmonics, U L1-L2
4309 | float | RD/WR | _THD_ZLL_AVG[1] | % | Mean value, interharmonics, U L2-L3
4311 | float | RD/WR | _THD_ZLL_AVG[2] | % | Mean value, interharmonics, U L3-L1
4313 | float | RD/WR | _ULL_OVER_AVG[0] | % | Mean value, over difference, U L1-L2 (61000-4-30)
4315 | float | RD/WR | _ULL_OVER_AVG[1] | % | Mean value, over difference, U L2-L3 (61000-4-30)
4317 | float | RD/WR | _ULL_OVER_AVG[2] | % | Mean value, over difference, U L3-L1 (61000-4-30)
4319 | float | RD/WR | _ULL_UNDER_AVG[0] | % | Mean value, under difference, U L1-L2 (61000-4-30)
4321 | float | RD/WR | _ULL_UNDER_AVG[1] | % | Mean value, under difference, U L2-L3 (61000-4-30)
4323 | float | RD/WR | _ULL_UNDER_AVG[2] | % | Mean value, under difference, U L3-L1 (61000-4-30)
4325 | float | RD/WR | _ULL_NEG_PEAK_AVG[0] | V | Mean value, peak value negative, U L1-L2
4327 | float | RD/WR | _ULL_NEG_PEAK_AVG[1] | V | Mean value, peak value negative, U L2-L3
4329 | float | RD/WR | _ULL_NEG_PEAK_AVG[2] | V | Mean value, peak value negative, U L3-L1
4331 | float | RD/WR | _ULL_POS_PEAK_AVG[0] | V | Mean value, peak value positive, U L1-L2
4333 | float | RD/WR | _ULL_POS_PEAK_AVG[1] | V | Mean value, peak value positive, U L2-L3
4335 | float | RD/WR | _ULL_POS_PEAK_AVG[2] | V | Mean value, peak value positive, U L3-L1
4337 | float | RD/WR | _ULL_PEAK_PEAK_AVG[0] | V | Mean value, peak-peak value, U L1-L2
4339 | float | RD/WR | _ULL_PEAK_PEAK_AVG[1] | V | Mean value, peak-peak value, U L2-L3
4341 | float | RD/WR | _ULL_PEAK_PEAK_AVG[2] | V | Mean value, peak-peak value, U L3-L1
4343 | float | RD/WR | _U_STERN_AVG | V
4345 | float | RD/WR | _U_SYM_AVG | % | Mean value, unsymmetrical, voltage
4347 | float | RD/WR | _FREQ_AVG | Hz | Mean value, measured frequency
4349 | float | RD/WR | _NORM_FREQ_AVG | Hz | Mean value, nominal frequency
4351 | float | RD/WR | _PLN_AVG[0] | W | Mean value, real power L1
4353 | float | RD/WR | _PLN_AVG[1] | W | Mean value, real power L2
4355 | float | RD/WR | _PLN_AVG[2] | W | Mean value, real power L3
4357 | float | RD/WR | _PLN_AVG[3] | W | Mean value, real power L4
4359 | float | RD/WR | _P_SUM_AVG | W | Mean value, sum; P = P1 + P2 + P3 + P4
4361 | float | RD/WR | _Q_SUM_AVG | var | Mean value, mains frequency reactive power
Sum; Q = Q1 + Q2 + Q3 + Q4
4363 | float | RD/WR | _QLN_AVG[0] | var | Mean value, reactive power L1 (fundamental comp.)
4365 | float | RD/WR | _QLN_AVG[1] | var | Mean value, reactive power L2 (fundamental comp.)
4367 | float | RD/WR | _QLN_AVG[2] | var | Mean value, reactive power L3 (fundamental comp.)
4369 | float | RD/WR | _QLN_AVG[3] | var | Mean value, reactive power L4 (fundamental comp.)
4371 | float | RD/WR | _P_SUM3_AVG | W | Mean value, Sum; P = P1 + P2 + P3
4373 | float | RD/WR | _Q_SUM3_AVG | var | Mean value, mains frequency reactive power
Sum; Q = Q1 + Q2 + Q3
4375 | float | RD/WR | _ILN_AVG[0] | A | Mean value, apparent current, L1
4377 | float | RD/WR | _ILN_AVG[1] | A | Mean value, apparent current, L2
4379 | float | RD/WR | _ILN_AVG[2] | A | Mean value, apparent current, L3
4381 | float | RD/WR | _ILN_AVG[3] | A | Mean value, apparent current, L4
4383 | float | RD/WR | _SLN_AVG[0] | VA | Mean value, apparent power L1
4385 | float | RD/WR | _SLN_AVG[1] | VA | Mean value, apparent power L2
4387 | float | RD/WR | _SLN_AVG[2] | VA | Mean value, apparent power L3
4389 | float | RD/WR | _SLN_AVG[3] | VA | Mean value, apparent power L4
4391 | float | RD/WR | _I_SUM3_AVG | A | Mean value, vector sum; IN = I1 + I2 + I3
4393 | float | RD/WR | _I_SUM_AVG | A | Mean value, vector sum; I1 + I2 + I3 + I4
4395 | float | RD/WR | _S_SUM3_AVG | VA | Mean value, sum; S = S1 + S2 + S3
4397 | float | RD/WR | _S_SUM_AVG | VA | Mean value, sum; S = S1 + S2 + S3 + S4
4399 | float | RD/WR | _THD_IL_AVG[0] | % | Mean value, harmonic, THD, I L1
4401 | float | RD/WR | _THD_IL_AVG[1] | % | Mean value, harmonic, THD, I L2
4403 | float | RD/WR | _THD_IL_AVG[2] | % | Mean value, harmonic, THD, I L3
4405 | float | RD/WR | _THD_IL_AVG[3] | % | Mean value, harmonic, THD, I L4
4407 | float | RD/WR | _ZHD_IL_AVG[0] | % | Mean value, interharmonics, ZHD, I, L1
4409 | float | RD/WR | _ZHD_IL_AVG[1] | % | Mean value, interharmonics, ZHD, I, L2
4411 | float | RD/WR | _ZHD_IL_AVG[2] | % | Mean value, interharmonics, ZHD, I, L3
4413 | float | RD/WR | _ZHD_IL_AVG[3] | % | Mean value, interharmonics, ZHD, I, L4
4415 | float | RD/WR | _ILN_CF_AVG[0] |  | Mean value, crest factor, I L1
4417 | float | RD/WR | _ILN_CF_AVG[1] |  | Mean value, crest factor, I L2
4419 | float | RD/WR | _ILN_CF_AVG[2] |  | Mean value, crest factor, I L3
4421 | float | RD/WR | _ILN_CF_AVG[3] |  | Mean value, crest factor, I L4
4423 | float | RD/WR | _IN_AVG | A | Mean value, zero sequence, current
4425 | float | RD/WR | _IM_AVG | A | Mean value, positive sequence, current
4427 | float | RD/WR | _IG_AVG | A | Mean value, negative sequence, current
4429 | float | RD/WR | _I_SYM_AVG | % | Mean value, unsymmetrical, current
4431 | float | RD/WR | _ILN_OVER_AVG[0] | % | Mean value, over difference, I L1
4433 | float | RD/WR | _ILN_OVER_AVG[1] | % | Mean value, over difference, I L2
4435 | float | RD/WR | _ILN_OVER_AVG[2] | % | Mean value, over difference, I L3
4437 | float | RD/WR | _ILN_OVER_AVG[3] | % | Mean value, over difference, I L4
4439 | float | RD/WR | _ILN_UNDER_AVG[0] | % | Mean value, under difference, I L1
4441 | float | RD/WR | _ILN_UNDER_AVG[1] | % | Mean value, under difference, I L2
4443 | float | RD/WR | _ILN_UNDER_AVG[2] | % | Mean value, under difference, I L3
4445 | float | RD/WR | _ILN_UNDER_AVG[3] | % | Mean value, under difference, I L4
4447 | float | RD/WR | _ILN_NEG_PEAK_AVG[0] | A | Mean value, peak value negative, I L1
4449 | float | RD/WR | _ILN_NEG_PEAK_AVG[1] | A | Mean value, peak value negative, I L2
4451 | float | RD/WR | _ILN_NEG_PEAK_AVG[2] | A | Mean value, peak value negative, I L3
4453 | float | RD/WR | _ILN_NEG_PEAK_AVG[3] | A | Mean value, peak value negative, I L4
4455 | float | RD/WR | _ILN_POS_PEAK_AVG[0] | A | Mean value, peak value positive, I L1
4457 | float | RD/WR | _ILN_POS_PEAK_AVG[1] | A | Mean value, peak value positive, I L2
4459 | float | RD/WR | _ILN_POS_PEAK_AVG[2] | A | Mean value, peak value positive, I L3
4461 | float | RD/WR | _ILN_POS_PEAK_AVG[3] | A | Mean value, peak value positive, I L4
4463 | float | RD/WR | _ILN_PEAK_PEAK_AVG[0] | A | Mean value, peak-peak value, I L1
4465 | float | RD/WR | _ILN_PEAK_PEAK_AVG[1] | A | Mean value, peak-peak value, I L2
4467 | float | RD/WR | _ILN_PEAK_PEAK_AVG[2] | A | Mean value, peak-peak value, I L3
4469 | float | RD/WR | _ILN_PEAK_PEAK_AVG[3] | A | Mean value, peak-peak value, I L4
4471 | float | RD/WR | _FLI_PF5_AVG[0] |  | Mean value, current flicker Pf5, L1-N
4473 | float | RD/WR | _FLI_PF5_AVG[1] |  | Mean value, current flicker Pf5, L2-N
4475 | float | RD/WR | _FLI_PF5_AVG[2] |  | Mean value, current flicker Pf5, L3-N
4477 | float | RD/WR | _FLI_PF5_AVG[3] |  | Mean value, current flicker Pf5, L4-N
4479 | float | RD/WR | _FLI_ST_AVG[0]
4481 | float | RD/WR | _FLI_ST_AVG[1]
4483 | float | RD/WR | _FLI_ST_AVG[2]
4485 | float | RD/WR | _FLI_ST_AVG[3]
4487 | float | RD/WR | _FLI_LT_AVG[0]
4489 | float | RD/WR | _FLI_LT_AVG[1]
4491 | float | RD/WR | _FLI_LT_AVG[2]
4493 | float | RD/WR | _FLI_LT_AVG[3]
4495 | float | RD/WR | _IRC_AVG[0] | A | Mean value, ripple control signal, I L1
4497 | float | RD/WR | _IRC_AVG[1] | A | Mean value, ripple control signal, I L2
4499 | float | RD/WR | _IRC_AVG[2] | A | Mean value, ripple control signal, I L3
4501 | float | RD/WR | _IRC_AVG[3] | A | Mean value, ripple control signal, I L4
4503 | float | RD/WR | _ULL_RC_AVG[0] | V | Mean value, ripple control signal, U L1-L2,
(61000-4-30)
4505 | float | RD/WR | _ULL_RC_AVG[1] | V | Mean value, ripple control signal, U L2-L3,
(61000-4-30
4507 | float | RD/WR | _ULL_RC_AVG[2] | V | Mean value, ripple control signal, U L3-L1,
(61000-4-30
4519 | float | RD/WR | _PFLN_AVG[0] | % | Mean value, power factor; L1
4521 | float | RD/WR | _PFLN_AVG[1] | % | Mean value, power factor; L2
4523 | float | RD/WR | _PFLN_AVG[2] | % | Mean value, power factor; L3
4525 | float | RD/WR | _PFLN_AVG[3] | % | Mean value, power factor; L4
4527 | float | RD/WR | _DLN_AVG[0] | var | Mean value, distortion power factor; L1
4529 | float | RD/WR | _DLN_AVG[1] | var | Mean value, distortion power factor; L2
4531 | float | RD/WR | _DLN_AVG[2] | var | Mean value, distortion power factor; L3
4533 | float | RD/WR | _DLN_AVG[3] | var | Mean value, distortion power factor; L4
4535 | float | RD/WR | _KFACT_AVG[0] | % | Mean value, K-Factor, L1
4537 | float | RD/WR | _KFACT_AVG[1] | % | Mean value, K-Factor, L2
4539 | float | RD/WR | _KFACT_AVG[2] | % | Mean value, K-Factor, L3
4541 | float | RD/WR | _KFACT_AVG[3] | % | Mean value, K-Factor, L4
4543 | float | RD/WR | _S0_POWER_AVG[0] | W | Mean value, Input 1, measured value
4545 | float | RD/WR | _S0_POWER_AVG[1] | W | Mean value, Input 2, measured value
4547 | float | RD/WR | _TEMPERATUR_AVG | °C | Mean value, internal temperature
Minimum values (float type)
Address | Format | RD/WR | Designation | Unit | Note
4549 | float | RD/WR | _ULN_MIN[0] | V | Min. value, voltage L1-N
4551 | float | RD/WR | _ULN_MIN[1] | V | Min. value, voltage L2-N
4553 | float | RD/WR | _ULN_MIN[2] | V | Min. value, voltage L3-N
4555 | float | RD/WR | _ULN_MIN[3] | V | Min. value, voltage L4-N
4557 | float | RD/WR | _ULL_MIN[0] | V | Min. value, phase conductor voltage; L1-L2
4559 | float | RD/WR | _ULL_MIN[1] | V | Min. value, phase conductor voltage; L2-L3
4561 | float | RD/WR | _ULL_MIN[2] | V | Min. value phase conductor voltage; L3-L1
4563 | float | RD/WR | _ULN_CF_MIN[0] |  | Min. value, crest factor of the Voltage U L1-N
4565 | float | RD/WR | _ULN_CF_MIN[1] |  | Min. value, crest factor of the Voltage U L2-N
4567 | float | RD/WR | _ULN_CF_MIN[2] |  | Min. value, crest factor of the Voltage U L3-N
4569 | float | RD/WR | _ULN_CF_MIN[3] |  | Min. value, crest factor of the Voltage U L4-N
4571 | float | RD/WR | _ULL_CF_MIN[0] |  | Min. value, crest factor of the Voltage U L1-L2
4573 | float | RD/WR | _ULL_CF_MIN[1] |  | Min. value, crest factor of the Voltage U L2-L3
4575 | float | RD/WR | _ULL_CF_MIN[2] |  | Min. value, crest factor of the Voltage U L3-L1
4577 | float | RD/WR | _UN_MIN | V | Min. value, zero sequence
4579 | float | RD/WR | _UM_MIN | V | Min. value, positive sequence
4581 | float | RD/WR | _UG_MIN | V | Min. value, negative sequence
4583 | float | RD/WR | _URC_MIN[0] | V | Min. value, ripple control signal, U L1-N (61000-4-30)
4585 | float | RD/WR | _URC_MIN[1] | V | Min. value, ripple control signal, U L2-N (61000-4-30)
4587 | float | RD/WR | _URC_MIN[2] | V | Min. value, ripple control signal, U L3-N (61000-4-30)
4589 | float | RD/WR | _URC_MIN[3] | V | Min. value, ripple control signal, U L4-N (61000-4-30)
4591 | float | RD/WR | _THD_ULN_MIN[0] | % | Min. value, harmonic, THD,U L1-N
4593 | float | RD/WR | _THD_ULN_MIN[1] | % | Min. value, harmonic, THD,U L2-N
4595 | float | RD/WR | _THD_ULN_MIN[2] | % | Min. value, harmonic, THD,U L3-N
4597 | float | RD/WR | _THD_ULN_MIN[3] | % | Min. value, harmonic, THD,U L4-N
4599 | float | RD/WR | _THD_ZLN_MIN[0] | % | Min. value, interharmonics, ZHD, U, L1
4601 | float | RD/WR | _THD_ZLN_MIN[1] | % | Min. value, interharmonics, ZHD, U, L2
4603 | float | RD/WR | _THD_ZLN_MIN[2] | % | Min. value, interharmonics, ZHD, U, L3
4605 | float | RD/WR | _THD_ZLN_MIN[3] | % | Min. value, interharmonics, ZHD, U, L4
4607 | float | RD/WR | _ULN_OVER_MIN[0] | % | Min. value, over difference, U L1 (61000-4-30)
4609 | float | RD/WR | _ULN_OVER_MIN[1] | % | Min. value, over difference, U L2 (61000-4-30)
4611 | float | RD/WR | _ULN_OVER_MIN[2] | % | Min. value, over difference, U L3 (61000-4-30)
4613 | float | RD/WR | _ULN_OVER_MIN[3] | % | Min. value, over difference, U L4 (61000-4-30)
4615 | float | RD/WR | _ULN_UNDER_MIN[0] | % | Min. value, under difference, U L1 (61000-4-30)
4617 | float | RD/WR | _ULN_UNDER_MIN[1] | % | Min. value, under difference, U L2 (61000-4-30)
4619 | float | RD/WR | _ULN_UNDER_MIN[2] | % | Min. value, under difference, U L3 (61000-4-30)
4621 | float | RD/WR | _ULN_UNDER_MIN[3] | % | Min. value, under difference, U L4 (61000-4-30)
4623 | float | RD/WR | _ULN_NEG_PEAK_MIN[0] | V | Min. value, peak value negative, U L1-N
4625 | float | RD/WR | _ULN_NEG_PEAK_MIN[1] | V | Min. value, peak value negative, U L2-N
4627 | float | RD/WR | _ULN_NEG_PEAK_MIN[2] | V | Min. value, peak value negative, U L3-N
4629 | float | RD/WR | _ULN_NEG_PEAK_MIN[3] | V | Min. value, peak value negative, U L4-N
4631 | float | RD/WR | _ULN_POS_PEAK_MIN[0] | V | Min. value, peak value positive, U L1-N
4633 | float | RD/WR | _ULN_POS_PEAK_MIN[1] | V | Min. value, peak value positive, U L2-N
4635 | float | RD/WR | _ULN_POS_PEAK_MIN[2] | V | Min. value, peak value positive, U L3-N
4637 | float | RD/WR | _ULN_POS_PEAK_MIN[3] | V | Min. value, peak value positive, U L4-N
4639 | float | RD/WR | _ULN_PEAK_PEAK_MIN[0] | V | Min. value, peak-peak value, U L1-N
4641 | float | RD/WR | _ULN_PEAK_PEAK_MIN[1] | V | Min. value, peak-peak value, U L2-N
4643 | float | RD/WR | _ULN_PEAK_PEAK_MIN[2] | V | Min. value, peak-peak value, U L3-N
4645 | float | RD/WR | _ULN_PEAK_PEAK_MIN[3] | V | Min. value, peak-peak value, U L4-N
4647 | float | RD/WR | _THD_ULL_MIN[0] | % | Min. value, harmonic, THD,U L1-L2
4649 | float | RD/WR | _THD_ULL_MIN[1] | % | Min. value, harmonic, THD,U L2-L3
4651 | float | RD/WR | _THD_ULL_MIN[2] | % | Min. value, harmonic, THD,U L3-L1
4653 | float | RD/WR | _THD_ZLL_MIN[0] | % | Min. value, interharmonics, U L1-L2
4655 | float | RD/WR | _THD_ZLL_MIN[1] | % | Min. value, interharmonics, U L2-L3
4657 | float | RD/WR | _THD_ZLL_MIN[2] | % | Min. value, interharmonics, U L3-L1
4659 | float | RD/WR | _ULL_OVER_MIN[0] | % | Min. value, over difference, U L1-L2 (61000-4-30)
4661 | float | RD/WR | _ULL_OVER_MIN[1] | % | Min. value, over difference, U L2-L3 (61000-4-30)
4663 | float | RD/WR | _ULL_OVER_MIN[2] | % | Min. value, over difference, U L3-L1 (61000-4-30)
4665 | float | RD/WR | _ULL_UNDER_MIN[0] | % | Min. value, under difference, U L1-L2 (61000-4-30)
4667 | float | RD/WR | _ULL_UNDER_MIN[1] | % | Min. value, under difference, U L2-L3 (61000-4-30)
4669 | float | RD/WR | _ULL_UNDER_MIN[2] | % | Min. value, under difference, U L3-L1 (61000-4-30)
4671 | float | RD/WR | _ULL_NEG_PEAK_MIN[0] | V | Min. value, peak value negative, U L1-L2
4673 | float | RD/WR | _ULL_NEG_PEAK_MIN[1] | V | Min. value, peak value negative, U L2-L3
4675 | float | RD/WR | _ULL_NEG_PEAK_MIN[2] | V | Min. value, peak value negative, U L3-L1
4677 | float | RD/WR | _ULL_POS_PEAK_MIN[0] | V | Min. value, peak value positive, U L1-L2
4679 | float | RD/WR | _ULL_POS_PEAK_MIN[1] | V | Min. value, peak value positive, U L2-L3
4681 | float | RD/WR | _ULL_POS_PEAK_MIN[2] | V | Min. value, peak value positive, U L3-L1
4683 | float | RD/WR | _ULL_PEAK_PEAK_MIN[0] | V | Min. value, peak-peak value, U L1-L2
4685 | float | RD/WR | _ULL_PEAK_PEAK_MIN[1] | V | Min. value, peak-peak value, U L2-L3
4687 | float | RD/WR | _ULL_PEAK_PEAK_MIN[2] | V | Min. value, peak-peak value, U L3-L1
4689 | float | RD/WR | _U_STERN_MIN | V
4691 | float | RD/WR | _U_SYM_MIN | % | Min. value, unsymmetrical; voltage
4693 | float | RD/WR | _FREQ_MIN | Hz | Min. value, measured frequency
4695 | float | RD/WR | _NORM_FREQ_MIN | Hz | Min. value, nominal frequency
4697 | float | RD/WR | _PLN_MIN[0] | W | Min. value, real power L1
4699 | float | RD/WR | _PLN_MIN[1] | W | Min. value, real power L2
4701 | float | RD/WR | _PLN_MIN[2] | W | Min. value, real power L3
4703 | float | RD/WR | _PLN_MIN[3] | W | Min. value, real power L4
4705 | float | RD/WR | _P_SUM_MIN | W | Min. value, sum; P = P1 + P2 + P3 + P4
4707 | float | RD/WR | _Q_SUM_MIN | var | Min. value, mains frequency reactive power
Sum; Q = Q1 + Q2 + Q3 + Q4
4709 | float | RD/WR | _QLN_MIN[0] | var | Min. value, reactive power L1 (fundamental comp.)
4711 | float | RD/WR | _QLN_MIN[1] | var | Min. value, reactive power L2 (fundamental comp.)
4713 | float | RD/WR | _QLN_MIN[2] | var | Min. value, reactive power L3 (fundamental comp.)
4715 | float | RD/WR | _QLN_MIN[3] | var | Min. value, reactive power L4 (fundamental comp.)
4717 | float | RD/WR | _P_SUM3_MIN | W | Min. value, Sum; P = P1 + P2 + P3
4719 | float | RD/WR | _Q_SUM3_MIN | var | Min. value, mains frequency reactive power
Sum; Q = Q1 + Q2 + Q3
4721 | float | RD/WR | _TEMPERATUR_MIN | °C | Min. value, internal temperature
Maximum values (float type)
Address | Format | RD/WR | Designation | Unit | Note
4723 | float | RD/WR | _ULN_MAX[0] | V | Max. value, voltage L1-N
4725 | float | RD/WR | _ULN_MAX[1] | V | Max. value, voltage L2-N
4727 | float | RD/WR | _ULN_MAX[2] | V | Max. value, voltage L3-N
4729 | float | RD/WR | _ULN_MAX[3] | V | Max. value, voltage L4-N
4731 | float | RD/WR | _ULL_MAX[0] | V | Max. value, phase conductor voltage; L1-L2
4733 | float | RD/WR | _ULL_MAX[1] | V | Max. value, phase conductor voltage; L2-L3
4735 | float | RD/WR | _ULL_MAX[2] | V | Max. value, phase conductor voltage; L3-L1
4737 | float | RD/WR | _ULN_CF_MAX[0] |  | Max. value, crest factor of the Voltage U L1-N
4739 | float | RD/WR | _ULN_CF_MAX[1] |  | Max. value, crest factor of the Voltage U L2-N
4741 | float | RD/WR | _ULN_CF_MAX[2] |  | Max. value, crest factor of the Voltage U L3-N
4743 | float | RD/WR | _ULN_CF_MAX[3] |  | Max. value, crest factor of the Voltage U L4-N
4745 | float | RD/WR | _ULL_CF_MAX[0] |  | Max. value, crest factor of the Voltage U L1-L2
4747 | float | RD/WR | _ULL_CF_MAX[1] |  | Max. value, crest factor of the Voltage U L2-L3
4749 | float | RD/WR | _ULL_CF_MAX[2] |  | Max. value, crest factor of the Voltage U L3-L1
4751 | float | RD/WR | _UN_MAX | V | Max. value, zero sequence
4753 | float | RD/WR | _UM_MAX | V | Max. value, positive sequence
4755 | float | RD/WR | _UG_MAX | V | Min. value, negative sequence
4757 | float | RD/WR | _URC_MAX[0] | V | Max. value, ripple control signal, U L1-N,
(61000-4-30)
4759 | float | RD/WR | _URC_MAX[1] | V | Max. value, ripple control signal, U L2-N,
(61000-4-30)
4761 | float | RD/WR | _URC_MAX[2] | V | Max. value, ripple control signal, U L3-N,
(61000-4-30)
4763 | float | RD/WR | _URC_MAX[3] | V | Max. value, ripple control signal, U L4-N,
(61000-4-30)
4765 | float | RD/WR | _THD_ULN_MAX[0] | % | Max. value, harmonic, THD,U L1-N
4767 | float | RD/WR | _THD_ULN_MAX[1] | % | Max. value, harmonic, THD,U L2-N
4769 | float | RD/WR | _THD_ULN_MAX[2] | % | Max. value, harmonic, THD,U L3-N
4771 | float | RD/WR | _THD_ULN_MAX[3] | % | Max. value, harmonic, THD,U L4-N
4773 | float | RD/WR | _THD_ZLN_MAX[0] | % | Max. value, interharmonics, ZHD, U, L1
4775 | float | RD/WR | _THD_ZLN_MAX[1] | % | Max. value, interharmonics, ZHD, U, L2
4777 | float | RD/WR | _THD_ZLN_MAX[2] | % | Max. value, interharmonics, ZHD, U, L3
4779 | float | RD/WR | _THD_ZLN_MAX[3] | % | Max. value, interharmonics, ZHD, U, L4
4781 | float | RD/WR | _ULN_OVER_MAX[0] | % | Max. value, over difference, U L1 (61000-4-30)
4783 | float | RD/WR | _ULN_OVER_MAX[1] | % | Max. value, over difference, U L2 (61000-4-30)
4785 | float | RD/WR | _ULN_OVER_MAX[2] | % | Max. value, over difference, U L3 (61000-4-30)
4787 | float | RD/WR | _ULN_OVER_MAX[3] | % | Max. value, over difference, U L4 (61000-4-30)
4789 | float | RD/WR | _ULN_UNDER_MAX[0] | % | Max. value, under difference, U L1 (61000-4-30)
4791 | float | RD/WR | _ULN_UNDER_MAX[1] | % | Max. value, under difference, U L2 (61000-4-30)
4793 | float | RD/WR | _ULN_UNDER_MAX[2] | % | Max. value, under difference, U L3 (61000-4-30)
4795 | float | RD/WR | _ULN_UNDER_MAX[3] | % | Max. value, under difference, U L4 (61000-4-30)
4797 | float | RD/WR | _ULN_NEG_PEAK_MAX[0] | V | Max. value, peak value negative, U L1-N
4799 | float | RD/WR | _ULN_NEG_PEAK_MAX[1] | V | Max. value, peak value negative, U L2-N
4801 | float | RD/WR | _ULN_NEG_PEAK_MAX[2] | V | Max. value, peak value negative, U L3-N
4803 | float | RD/WR | _ULN_NEG_PEAK_MAX[3] | V | Max. value, peak value negative, U L4-N
4805 | float | RD/WR | _ULN_POS_PEAK_MAX[0] | V | Max. value, peak value positive, U L1-N
4807 | float | RD/WR | _ULN_POS_PEAK_MAX[1] | V | Max. value, peak value positive, U L2-N
4809 | float | RD/WR | _ULN_POS_PEAK_MAX[2] | V | Max. value, peak value positive, U L3-N
4811 | float | RD/WR | _ULN_POS_PEAK_MAX[3] | V | Max. value, peak value positive, U L4-N
4813 | float | RD/WR | _ULN_PEAK_PEAK_MAX[0] | V | Max. value, peak-peak value, U L1-N
4815 | float | RD/WR | _ULN_PEAK_PEAK_MAX[1] | V | Max. value, peak-peak value, U L2-N
4817 | float | RD/WR | _ULN_PEAK_PEAK_MAX[2] | V | Max. value, peak-peak value, U L3-N
4819 | float | RD/WR | _ULN_PEAK_PEAK_MAX[3] | V | Max. value, peak-peak value, U L4-N
4821 | float | RD/WR | _THD_ULL_MAX[0] | % | Max. value, harmonic, THD,U L1-L2
4823 | float | RD/WR | _THD_ULL_MAX[1] | % | Max. value, harmonic, THD,U L2-L3
4825 | float | RD/WR | _THD_ULL_MAX[2] | % | Max. value, harmonic, THD,U L3-L1
4827 | float | RD/WR | _THD_ZLL_MAX[0] | % | Max. value, interharmonics, U L1-L2
4829 | float | RD/WR | _THD_ZLL_MAX[1] | % | Max. value, interharmonics, U L2-L3
4831 | float | RD/WR | _THD_ZLL_MAX[2] | % | Max. value, interharmonics, U L3-L1
4833 | float | RD/WR | _ULL_OVER_MAX[0] | % | Max. value, over difference, U L1-L2 (61000-4-30)
4835 | float | RD/WR | _ULL_OVER_MAX[1] | % | Max. value, over difference, U L2-L3 (61000-4-30)
4837 | float | RD/WR | _ULL_OVER_MAX[2] | % | Max. value, over difference, U L3-L1 (61000-4-30)
4839 | float | RD/WR | _ULL_UNDER_MAX[0] | % | Max. value, under difference, U L1-L2 (61000-4-30)
4841 | float | RD/WR | _ULL_UNDER_MAX[1] | % | Max. value, under difference, U L2-L3 (61000-4-30)
4843 | float | RD/WR | _ULL_UNDER_MAX[2] | % | Max. value, under difference, U L3-L1 (61000-4-30)
4845 | float | RD/WR | _ULL_NEG_PEAK_MAX[0] | V | Max. value, peak value negative, U L1-L2
4847 | float | RD/WR | _ULL_NEG_PEAK_MAX[1] | V | Max. value, peak value negative, U L2-L3
4849 | float | RD/WR | _ULL_NEG_PEAK_MAX[2] | V | Max. value, peak value negative, U L3-L1
4851 | float | RD/WR | _ULL_POS_PEAK_MAX[0] | V | Max. value, peak value positive, U L1-L2
4853 | float | RD/WR | _ULL_POS_PEAK_MAX[1] | V | Max. value, peak value positive, U L2-L3
4855 | float | RD/WR | _ULL_POS_PEAK_MAX[2] | V | Max. value, peak value positive, U L3-L1
4857 | float | RD/WR | _ULL_PEAK_PEAK_MAX[0] | V | Max. value, peak-peak value, U L1-L2
4859 | float | RD/WR | _ULL_PEAK_PEAK_MAX[1] | V | Max. value, peak-peak value, U L2-L3
4861 | float | RD/WR | _ULL_PEAK_PEAK_MAX[2] | V | Max. value, peak-peak value, U L3-L1
4863 | float | RD/WR | _U_STERN_MAX | V
4865 | float | RD/WR | _U_SYM_MAX | % | Max. value, unsymmetrical; voltage
4867 | float | RD/WR | _FREQ_MAX | Hz | Max. value, measured frequency
4869 | float | RD/WR | _NORM_FREQ_MAX | Hz | Max. value, nominal frequency
4871 | float | RD/WR | _PLN_MAX[0] | W | Max. value, real power L1
4873 | float | RD/WR | _PLN_MAX[1] | W | Max. value, real power L2
4875 | float | RD/WR | _PLN_MAX[2] | W | Max. value, real power L3
4877 | float | RD/WR | _PLN_MAX[3] | W | Max. value, real power L4
4879 | float | RD/WR | _P_SUM_MAX | W | Max. value, sum; P = P1 + P2 + P3 + P4
4881 | float | RD/WR | _Q_SUM_MAX | var | Max. value, mains frequency reactive power
Sum; Q = Q1 + Q2 + Q3 + Q4
4883 | float | RD/WR | _QLN_MAX[0] | var | Max. value, reactive power L1 (fundamental comp.)
4885 | float | RD/WR | _QLN_MAX[1] | var | Max. value, reactive power L2 (fundamental comp.)
4887 | float | RD/WR | _QLN_MAX[2] | var | Max. value, reactive power L3 (fundamental comp.)
4889 | float | RD/WR | _QLN_MAX[3] | var | Max. value, reactive power L4 (fundamental comp.)
4891 | float | RD/WR | _P_SUM3_MAX | W | Max. value, Sum; P = P1 + P2 + P3
4893 | float | RD/WR | _Q_SUM3_MAX | var | Max. value, mains frequency reactive power
Sum; Q = Q1 + Q2 + Q3
4895 | float | RD/WR | _ILN_MAX[0] | A | Max. value, apparent current, L1
4897 | float | RD/WR | _ILN_MAX[1] | A | Max. value, apparent current, L2
4899 | float | RD/WR | _ILN_MAX[2] | A | Max. value, apparent current, L3
4901 | float | RD/WR | _ILN_MAX[3] | A | Max. value, apparent current, L4
4903 | float | RD/WR | _SLN_MAX[0] | VA | Max. value, apparent power L1
4905 | float | RD/WR | _SLN_MAX[1] | VA | Max. value, apparent power L2
4907 | float | RD/WR | _SLN_MAX[2] | VA | Max. value, apparent power L3
4909 | float | RD/WR | _SLN_MAX[3] | VA | Max. value, apparent power L4
4911 | float | RD/WR | _I_SUM3_MAX | A | Max. value, vector sum; IN = I1 + I2 + I3
4913 | float | RD/WR | _I_SUM_MAX | A | Max. value, vector sum; I1 + I2 + I3 + I4
4915 | float | RD/WR | _S_SUM3_MAX | VA | Max. value, sum; S = S1 + S2 + S3
4917 | float | RD/WR | _S_SUM_MAX | VA | Max. value, sum; S = S1 + S2 + S3 + S4
4919 | float | RD/WR | _THD_IL_MAX[0] | % | Max. value, harmonic, THD, I L1
4921 | float | RD/WR | _THD_IL_MAX[1] | % | Max. value, harmonic, THD, I L2
4923 | float | RD/WR | _THD_IL_MAX[2] | % | Max. value, harmonic, THD, I L3
4925 | float | RD/WR | _THD_IL_MAX[3] | % | Max. value, harmonic, THD, I L4
4927 | float | RD/WR | _ZHD_IL_MAX[0] | % | Max. value, interharmonics, ZHD, I, L1
4929 | float | RD/WR | _ZHD_IL_MAX[1] | % | Max. value, interharmonics, ZHD, I, L2
4931 | float | RD/WR | _ZHD_IL_MAX[2] | % | Max. value, interharmonics, ZHD, I, L3
4933 | float | RD/WR | _ZHD_IL_MAX[3] | % | Max. value, interharmonics, ZHD, I, L4
4935 | float | RD/WR | _ILN_CF_MAX[0] |  | Max. value, crest factor, I L1
4937 | float | RD/WR | _ILN_CF_MAX[1] |  | Max. value, crest factor, I L2
4939 | float | RD/WR | _ILN_CF_MAX[2] |  | Max. value, crest factor, I L3
4941 | float | RD/WR | _ILN_CF_MAX[3] |  | Max. value, crest factor, I L4
4943 | float | RD/WR | _IN_MAX | A | Max. value, zero sequence, current
4945 | float | RD/WR | _IM_MAX | A | Max. value, positive sequence, current
4947 | float | RD/WR | _IG_MAX | A | Max. value, negative sequence, current
4949 | float | RD/WR | _I_SYM_MAX | % | Max. value, unsymmetrical; current
4951 | float | RD/WR | _ILN_OVER_MAX[0] | % | Max. value, over difference, I L1
4953 | float | RD/WR | _ILN_OVER_MAX[1] | % | Max. value, over difference, I L2
4955 | float | RD/WR | _ILN_OVER_MAX[2] | % | Max. value, over difference, I L3
4957 | float | RD/WR | _ILN_OVER_MAX[3] | % | Max. value, over difference, I L4
4959 | float | RD/WR | _ILN_UNDER_MAX[0] | % | Max. value, under difference, I L1
4961 | float | RD/WR | _ILN_UNDER_MAX[1] | % | Max. value, under difference, I L2
4963 | float | RD/WR | _ILN_UNDER_MAX[2] | % | Max. value, under difference, I L3
4965 | float | RD/WR | _ILN_UNDER_MAX[3] | % | Max. value, under difference, I L4
4967 | float | RD/WR | _ILN_NEG_PEAK_MAX[0] | A | Max. value, peak value negative, I L1
4969 | float | RD/WR | _ILN_NEG_PEAK_MAX[1] | A | Max. value, peak value negative, I L2
4971 | float | RD/WR | _ILN_NEG_PEAK_MAX[2] | A | Max. value, peak value negative, I L3
4973 | float | RD/WR | _ILN_NEG_PEAK_MAX[3] | A | Max. value, peak value negative, I L4
4975 | float | RD/WR | _ILN_POS_PEAK_MAX[0] | A | Max. value, peak value positive, I L1
4977 | float | RD/WR | _ILN_POS_PEAK_MAX[1] | A | Max. value, peak value positive, I L2
4979 | float | RD/WR | _ILN_POS_PEAK_MAX[2] | A | Max. value, peak value positive, I L3
4981 | float | RD/WR | _ILN_POS_PEAK_MAX[3] | A | Max. value, peak value positive, I L4
4983 | float | RD/WR | _ILN_PEAK_PEAK_MAX[0] | A | Max. value, peak-peak value, I L1
4985 | float | RD/WR | _ILN_PEAK_PEAK_MAX[1] | A | Max. value, peak-peak value, I L2
4987 | float | RD/WR | _ILN_PEAK_PEAK_MAX[2] | A | Max. value, peak-peak value, I L3
4989 | float | RD/WR | _ILN_PEAK_PEAK_MAX[3] | A | Max. value, peak-peak value, I L4
4991 | float | RD/WR | _FLI_PF5_MAX[0] |  | Max. value, current flicker Pf5, L1-N
4993 | float | RD/WR | _FLI_PF5_MAX[1] |  | Max. value, current flicker Pf5, L2-N
4995 | float | RD/WR | _FLI_PF5_MAX[2] |  | Max. value, current flicker Pf5, L3-N
4997 | float | RD/WR | _FLI_PF5_MAX[3] |  | Max. value, current flicker Pf5, L4-N
4999 | float | RD/WR | _FLI_ST_MAX[0]
5001 | float | RD/WR | _FLI_ST_MAX[1]
5003 | float | RD/WR | _FLI_ST_MAX[2]
5005 | float | RD/WR | _FLI_ST_MAX[3]
5007 | float | RD/WR | _FLI_LT_MAX[0]
5009 | float | RD/WR | _FLI_LT_MAX[1]
5011 | float | RD/WR | _FLI_LT_MAX[2]
5013 | float | RD/WR | _FLI_LT_MAX[3]
5015 | float | RD/WR | _ILN_RC_MAX[0] | A | Max. value, ripple control signal, I L1
5017 | float | RD/WR | _ILN_RC_MAX[1] | A | Max. value, ripple control signal, I L2
5019 | float | RD/WR | _ILN_RC_MAX[2] | A | Max. value, ripple control signal, I L3
5021 | float | RD/WR | _ILN_RC_MAX[3] | A | Max. value, ripple control signal, I L4
5023 | float | RD/WR | _ULL_RC_MAX[0] | V | Max. value, ripple control signal, U L1-L2
5025 | float | RD/WR | _ULL_RC_MAX[1] | V | Max. value, ripple control signal, U L2-L3
5027 | float | RD/WR | _ULL_RC_MAX[2] | V | Max. value, ripple control signal, U L3-L1
5039 | float | RD/WR | _PFLN_MAX[0] | % | Max. value, power factor; L1
5041 | float | RD/WR | _PFLN_MAX[1] | % | Max. value, power factor; L2
5043 | float | RD/WR | _PFLN_MAX[2] | % | Max. value, power factor; L3
5045 | float | RD/WR | _PFLN_MAX[3] | % | Max. value, power factor; L4
5047 | float | RD/WR | _DLN_MAX[0] | var | Max. value, distortion power factor; L1
5049 | float | RD/WR | _DLN_MAX[1] | var | Max. value, distortion power factor; L2
5051 | float | RD/WR | _DLN_MAX[2] | var | Max. value, distortion power factor; L3
5053 | float | RD/WR | _DLN_MAX[3] | var | Max. value, distortion power factor; L4
5055 | float | RD/WR | _KFACT_MAX[0] | % | Max. value, K-Factor, L1
5057 | float | RD/WR | _KFACT_MAX[1] | % | Max. value, K-Factor, L2
5059 | float | RD/WR | _KFACT_MAX[2] | % | Max. value, K-Factor, L3
5061 | float | RD/WR | _KFACT_MAX[3] | % | Max. value, K-Factor, L4
5063 | float | RD/WR | _S0_POWER_MAX[0] | W | Max. value, Input 1, measured value
5065 | float | RD/WR | _S0_POWER_MAX[1] | W | Max. value, Input 2, measured value
5067 | float | RD/WR | _TEMPERATUR_MAX | °C | Max. value, internal temperature
Averaging time (short type)
Address | Format | RD/WR | Designation | Unit | Note
5069 | short | RD/WR | _ULN_AVG_T[0] | n | Averaging time, U L1-N
5070 | short | RD/WR | _ULN_AVG_T[1] | n | Averaging time, U L2-N
5071 | short | RD/WR | _ULN_AVG_T[2] | n | Averaging time, U L3-N
5072 | short | RD/WR | _ULN_AVG_T[3] | n | Averaging time, U L4-N
5073 | short | RD/WR | _ULL_AVG_T[0] | n | Averaging time, U L1-L2
5074 | short | RD/WR | _ULL_AVG_T[1] | n | Averaging time, U L2-L3
5075 | short | RD/WR | _ULL_AVG_T[2] | n | Averaging time, U L3-L1
5076 | short | RD/WR | _ULN_CF_AVG_T[0] | n | Averaging time, crest factor, U L1-N
5077 | short | RD/WR | _ULN_CF_AVG_T[1] | n | Averaging time, crest factor, U L2-N
5078 | short | RD/WR | _ULN_CF_AVG_T[2] | n | Averaging time, crest factor, U L3-N
5079 | short | RD/WR | _ULN_CF_AVG_T[3] | n | Averaging time, crest factor, U L4-N
5080 | short | RD/WR | _ULL_CF_AVG_T[0] | n | Averaging time, crest factor, U L1-L2
5081 | short | RD/WR | _ULL_CF_AVG_T[1] | n | Averaging time, crest factor, U L2-L3
5082 | short | RD/WR | _ULL_CF_AVG_T[2] | n | Averaging time, crest factor, U L3-L1
5083 | short | RD/WR | _UN_AVG_T | n | Averaging time, zero sequence
5084 | short | RD/WR | _UM_AVG_T | n | Averaging time, positive sequence
5085 | short | RD/WR | _UG_AVG_T | n | Averaging time, negative sequence
5086 | short | RD/WR | _URC_AVG_T[0] | n | Averaging time, ripple control signal, U L1-N
5087 | short | RD/WR | _URC_AVG_T[1] | n | Averaging time, ripple control signal, U L2-N
5088 | short | RD/WR | _URC_AVG_T[2] | n | Averaging time, ripple control signal, U L3-N
5089 | short | RD/WR | _URC_AVG_T[3] | n | Averaging time, ripple control signal, U L4-N
5090 | short | RD/WR | _THD_ULN_AVG_T[0] | n | Averaging time, harmonics, THD, U L1-N
5091 | short | RD/WR | _THD_ULN_AVG_T[1] | n | Averaging time, harmonics, THD, U L2-N
5092 | short | RD/WR | _THD_ULN_AVG_T[2] | n | Averaging time, harmonics, THD, U L3-N
5093 | short | RD/WR | _THD_ULN_AVG_T[3] | n | Averaging time, harmonics, THD, U L4-N
5094 | short | RD/WR | _THD_ZLN_AVG_T[0] | n | Averaging time, interharmonics, ZHD, U, L1
5095 | short | RD/WR | _THD_ZLN_AVG_T[1] | n | Averaging time, interharmonics, ZHD, U, L2
5096 | short | RD/WR | _THD_ZLN_AVG_T[2] | n | Averaging time, interharmonics, ZHD, U, L3
5097 | short | RD/WR | _THD_ZLN_AVG_T[3] | n | Averaging time, interharmonics, ZHD, U, L4
5098 | short | RD/WR | _ULN_OVER_AVG_T[0] | n | Averaging time, over difference, U L1
5099 | short | RD/WR | _ULN_OVER_AVG_T[1] | n | Averaging time, over difference, U L2
5100 | short | RD/WR | _ULN_OVER_AVG_T[2] | n | Averaging time, over difference, U L3
5101 | short | RD/WR | _ULN_OVER_AVG_T[3] | n | Averaging time, over difference, U L4
5102 | short | RD/WR | _ULN_UNDER_AVG_T[0] | n | Averaging time, under difference, U L1
5103 | short | RD/WR | _ULN_UNDER_AVG_T[1] | n | Averaging time, under difference, U L2
5104 | short | RD/WR | _ULN_UNDER_AVG_T[2] | n | Averaging time, under difference, U L3
5105 | short | RD/WR | _ULN_UNDER_AVG_T[3] | n | Averaging time, under difference, U L4
5106 | short | RD/WR | _ULN_NEG_PEAK_AVG_T[0] | n | Averaging time, peak value negative, U L1-N
5107 | short | RD/WR | _ULN_NEG_PEAK_AVG_T[1] | n | Averaging time, peak value negative, U L2-N
5108 | short | RD/WR | _ULN_NEG_PEAK_AVG_T[2] | n | Averaging time, peak value negative, U L3-N
5109 | short | RD/WR | _ULN_NEG_PEAK_AVG_T[3] | n | Averaging time, peak value negative, U L4-N
5110 | short | RD/WR | _ULN_POS_PEAK_AVG_T[0] | n | Averaging time, peak value positive, U L1-N
5111 | short | RD/WR | _ULN_POS_PEAK_AVG_T[1] | n | Averaging time, peak value positive, U L2-N
5112 | short | RD/WR | _ULN_POS_PEAK_AVG_T[2] | n | Averaging time, peak value positive, U L3-N
5113 | short | RD/WR | _ULN_POS_PEAK_AVG_T[3] | n | Averaging time, peak value positive, U L4-N
5114 | short | RD/WR | _ULN_PEAK_PEAK_AVG_T[0] | n | Averaging time, peak-peak value, U L1-N
5115 | short | RD/WR | _ULN_PEAK_PEAK_AVG_T[1] | n | Averaging time, peak-peak value, U L2-N
5116 | short | RD/WR | _ULN_PEAK_PEAK_AVG_T[2] | n | Averaging time, peak-peak value, U L3-N
5117 | short | RD/WR | _ULN_PEAK_PEAK_AVG_T[3] | n | Averaging time, peak-peak value, U L4-N
5118 | short | RD/WR | _THD_ULL_AVG_T[0] | n | Averaging time, harmonic, THD,U L1-L2
5119 | short | RD/WR | _THD_ULL_AVG_T[1] | n | Averaging time, harmonic, THD,U L2-L3
5120 | short | RD/WR | _THD_ULL_AVG_T[2] | n | Averaging time, harmonic, THD,U L3-L1
5121 | short | RD/WR | _THD_ZLL_AVG_T[0] | n | Averaging time, interharmonics, U L1-L2
5122 | short | RD/WR | _THD_ZLL_AVG_T[1] | n | Averaging time, interharmonics, U L2-L3
5123 | short | RD/WR | _THD_ZLL_AVG_T[2] | n | Averaging time, interharmonics, U L3-L1
5124 | short | RD/WR | _ULL_OVER_AVG_T[0] | n | Averaging time, over difference, U L1-L2
5125 | short | RD/WR | _ULL_OVER_AVG_T[1] | n | Averaging time, over difference, U L2-L3
5126 | short | RD/WR | _ULL_OVER_AVG_T[2] | n | Averaging time, over difference, U L3-L1
5127 | short | RD/WR | _ULL_UNDER_AVG_T[0] | n | Averaging time, under difference, U L1-L2
5128 | short | RD/WR | _ULL_UNDER_AVG_T[1] | n | Averaging time, under difference, U L2-L3
5129 | short | RD/WR | _ULL_UNDER_AVG_T[2] | n | Averaging time, under difference, U L3-L1
5130 | short | RD/WR | _ULL_NEG_PEAK_AVG_T[0] | n | Averaging time, peak value negative, U L1-L2
5131 | short | RD/WR | _ULL_NEG_PEAK_AVG_T[1] | n | Averaging time, peak value negative, U L2-L3
5132 | short | RD/WR | _ULL_NEG_PEAK_AVG_T[2] | n | Averaging time, peak value negative, U L3-L1
5133 | short | RD/WR | _ULL_POS_PEAK_AVG_T[0] | n | Averaging time, peak value positive, U L1-L2
5134 | short | RD/WR | _ULL_POS_PEAK_AVG_T[1] | n | Averaging time, peak value positive, U L2-L3
5135 | short | RD/WR | _ULL_POS_PEAK_AVG_T[2] | n | Averaging time, peak value positive, U L3-L1
5136 | short | RD/WR | _ULL_PEAK_PEAK_AVG_T[0] | n | Averaging time, peak-peak value, U L1-L2
5137 | short | RD/WR | _ULL_PEAK_PEAK_AVG_T[1] | n | Averaging time, peak-peak value, U L2-L3
5138 | short | RD/WR | _ULL_PEAK_PEAK_AVG_T[2] | n | Averaging time, peak-peak value, U L3-L1
5139 | short | RD/WR | _U_STERN_AVG_T
5140 | short | RD/WR | _U_SYM_AVG_T | n | Averaging time, unsymmetrical voltage
5141 | short | RD/WR | _FREQ_AVG_T | n | Averaging time, measured frequency
5142 | short | RD/WR | _NORM_FREQ_AVG_T | n | Averaging time, nominal frequency
5143 | short | RD/WR | _PLN_AVG_T[0] | n | Averaging time, real power L1
5144 | short | RD/WR | _PLN_AVG_T[1] | n | Averaging time, real power L2
5145 | short | RD/WR | _PLN_AVG_T[2] | n | Averaging time, real power L3
5146 | short | RD/WR | _PLN_AVG_T[3] | n | Averaging time, real power L4
5147 | short | RD/WR | _P_SUM_AVG_T | n | Averaging time, sum P = P1 + P2 + P3 + P4
5148 | short | RD/WR | _Q_SUM_AVG_T | n | Averaging time, mains frequency reactive power
Sum Q = Q1 + Q2 + Q3 + Q4
5149 | short | RD/WR | _QLN_AVG_T[0] | n | Averaging time, reactive power L1
5150 | short | RD/WR | _QLN_AVG_T[1] | n | Averaging time, reactive power L2
5151 | short | RD/WR | _QLN_AVG_T[2] | n | Averaging time, reactive power L3
5152 | short | RD/WR | _QLN_AVG_T[3] | n | Averaging time, reactive power L4
5153 | short | RD/WR | _P_SUM3_AVG_T | n | Averaging time, Sum P = P1 + P2 + P3
5154 | short | RD/WR | _Q_SUM3_AVG_T | n | Averaging time, mains frequency reactive power
Sum Q = Q1 + Q2 + Q3
5155 | short | RD/WR | _ILN_AVG_T[0] | n | Averaging time, apparent current, L1
5156 | short | RD/WR | _ILN_AVG_T[1] | n | Averaging time, apparent current, L2
5157 | short | RD/WR | _ILN_AVG_T[2] | n | Averaging time, apparent current, L3
5158 | short | RD/WR | _ILN_AVG_T[3] | n | Averaging time, apparent current, L4
5159 | short | RD/WR | _SLN_AVG_T[0] | n | Averaging time, apparent power L1
5160 | short | RD/WR | _SLN_AVG_T[1] | n | Averaging time, apparent power L2
5161 | short | RD/WR | _SLN_AVG_T[2] | n | Averaging time, apparent power L3
5162 | short | RD/WR | _SLN_AVG_T[3] | n | Averaging time, apparent power L4
5163 | short | RD/WR | _I_SUM3_AVG_T | n | Averaging time, vector sum; IN = I1 + I2 + I3
5164 | short | RD/WR | _I_SUM_AVG_T | n | Averaging time, vector sum; I1 + I2 + I3 + I4
5165 | short | RD/WR | _S_SUM3_AVG_T | n | Averaging time, sum; S = S1 + S2 + S3
5166 | short | RD/WR | _S_SUM_AVG_T | n | Averaging time, sum; S = S1 + S2 + S3 + S4
5167 | short | RD/WR | _THD_IL_AVG_T[0] | n | Averaging time, harmonic, THD, I L1
5168 | short | RD/WR | _THD_IL_AVG_T[1] | n | Averaging time, harmonic, THD, I L2
5169 | short | RD/WR | _THD_IL_AVG_T[2] | n | Averaging time, harmonic, THD, I L3
5170 | short | RD/WR | _THD_IL_AVG_T[3] | n | Averaging time, harmonic, THD, I L4
5171 | short | RD/WR | _ZHD_IL_AVG_T[0] | n | Averaging time, interharmonics, ZHD, I, L1
5172 | short | RD/WR | _ZHD_IL_AVG_T[1] | n | Averaging time, interharmonics, ZHD, I, L2
5173 | short | RD/WR | _ZHD_IL_AVG_T[2] | n | Averaging time, interharmonics, ZHD, I, L3
5174 | short | RD/WR | _ZHD_IL_AVG_T[3] | n | Averaging time, interharmonics, ZHD, I, L4
5175 | short | RD/WR | _ILN_CF_AVG_T[0] | n | Averaging time, crest factor, I L1
5176 | short | RD/WR | _ILN_CF_AVG_T[1] | n | Averaging time, crest factor, I L2
5177 | short | RD/WR | _ILN_CF_AVG_T[2] | n | Averaging time, crest factor, I L3
5178 | short | RD/WR | _ILN_CF_AVG_T[3] | n | Averaging time, crest factor, I L4
5179 | short | RD/WR | _IN_AVG_T | n | Averaging time, zero sequence, current
5180 | short | RD/WR | _IM_AVG_T | n | Averaging time, positive sequence, current
5181 | short | RD/WR | _IG_AVG_T | n | Averaging time, negative sequence, current
5182 | short | RD/WR | _I_SYM_AVG_T | n | Averaging time, unsymmetrical current
5183 | short | RD/WR | _ILN_OVER_AVG_T[0] | n | Averaging time, over difference, I L1
5184 | short | RD/WR | _ILN_OVER_AVG_T[1] | n | Averaging time, over difference, I L2
5185 | short | RD/WR | _ILN_OVER_AVG_T[2] | n | Averaging time, over difference, I L3
5186 | short | RD/WR | _ILN_OVER_AVG_T[3] | n | Averaging time, over difference, I L4
5187 | short | RD/WR | _ILN_UNDER_AVG_T[0] | n | Averaging time, under difference, I L1
5188 | short | RD/WR | _ILN_UNDER_AVG_T[1] | n | Averaging time, under difference, I L2
5189 | short | RD/WR | _ILN_UNDER_AVG_T[2] | n | Averaging time, under difference, I L3
5190 | short | RD/WR | _ILN_UNDER_AVG_T[3] | n | Averaging time, under difference, I L4
5191 | short | RD/WR | _ILN_NEG_PEAK_AVG_T[0] | n | Averaging time, peak value negative, I L1
5192 | short | RD/WR | _ILN_NEG_PEAK_AVG_T[1] | n | Averaging time, peak value negative, I L2
5193 | short | RD/WR | _ILN_NEG_PEAK_AVG_T[2] | n | Averaging time, peak value negative, I L3
5194 | short | RD/WR | _ILN_NEG_PEAK_AVG_T[3] | n | Averaging time, peak value negative, I L4
5195 | short | RD/WR | _ILN_POS_PEAK_AVG_T[0] | n | Averaging time, peak value positive, I L1
5196 | short | RD/WR | _ILN_POS_PEAK_AVG_T[1] | n | Averaging time, peak value positive, I L2
5197 | short | RD/WR | _ILN_POS_PEAK_AVG_T[2] | n | Averaging time, peak value positive, I L3
5198 | short | RD/WR | _ILN_POS_PEAK_AVG_T[3] | n | Averaging time, peak value positive, I L4
5199 | short | RD/WR | _ILN_PEAK_PEAK_AVG_T[0] | n | Averaging time, peak-peak value, I L1
5200 | short | RD/WR | _ILN_PEAK_PEAK_AVG_T[1] | n | Averaging time, peak-peak value, I L2
5201 | short | RD/WR | _ILN_PEAK_PEAK_AVG_T[2] | n | Averaging time, peak-peak value, I L3
5202 | short | RD/WR | _ILN_PEAK_PEAK_AVG_T[3] | n | Averaging time, peak-peak value, I L4
5203 | short | RD/WR | _FLI_PF5_AVG_T[0] | n | Averaging time, current flicker Pf5, L1-N
5204 | short | RD/WR | _FLI_PF5_AVG_T[1] | n | Averaging time, current flicker Pf5, L2-N
5205 | short | RD/WR | _FLI_PF5_AVG_T[2] | n | Averaging time, current flicker Pf5, L3-N
5206 | short | RD/WR | _FLI_PF5_AVG_T[3] | n | Averaging time, current flicker Pf5, L4-N
5207 | short | RD/WR | _FLI_ST_AVG_T[0] | n
5208 | short | RD/WR | _FLI_ST_AVG_T[1] | n
5209 | short | RD/WR | _FLI_ST_AVG_T[2] | n
5210 | short | RD/WR | _FLI_ST_AVG_T[3] | n
5211 | short | RD/WR | _FLI_LT_AVG_T[0] | n
5212 | short | RD/WR | _FLI_LT_AVG_T[1] | n
5213 | short | RD/WR | _FLI_LT_AVG_T[2] | n
5214 | short | RD/WR | _FLI_LT_AVG_T[3] | n
5215 | short | RD/WR | _ILN_RC_AVG_T[0] | n | Averaging time, ripple control signal, I L1
5216 | short | RD/WR | _ILN_RC_AVG_T[1] | n | Averaging time, ripple control signal, I L2
5217 | short | RD/WR | _ILN_RC_AVG_T[2] | n | Averaging time, ripple control signal, I L3
5218 | short | RD/WR | _ILN_RC_AVG_T[3] | n | Averaging time, ripple control signal, I L4
5219 | short | RD/WR | _ULL_RC_AVG_T[0] | n | Averaging time, ripple control signal, U L1-L2
5220 | short | RD/WR | _ULL_RC_AVG_T[1] | n | Averaging time, ripple control signal, U L1-L2
5221 | short | RD/WR | _ULL_RC_AVG_T[2] | n | Averaging time, ripple control signal, U L1-L2
5227 | short | RD/WR | _PFLN_AVG_T[0] | n | Averaging time, power factor; L1
5228 | short | RD/WR | _PFLN_AVG_T[1] | n | Averaging time, power factor; L2
5229 | short | RD/WR | _PFLN_AVG_T[2] | n | Averaging time, power factor; L3
5230 | short | RD/WR | _PFLN_AVG_T[3] | n | Averaging time, power factor; L4
5231 | short | RD/WR | _DLN_AVG_T[0] | n | Averaging time, distortion power factor; L1
5232 | short | RD/WR | _DLN_AVG_T[1] | n | Averaging time, distortion power factor; L2
5233 | short | RD/WR | _DLN_AVG_T[2] | n | Averaging time, distortion power factor; L3
5234 | short | RD/WR | _DLN_AVG_T[3] | n | Averaging time, distortion power factor; L4
5235 | short | RD/WR | _KFACT_AVG_T[0] | n | Averaging time, K-Factor, L1
5236 | short | RD/WR | _KFACT_AVG_T[1] | n | Averaging time, K-Factor, L2
5237 | short | RD/WR | _KFACT_AVG_T[2] | n | Averaging time, K-Factor, L3
5238 | short | RD/WR | _KFACT_AVG_T[3] | n | Averaging time, K-Factor, L4
5239 | short | RD/WR | _S0_POWER_AVG_T[0] | n | Averaging time, input 1, measured value
5240 | short | RD/WR | _S0_POWER_AVG_T[1] | n | Averaging time, input 2, measured value
5241 | short | RD/WR | _TEMPERATUR_AVG_T | n | Averaging time, internal temperature
Minimum values time stamp (uint type)
Address | Format | RD/WR | Designation | Unit | Note
5242 | uint | RD/WR | _ULN_MIN_T[0] | s | Time of min. val. (UTC), U L1-N
5244 | uint | RD/WR | _ULN_MIN_T[1] | s | Time of min. val. (UTC), U L2-N
5246 | uint | RD/WR | _ULN_MIN_T[2] | s | Time of min. val. (UTC), U L3-N
5248 | uint | RD/WR | _ULN_MIN_T[3] | s | Time of min. val. (UTC), U L4-N
5250 | uint | RD/WR | _ULL_MIN_T[0] | s | Time of min. val. (UTC), U L1-L2
5252 | uint | RD/WR | _ULL_MIN_T[1] | s | Time of min. val. (UTC), U L2-L3
5254 | uint | RD/WR | _ULL_MIN_T[2] | s | Time of min. val. (UTC), U L3-L1
5256 | uint | RD/WR | _ULN_CF_MIN_T[0] | s | Time of min. val. (UTC), crest factor, U L1-N
5258 | uint | RD/WR | _ULN_CF_MIN_T[1] | s | Time of min. val. (UTC), crest factor, U L2-N
5260 | uint | RD/WR | _ULN_CF_MIN_T[2] | s | Time of min. val. (UTC), crest factor, U L3-N
5262 | uint | RD/WR | _ULN_CF_MIN_T[3] | s | Time of min. val. (UTC), crest factor, U L4-N
5264 | uint | RD/WR | _ULL_CF_MIN_T[0] | s | Time of min. val. (UTC), crest factor, U L1-L2
5266 | uint | RD/WR | _ULL_CF_MIN_T[1] | s | Time of min. val. (UTC), crest factor, U L2-L3
5268 | uint | RD/WR | _ULL_CF_MIN_T[2] | s | Time of min. val. (UTC), crest factor, U L3-L1
5270 | uint | RD/WR | _UN_MIN_T | s | Time of min. val. (UTC), zero sequence
5272 | uint | RD/WR | _UM_MIN_T | s | Time of min. val. (UTC), positive sequence
5274 | uint | RD/WR | _UG_MIN_T | s | Time of min. val. (UTC), negative sequence
5276 | uint | RD/WR | _URC_MIN_T[0] | s | Time of min. val. (UTC), ripple control signal, U L1-N
5278 | uint | RD/WR | _URC_MIN_T[1] | s | Time of min. val. (UTC), ripple control signal, U L2-N
5280 | uint | RD/WR | _URC_MIN_T[2] | s | Time of min. val. (UTC), ripple control signal, U L3-N
5282 | uint | RD/WR | _URC_MIN_T[3] | s | Time of min. val. (UTC), ripple control signal, U L4-N
5284 | uint | RD/WR | _THD_ULN_MIN_T[0] | s | Time of min. val. (UTC), harmonics, THD, U L1-N
5286 | uint | RD/WR | _THD_ULN_MIN_T[1] | s | Time of min. val. (UTC), harmonics, THD, U L2-N
5288 | uint | RD/WR | _THD_ULN_MIN_T[2] | s | Time of min. val. (UTC), harmonics, THD, U L3-N
5290 | uint | RD/WR | _THD_ULN_MIN_T[3] | s | Time of min. val. (UTC), harmonics, THD, U L4-N
5292 | uint | RD/WR | _THD_ZLN_MIN_T[0] | s | Time of min. val. (UTC), interharmonics, ZHD, U, L1
5294 | uint | RD/WR | _THD_ZLN_MIN_T[1] | s | Time of min. val. (UTC), interharmonics, ZHD, U, L2
5296 | uint | RD/WR | _THD_ZLN_MIN_T[2] | s | Time of min. val. (UTC), interharmonics, ZHD, U, L3
5298 | uint | RD/WR | _THD_ZLN_MIN_T[3] | s | Time of min. val. (UTC), interharmonics, ZHD, U, L4
5300 | uint | RD/WR | _ULN_OVER_MIN_T[0] | s | Time of min. val. (UTC), over difference, U L1
5302 | uint | RD/WR | _ULN_OVER_MIN_T[1] | s | Time of min. val. (UTC), over difference, U L2
5304 | uint | RD/WR | _ULN_OVER_MIN_T[2] | s | Time of min. val. (UTC), over difference, U L3
5306 | uint | RD/WR | _ULN_OVER_MIN_T[3] | s | Time of min. val. (UTC), over difference, U L4
5308 | uint | RD/WR | _ULN_UNDER_MIN_T[0] | s | Time of min. val. (UTC), under difference, U L1
5310 | uint | RD/WR | _ULN_UNDER_MIN_T[1] | s | Time of min. val. (UTC), under difference, U L2
5312 | uint | RD/WR | _ULN_UNDER_MIN_T[2] | s | Time of min. val. (UTC), under difference, U L3
5314 | uint | RD/WR | _ULN_UNDER_MIN_T[3] | s | Time of min. val. (UTC), under difference, U L4
5316 | uint | RD/WR | _ULN_NEG_PEAK_MIN_T[0] | s | Time of min. val. (UTC), peak value negative, U L1-N
5318 | uint | RD/WR | _ULN_NEG_PEAK_MIN_T[1] | s | Time of min. val. (UTC), peak value negative, U L2-N
5320 | uint | RD/WR | _ULN_NEG_PEAK_MIN_T[2] | s | Time of min. val. (UTC), peak value negative, U L3-N
5322 | uint | RD/WR | _ULN_NEG_PEAK_MIN_T[3] | s | Time of min. val. (UTC), peak value negative, U L4-N
5324 | uint | RD/WR | _ULN_POS_PEAK_MIN_T[0] | s | Time of min. val. (UTC), peak value positive, U L1-N
5326 | uint | RD/WR | _ULN_POS_PEAK_MIN_T[1] | s | Time of min. val. (UTC), peak value positive, U L2-N
5328 | uint | RD/WR | _ULN_POS_PEAK_MIN_T[2] | s | Time of min. val. (UTC), peak value positive, U L3-N
5330 | uint | RD/WR | _ULN_POS_PEAK_MIN_T[3] | s | Time of min. val. (UTC), peak value positive, U L4-N
5332 | uint | RD/WR | _ULN_PEAK_PEAK_MIN_T[0] | s | Time of min. val. (UTC), peak-peak value, U L1-N
5334 | uint | RD/WR | _ULN_PEAK_PEAK_MIN_T[1] | s | Time of min. val. (UTC), peak-peak value, U L2-N
5336 | uint | RD/WR | _ULN_PEAK_PEAK_MIN_T[2] | s | Time of min. val. (UTC), peak-peak value, U L3-N
5338 | uint | RD/WR | _ULN_PEAK_PEAK_MIN_T[3] | s | Time of min. val. (UTC), peak-peak value, U L4-N
5340 | uint | RD/WR | _THD_ULL_MIN_T[0] | s | Time of min. val. (UTC), harmonic, THD,U L1-L2
5342 | uint | RD/WR | _THD_ULL_MIN_T[1] | s | Time of min. val. (UTC), harmonic, THD,U L2-L3
5344 | uint | RD/WR | _THD_ULL_MIN_T[2] | s | Time of min. val. (UTC), harmonic, THD,U L3-L1
5346 | uint | RD/WR | _THD_ZLL_MIN_T[0] | s | Time of min. val. (UTC), interharmonics, U L1-L2
5348 | uint | RD/WR | _THD_ZLL_MIN_T[1] | s | Time of min. val. (UTC), interharmonics, U L2-L3
5350 | uint | RD/WR | _THD_ZLL_MIN_T[2] | s | Time of min. val. (UTC), interharmonics, U L3-L1
5352 | uint | RD/WR | _ULL_OVER_MIN_T[0] | s | Time of min. val. (UTC), over difference, U L1-L2
5354 | uint | RD/WR | _ULL_OVER_MIN_T[1] | s | Time of min. val. (UTC), over difference, U L2-L3
5356 | uint | RD/WR | _ULL_OVER_MIN_T[2] | s | Time of min. val. (UTC), over difference, U L3-L1
5358 | uint | RD/WR | _ULL_UNDER_MIN_T[0] | s | Time of min. val. (UTC), under difference, U L1-L2
5360 | uint | RD/WR | _ULL_UNDER_MIN_T[1] | s | Time of min. val. (UTC), under difference, U L2-L3
5362 | uint | RD/WR | _ULL_UNDER_MIN_T[2] | s | Time of min. val. (UTC), under difference, U L3-L4
5364 | uint | RD/WR | _ULL_NEG_PEAK_MIN_T[0] | s | Time of min. val. (UTC), peak value negative, U L1-L2
5366 | uint | RD/WR | _ULL_NEG_PEAK_MIN_T[1] | s | Time of min. val. (UTC), peak value negative, U L2-L3
5368 | uint | RD/WR | _ULL_NEG_PEAK_MIN_T[2] | s | Time of min. val. (UTC), peak value negative, U L3-L1
5370 | uint | RD/WR | _ULL_POS_PEAK_MIN_T[0] | s | Time of min. val. (UTC), peak value positive, U L1-L2
5372 | uint | RD/WR | _ULL_POS_PEAK_MIN_T[1] | s | Time of min. val. (UTC), peak value positive, U L2-L3
5374 | uint | RD/WR | _ULL_POS_PEAK_MIN_T[2] | s | Time of min. val. (UTC), peak value positive, U L3-L1
5376 | uint | RD/WR | _ULL_PEAK_PEAK_MIN_T[0] | s | Time of min. val. (UTC), peak-peak value, U L1-L2
5378 | uint | RD/WR | _ULL_PEAK_PEAK_MIN_T[1] | s | Time of min. val. (UTC), peak-peak value, U L2-L3
5380 | uint | RD/WR | _ULL_PEAK_PEAK_MIN_T[2] | s | Time of min. val. (UTC), peak-peak value, U L3-L1
5382 | uint | RD/WR | _U_STERN_MIN_T | s
5384 | uint | RD/WR | _U_SYM_MIN_T | s | Time of min. val. (UTC), unsymmetrical voltage
5386 | uint | RD/WR | _FREQ_MIN_T | s | Time of min. val. (UTC), measured frequency
5388 | uint | RD/WR | _NORM_FREQ_MIN_T | s | Time of min. val. (UTC), nominal frequency
5390 | uint | RD/WR | _PLN_MIN_T[0] | s | Time of min. val. (UTC), real power L1
5392 | uint | RD/WR | _PLN_MIN_T[1] | s | Time of min. val. (UTC), real power L2
5394 | uint | RD/WR | _PLN_MIN_T[2] | s | Time of min. val. (UTC), real power L3
5396 | uint | RD/WR | _PLN_MIN_T[3] | s | Time of min. val. (UTC), real power L4
5398 | uint | RD/WR | _P_SUM_MIN_T | s | Time of min. val. (UTC), sum; P = P1 + P2 + P3 + P4
5400 | uint | RD/WR | _Q_SUM_MIN_T | s | Time of min. val. (UTC), sum; Q = Q1 + Q2 + Q3 + Q4
5402 | uint | RD/WR | _QLN_MIN_T[0] | s | Time of min. val. (UTC), reactive power L1
5404 | uint | RD/WR | _QLN_MIN_T[1] | s | Time of min. val. (UTC), reactive power L2
5406 | uint | RD/WR | _QLN_MIN_T[2] | s | Time of min. val. (UTC), reactive power L3
5408 | uint | RD/WR | _QLN_MIN_T[3] | s | Time of min. val. (UTC), reactive power L4
5410 | uint | RD/WR | _P_SUM3_MIN_T | s | Time of min. val. (UTC), sum; P = P1 + P2 + P3
5412 | uint | RD/WR | _Q_SUM3_MIN_T | s | Time of min. val. (UTC), sum; Q = Q1 + Q2 + Q3
5414 | uint | RD/WR | _TEMPERATUR_MIN_T | s | Time of min. val. (UTC), internal temperature
Maximum values time stamp (uint type)
Address | Format | RD/WR | Designation | Unit | Note
5416 | uint | RD/WR | _ULN_MAX_T[0] | s | Time of max. val. (UTC), U L1-N
5418 | uint | RD/WR | _ULN_MAX_T[1] | s | Time of max. val. (UTC), U L2-N
5420 | uint | RD/WR | _ULN_MAX_T[2] | s | Time of max. val. (UTC), U L3-N
5422 | uint | RD/WR | _ULN_MAX_T[3] | s | Time of max. val. (UTC), U L4-N
5424 | uint | RD/WR | _ULL_MAX_T[0] | s | Time of max. val. (UTC), U L1-L2
5426 | uint | RD/WR | _ULL_MAX_T[1] | s | Time of max. val. (UTC), U L2-L3
5428 | uint | RD/WR | _ULL_MAX_T[2] | s | Time of max. val. (UTC), U L3-L1
5430 | uint | RD/WR | _ULN_CF_MAX_T[0] | s | Time of max. val. (UTC), crest factor, U L1-N
5432 | uint | RD/WR | _ULN_CF_MAX_T[1] | s | Time of max. val. (UTC), crest factor, U L2-N
5434 | uint | RD/WR | _ULN_CF_MAX_T[2] | s | Time of max. val. (UTC), crest factor, U L3-N
5436 | uint | RD/WR | _ULN_CF_MAX_T[3] | s | Time of max. val. (UTC), crest factor, U L4-N
5438 | uint | RD/WR | _ULL_CF_MAX_T[0] | s | Time of max. val. (UTC), crest factor, U L1-L2
5440 | uint | RD/WR | _ULL_CF_MAX_T[1] | s | Time of max. val. (UTC), crest factor, U L2-L3
5442 | uint | RD/WR | _ULL_CF_MAX_T[2] | s | Time of max. val. (UTC), crest factor, U L3-L1
5444 | uint | RD/WR | _UN_MAX_T | s | Time of max. val. (UTC), zero sequence
5446 | uint | RD/WR | _UM_MAX_T | s | Time of max. val. (UTC), positive sequence
5448 | uint | RD/WR | _UG_MAX_T | s | Time of max. val. (UTC), negative sequence
5450 | uint | RD/WR | _URC_MAX_T[0] | s | Time of max. val. (UTC), ripple control signal, U L1-N
5452 | uint | RD/WR | _URC_MAX_T[1] | s | Time of max. val. (UTC), ripple control signal, U L2-N
5454 | uint | RD/WR | _URC_MAX_T[2] | s | Time of max. val. (UTC), ripple control signal, U L3-N
5456 | uint | RD/WR | _URC_MAX_T[3] | s | Time of max. val. (UTC), ripple control signal, U L4-N
5458 | uint | RD/WR | _THD_ULN_MAX_T[0] | s | Time of max. val. (UTC), harmonics, THD, U L1-N
5460 | uint | RD/WR | _THD_ULN_MAX_T[1] | s | Time of max. val. (UTC), harmonics, THD, U L2-N
5462 | uint | RD/WR | _THD_ULN_MAX_T[2] | s | Time of max. val. (UTC), harmonics, THD, U L3-N
5464 | uint | RD/WR | _THD_ULN_MAX_T[3] | s | Time of max. val. (UTC), harmonics, THD, U L4-N
5466 | uint | RD/WR | _THD_ZLN_MAX_T[0] | s | Time of max. val. (UTC), interharmonics, ZHD, U, L1
5468 | uint | RD/WR | _THD_ZLN_MAX_T[1] | s | Time of max. val. (UTC), interharmonics, ZHD, U, L2
5470 | uint | RD/WR | _THD_ZLN_MAX_T[2] | s | Time of max. val. (UTC), interharmonics, ZHD, U, L3
5472 | uint | RD/WR | _THD_ZLN_MAX_T[3] | s | Time of max. val. (UTC), interharmonics, ZHD, U, L4
5474 | uint | RD/WR | _ULN_OVER_MAX_T[0] | s | Time of max. val. (UTC), over difference, U L1
5476 | uint | RD/WR | _ULN_OVER_MAX_T[1] | s | Time of max. val. (UTC), over difference, U L2
5478 | uint | RD/WR | _ULN_OVER_MAX_T[2] | s | Time of max. val. (UTC), over difference, U L3
5480 | uint | RD/WR | _ULN_OVER_MAX_T[3] | s | Time of max. val. (UTC), over difference, U L4
5482 | uint | RD/WR | _ULN_UNDER_MAX_T[0] | s | Time of max. val. (UTC), under difference, U L1
5484 | uint | RD/WR | _ULN_UNDER_MAX_T[1] | s | Time of max. val. (UTC), under difference, U L2
5486 | uint | RD/WR | _ULN_UNDER_MAX_T[2] | s | Time of max. val. (UTC), under difference, U L3
5488 | uint | RD/WR | _ULN_UNDER_MAX_T[3] | s | Time of max. val. (UTC), under difference, U L4
5490 | uint | RD/WR | _ULN_NEG_PEAK_MAX_T[0] | s | Time of max. val. (UTC), peak value negative, U L1-N
5492 | uint | RD/WR | _ULN_NEG_PEAK_MAX_T[1] | s | Time of max. val. (UTC), peak value negative, U L2-N
5494 | uint | RD/WR | _ULN_NEG_PEAK_MAX_T[2] | s | Time of max. val. (UTC), peak value negative, U L3-N
5496 | uint | RD/WR | _ULN_NEG_PEAK_MAX_T[3] | s | Time of max. val. (UTC), peak value negative, U L4-N
5498 | uint | RD/WR | _ULN_POS_PEAK_MAX_T[0] | s | Time of max. val. (UTC), peak value positive, U L1-N
5500 | uint | RD/WR | _ULN_POS_PEAK_MAX_T[1] | s | Time of max. val. (UTC), peak value positive, U L2-N
5502 | uint | RD/WR | _ULN_POS_PEAK_MAX_T[2] | s | Time of max. val. (UTC), peak value positive, U L3-N
5504 | uint | RD/WR | _ULN_POS_PEAK_MAX_T[3] | s | Time of max. val. (UTC), peak value positive, U L4-N
5506 | uint | RD/WR | _ULN_PEAK_PEAK_MAX_T[0] | s | Time of max. val. (UTC), peak-peak value, U L1-N
5508 | uint | RD/WR | _ULN_PEAK_PEAK_MAX_T[1] | s | Time of max. val. (UTC), peak-peak value, U L2-N
5510 | uint | RD/WR | _ULN_PEAK_PEAK_MAX_T[2] | s | Time of max. val. (UTC), peak-peak value, U L3-N
5512 | uint | RD/WR | _ULN_PEAK_PEAK_MAX_T[3] | s | Time of max. val. (UTC), peak-peak value, U L4-N
5514 | uint | RD/WR | _THD_ULL_MAX_T[0] | s | Time of max. val. (UTC), harmonic, THD,U L1-L2
5516 | uint | RD/WR | _THD_ULL_MAX_T[1] | s | Time of max. val. (UTC), harmonic, THD,U L2-L3
5518 | uint | RD/WR | _THD_ULL_MAX_T[2] | s | Time of max. val. (UTC), harmonic, THD,U L3-L1
5520 | uint | RD/WR | _THD_ZLL_MAX_T[0] | s | Time of max. val. (UTC), interharmonics, U L1-L2
5522 | uint | RD/WR | _THD_ZLL_MAX_T[1] | s | Time of max. val. (UTC), interharmonics, U L2-L3
5524 | uint | RD/WR | _THD_ZLL_MAX_T[2] | s | Time of max. val. (UTC), interharmonics, U L3-L1
5526 | uint | RD/WR | _ULL_OVER_MAX_T[0] | s | Time of max. val. (UTC), over difference, U L1-L2
5528 | uint | RD/WR | _ULL_OVER_MAX_T[1] | s | Time of max. val. (UTC), over difference, U L2-L3
5530 | uint | RD/WR | _ULL_OVER_MAX_T[2] | s | Time of max. val. (UTC), over difference, U L3-L1
5532 | uint | RD/WR | _ULL_UNDER_MAX_T[0] | s | Time of max. val. (UTC), under difference, U L1-L2
5534 | uint | RD/WR | _ULL_UNDER_MAX_T[1] | s | Time of max. val. (UTC), under difference, U L2-L3
5536 | uint | RD/WR | _ULL_UNDER_MAX_T[2] | s | Time of max. val. (UTC), under difference, U L3-L1
5538 | uint | RD/WR | _ULL_NEG_PEAK_MAX_T[0] | s | Time of max. val. (UTC), peak value negative, U L1-L2
5540 | uint | RD/WR | _ULL_NEG_PEAK_MAX_T[1] | s | Time of max. val. (UTC), peak value negative, U L2-L3
5542 | uint | RD/WR | _ULL_NEG_PEAK_MAX_T[2] | s | Time of max. val. (UTC), peak value negative, U L3-L1
5544 | uint | RD/WR | _ULL_POS_PEAK_MAX_T[0] | s | Time of max. val. (UTC), peak value positive, U L1-L2
5546 | uint | RD/WR | _ULL_POS_PEAK_MAX_T[1] | s | Time of max. val. (UTC), peak value positive, U L2-L3
5548 | uint | RD/WR | _ULL_POS_PEAK_MAX_T[2] | s | Time of max. val. (UTC), peak value positive, U L3-L1
5550 | uint | RD/WR | _ULL_PEAK_PEAK_MAX_T[0] | s | Time of max. val. (UTC), peak-peak value, U L1-L2
5552 | uint | RD/WR | _ULL_PEAK_PEAK_MAX_T[1] | s | Time of max. val. (UTC), peak-peak value, U L2-L3
5554 | uint | RD/WR | _ULL_PEAK_PEAK_MAX_T[2] | s | Time of max. val. (UTC), peak-peak value, U L3-L1
5556 | uint | RD/WR | _U_STERN_MAX_T | s
5558 | uint | RD/WR | _U_SYM_MAX_T | s | Time of max. val. (UTC), unsymmetrical voltage
5560 | uint | RD/WR | _FREQ_MAX_T | s | Time of max. val. (UTC), measured frequency
5562 | uint | RD/WR | _NORM_FREQ_MAX_T | s | Time of max. val. (UTC), nominal frequency
5564 | uint | RD/WR | _PLN_MAX_T[0] | s | Time of max. val. (UTC), real power L1
5566 | uint | RD/WR | _PLN_MAX_T[1] | s | Time of max. val. (UTC), real power L2
5568 | uint | RD/WR | _PLN_MAX_T[2] | s | Time of max. val. (UTC), real power L3
5570 | uint | RD/WR | _PLN_MAX_T[3] | s | Time of max. val. (UTC), real power L4
5572 | uint | RD/WR | _P_SUM_MAX_T | s | Time of max. val. (UTC), sum P = P1 + P2 + P3 + P4
5574 | uint | RD/WR | _Q_SUM_MAX_T | s | Time of max. val. (UTC), sum Q = Q1 + Q2 + Q3 + Q4
5576 | uint | RD/WR | _QLN_MAX_T[0] | s | Time of max. val. (UTC), reactive power L1
5578 | uint | RD/WR | _QLN_MAX_T[1] | s | Time of max. val. (UTC), reactive power L2
5580 | uint | RD/WR | _QLN_MAX_T[2] | s | Time of max. val. (UTC), reactive power L3
5582 | uint | RD/WR | _QLN_MAX_T[3] | s | Time of max. val. (UTC), reactive power L4
5584 | uint | RD/WR | _P_SUM3_MAX_T | s | Time of max. val. (UTC), sum P = P1 + P2 + P3
5586 | uint | RD/WR | _Q_SUM3_MAX_T | s | Time of max. val. (UTC), sum Q = Q1 + Q2 + Q3
5588 | uint | RD/WR | _ILN_MAX_T[0] | s | Time of max. val. (UTC), apparent current, L1
5590 | uint | RD/WR | _ILN_MAX_T[1] | s | Time of max. val. (UTC), apparent current, L2
5592 | uint | RD/WR | _ILN_MAX_T[2] | s | Time of max. val. (UTC), apparent current, L3
5594 | uint | RD/WR | _ILN_MAX_T[3] | s | Time of max. val. (UTC), apparent current, L4
5596 | uint | RD/WR | _SLN_MAX_T[0] | s | Time of max. val. (UTC), apparent power L1
5598 | uint | RD/WR | _SLN_MAX_T[1] | s | Time of max. val. (UTC), apparent power L2
5600 | uint | RD/WR | _SLN_MAX_T[2] | s | Time of max. val. (UTC), apparent power L3
5602 | uint | RD/WR | _SLN_MAX_T[3] | s | Time of max. val. (UTC), apparent power L4
5604 | uint | RD/WR | _I_SUM3_MAX_T | s | Time of max. val. (UTC), vector sum; IN = I1 + I2 + I3
5606 | uint | RD/WR | _I_SUM_MAX_T | s | Time of max. val. (UTC), vector sum; I1 + I2 + I3 + I4
5608 | uint | RD/WR | _S_SUM3_MAX_T | s | Time of max. val. (UTC), sum S = S1 + S2 + S3
5610 | uint | RD/WR | _S_SUM_MAX_T | s | Time of max. val. (UTC), sum S = S1 + S2 + S3 + S4
5612 | uint | RD/WR | _THD_IL_MAX_T[0] | s | Time of max. val. (UTC), harmonic, THD, I L1
5614 | uint | RD/WR | _THD_IL_MAX_T[1] | s | Time of max. val. (UTC), harmonic, THD, I L2
5616 | uint | RD/WR | _THD_IL_MAX_T[2] | s | Time of max. val. (UTC), harmonic, THD, I L3
5618 | uint | RD/WR | _THD_IL_MAX_T[3] | s | Time of max. val. (UTC), harmonic, THD, I L4
5620 | uint | RD/WR | _ZHD_IL_MAX_T[0] | s | Time of max. val. (UTC), interharmonics, ZHD, I, L1
5622 | uint | RD/WR | _ZHD_IL_MAX_T[1] | s | Time of max. val. (UTC), interharmonics, ZHD, I, L2
5624 | uint | RD/WR | _ZHD_IL_MAX_T[2] | s | Time of max. val. (UTC), interharmonics, ZHD, I, L3
5626 | uint | RD/WR | _ZHD_IL_MAX_T[3] | s | Time of max. val. (UTC), interharmonics, ZHD, I, L4
5628 | uint | RD/WR | _ILN_CF_MAX_T[0] | s | Time of max. val. (UTC), crest factor, I L1
5630 | uint | RD/WR | _ILN_CF_MAX_T[1] | s | Time of max. val. (UTC), crest factor, I L2
5632 | uint | RD/WR | _ILN_CF_MAX_T[2] | s | Time of max. val. (UTC), crest factor, I L3
5634 | uint | RD/WR | _ILN_CF_MAX_T[3] | s | Time of max. val. (UTC), crest factor, I L4
5636 | uint | RD/WR | _IN_MAX_T | s | Time of max. val. (UTC), zero sequence, current
5638 | uint | RD/WR | _IM_MAX_T | s | Time of max. val. (UTC), positive sequence, current
5640 | uint | RD/WR | _IG_MAX_T | s | Time of max. val. (UTC), negative sequence, current
5642 | uint | RD/WR | _I_SYM_MAX_T | s | Time of max. val. (UTC), unsymmetrical; current
5644 | uint | RD/WR | _ILN_OVER_MAX_T[0] | s | Time of max. val. (UTC), over difference, I L1
5646 | uint | RD/WR | _ILN_OVER_MAX_T[1] | s | Time of max. val. (UTC), over difference, I L2
5648 | uint | RD/WR | _ILN_OVER_MAX_T[2] | s | Time of max. val. (UTC), over difference, I L3
5650 | uint | RD/WR | _ILN_OVER_MAX_T[3] | s | Time of max. val. (UTC), over difference, I L4
5652 | uint | RD/WR | _ILN_UNDER_MAX_T[0] | s | Time of max. val. (UTC), under difference, I L1
5654 | uint | RD/WR | _ILN_UNDER_MAX_T[1] | s | Time of max. val. (UTC), under difference, I L2
5656 | uint | RD/WR | _ILN_UNDER_MAX_T[2] | s | Time of max. val. (UTC), under difference, I L3
5658 | uint | RD/WR | _ILN_UNDER_MAX_T[3] | s | Time of max. val. (UTC), under difference, I L4
5660 | uint | RD/WR | _ILN_NEG_PEAK_MAX_T[0] | s | Time of max. val. (UTC), peak value negative, I L1
5662 | uint | RD/WR | _ILN_NEG_PEAK_MAX_T[1] | s | Time of max. val. (UTC), peak value negative, I L2
5664 | uint | RD/WR | _ILN_NEG_PEAK_MAX_T[2] | s | Time of max. val. (UTC), peak value negative, I L3
5666 | uint | RD/WR | _ILN_NEG_PEAK_MAX_T[3] | s | Time of max. val. (UTC), peak value negative, I L4
5668 | uint | RD/WR | _ILN_POS_PEAK_MAX_T[0] | s | Time of max. val. (UTC), peak value positive, I L1
5670 | uint | RD/WR | _ILN_POS_PEAK_MAX_T[1] | s | Time of max. val. (UTC), peak value positive, I L2
5672 | uint | RD/WR | _ILN_POS_PEAK_MAX_T[2] | s | Time of max. val. (UTC), peak value positive, I L3
5674 | uint | RD/WR | _ILN_POS_PEAK_MAX_T[3] | s | Time of max. val. (UTC), peak value positive, I L4
5676 | uint | RD/WR | _ILN_PEAK_PEAK_MAX_T[0] | s | Time of max. val. (UTC), peak-peak value, I L1
5678 | uint | RD/WR | _ILN_PEAK_PEAK_MAX_T[1] | s | Time of max. val. (UTC), peak-peak value, I L2
5680 | uint | RD/WR | _ILN_PEAK_PEAK_MAX_T[2] | s | Time of max. val. (UTC), peak-peak value, I L3
5682 | uint | RD/WR | _ILN_PEAK_PEAK_MAX_T[3] | s | Time of max. val. (UTC), peak-peak value, I L4
5684 | uint | RD/WR | _FLI_PF5_MAX_T[0] | s | Time of max. val. (UTC), current flicker Pf5, L1-N
5686 | uint | RD/WR | _FLI_PF5_MAX_T[1] | s | Time of max. val. (UTC), current flicker Pf5, L2-N
5688 | uint | RD/WR | _FLI_PF5_MAX_T[2] | s | Time of max. val. (UTC), current flicker Pf5, L3-N
5690 | uint | RD/WR | _FLI_PF5_MAX_T[3] | s | Time of max. val. (UTC), current flicker Pf5, L4-N
5692 | uint | RD/WR | _FLI_ST_MAX_T[0] | s
5694 | uint | RD/WR | _FLI_ST_MAX_T[1] | s
5696 | uint | RD/WR | _FLI_ST_MAX_T[2] | s
5698 | uint | RD/WR | _FLI_ST_MAX_T[3] | s
5700 | uint | RD/WR | _FLI_LT_MAX_T[0] | s
5702 | uint | RD/WR | _FLI_LT_MAX_T[1] | s
5704 | uint | RD/WR | _FLI_LT_MAX_T[2] | s
5706 | uint | RD/WR | _FLI_LT_MAX_T[3] | s
5708 | uint | RD/WR | _ILN_RC_MAX_T[0] | s | Time of max. val. (UTC), ripple control signal, I L1
5710 | uint | RD/WR | _ILN_RC_MAX_T[1] | s | Time of max. val. (UTC), ripple control signal, I L2
5712 | uint | RD/WR | _ILN_RC_MAX_T[2] | s | Time of max. val. (UTC), ripple control signal, I L3
5714 | uint | RD/WR | _ILN_RC_MAX_T[3] | s | Time of max. val. (UTC), ripple control signal, I L4
5716 | uint | RD/WR | _ULL_RC_MAX_T[0] | s | Time of max. val. (UTC), ripple control signal, U L1-L2
5718 | uint | RD/WR | _ULL_RC_MAX_T[1] | s | Time of max. val. (UTC), ripple control signal, U L2-L3
5720 | uint | RD/WR | _ULL_RC_MAX_T[2] | s | Time of max. val. (UTC), ripple control signal, U L3-L1
5732 | uint | RD/WR | _PFLN_MAX_T[0] | s | Time of max. val. (UTC), power factor; L1
5734 | uint | RD/WR | _PFLN_MAX_T[1] | s | Time of max. val. (UTC), power factor; L2
5736 | uint | RD/WR | _PFLN_MAX_T[2] | s | Time of max. val. (UTC), power factor; L3
5738 | uint | RD/WR | _PFLN_MAX_T[3] | s | Time of max. val. (UTC), power factor; L4
5740 | uint | RD/WR | _DLN_MAX_T[0] | s | Time of max. val. (UTC), distortion power factor; L1
5742 | uint | RD/WR | _DLN_MAX_T[1] | s | Time of max. val. (UTC), distortion power factor; L2
5744 | uint | RD/WR | _DLN_MAX_T[2] | s | Time of max. val. (UTC), distortion power factor; L3
5746 | uint | RD/WR | _DLN_MAX_T[3] | s | Time of max. val. (UTC), distortion power factor; L4
5748 | uint | RD/WR | _KFACT_MAX_T[0] | s | Time of max. val. (UTC), K-Factor, L1
5750 | uint | RD/WR | _KFACT_MAX_T[1] | s | Time of max. val. (UTC), K-Factor, L2
5752 | uint | RD/WR | _KFACT_MAX_T[2] | s | Time of max. val. (UTC), K-Factor, L3
5754 | uint | RD/WR | _KFACT_MAX_T[3] | s | Time of max. val. (UTC), K-Factor, L4
5756 | uint | RD/WR | _S0_POWER_MAX_T[0] | s | Time of max. val. (UTC), Input 1, measured value
5758 | uint | RD/WR | _S0_POWER_MAX_T[1] | s | Time of max. val. (UTC), Input 2, measured value
5760 | uint | RD/WR | _TEMPERATUR_MAX_T | s | Time of max. val. (UTC), internal temperature
Maximum values of mean values (float type)
Address | Format | RD/WR | Designation | Unit | Note
5762 | float | RD/WR | _ULN_AVG_MAX[0] | V | Max. values of mean val. U L1-N
5764 | float | RD/WR | _ULN_AVG_MAX[1] | V | Max. values of mean val. U L2-N
5766 | float | RD/WR | _ULN_AVG_MAX[2] | V | Max. values of mean val. U L3-N
5768 | float | RD/WR | _ULN_AVG_MAX[3] | V | Max. values of mean val. U L4-N
5770 | float | RD/WR | _ULL_AVG_MAX[0] | V | Max. values of mean val. U L1-L2
5772 | float | RD/WR | _ULL_AVG_MAX[1] | V | Max. values of mean val. U L2-L3
5774 | float | RD/WR | _ULL_AVG_MAX[2] | V | Max. values of mean val. U L3-L1
5776 | float | RD/WR | _ULN_CF_AVG_MAX[0] |  | Max. values of mean val., crest factor, U L1-N
5778 | float | RD/WR | _ULN_CF_AVG_MAX[1] |  | Max. values of mean val., crest factor, U L2-N
5780 | float | RD/WR | _ULN_CF_AVG_MAX[2] |  | Max. values of mean val., crest factor, U L3-N
5782 | float | RD/WR | _ULN_CF_AVG_MAX[3] |  | Max. values of mean val., crest factor, U L4-N
5784 | float | RD/WR | _ULL_CF_AVG_MAX[0] |  | Max. values of mean val., crest factor, U L1-L2
5786 | float | RD/WR | _ULL_CF_AVG_MAX[1] |  | Max. values of mean val., crest factor, U L2-L3
5788 | float | RD/WR | _ULL_CF_AVG_MAX[2] |  | Max. values of mean val., crest factor, U L3-L1
5790 | float | RD/WR | _UN_AVG_MAX | V | Max. values of mean val., zero sequence
5792 | float | RD/WR | _UM_AVG_MAX | V | Max. values of mean val., positive sequence
5794 | float | RD/WR | _UG_AVG_MAX | V | Max. values of mean val., negative sequence
5796 | float | RD/WR | _URC_AVG_MAX[0] | V | Max. values of mean val., ripple control signal, U L1-N
5798 | float | RD/WR | _URC_AVG_MAX[1] | V | Max. values of mean val., ripple control signal, U L2-N
5800 | float | RD/WR | _URC_AVG_MAX[2] | V | Max. values of mean val., ripple control signal, U L3-N
5802 | float | RD/WR | _URC_AVG_MAX[3] | V | Max. values of mean val., ripple control signal, U L4-N
5804 | float | RD/WR | _THD_ULN_AVG_MAX[0] | % | Max. values of mean val., harmonics, THD, U L1-N
5806 | float | RD/WR | _THD_ULN_AVG_MAX[1] | % | Max. values of mean val., harmonics, THD, U L2-N
5808 | float | RD/WR | _THD_ULN_AVG_MAX[2] | % | Max. values of mean val., harmonics, THD, U L3-N
5810 | float | RD/WR | _THD_ULN_AVG_MAX[3] | % | Max. values of mean val., harmonics, THD, U L4-N
5812 | float | RD/WR | _THD_ZLN_AVG_MAX[0] | % | Max. values of mean val., interharmonics, ZHD, U, L1
5814 | float | RD/WR | _THD_ZLN_AVG_MAX[1] | % | Max. values of mean val., interharmonics, ZHD, U, L2
5816 | float | RD/WR | _THD_ZLN_AVG_MAX[2] | % | Max. values of mean val., interharmonics, ZHD, U, L3
5818 | float | RD/WR | _THD_ZLN_AVG_MAX[3] | % | Max. values of mean val., interharmonics, ZHD, U, L4
5820 | float | RD/WR | _ULN_OVER_AVG_MAX[0] | % | Max. values of mean val., over difference, U L1
5822 | float | RD/WR | _ULN_OVER_AVG_MAX[1] | % | Max. values of mean val., over difference, U L2
5824 | float | RD/WR | _ULN_OVER_AVG_MAX[2] | % | Max. values of mean val., over difference, U L3
5826 | float | RD/WR | _ULN_OVER_AVG_MAX[3] | % | Max. values of mean val., over difference, U L4
5828 | float | RD/WR | _ULN_UNDER_AVG_MAX[0] | % | Max. values of mean val., under difference, U L1
5830 | float | RD/WR | _ULN_UNDER_AVG_MAX[1] | % | Max. values of mean val., under difference, U L2
5832 | float | RD/WR | _ULN_UNDER_AVG_MAX[2] | % | Max. values of mean val., under difference, U L3
5834 | float | RD/WR | _ULN_UNDER_AVG_MAX[3] | % | Max. values of mean val., under difference, U L4
5836 | float | RD/WR | _ULN_NEG_PEAK_AVG_MAX[0] | V | Max. values of mean val., peak value negative, U L1-N
5838 | float | RD/WR | _ULN_NEG_PEAK_AVG_MAX[1] | V | Max. values of mean val., peak value negative, U L2-N
5840 | float | RD/WR | _ULN_NEG_PEAK_AVG_MAX[2] | V | Max. values of mean val., peak value negative, U L3-N
5842 | float | RD/WR | _ULN_NEG_PEAK_AVG_MAX[3] | V | Max. values of mean val., peak value negative, U L4-N
5844 | float | RD/WR | _ULN_POS_PEAK_AVG_MAX[0] | V | Max. values of mean val., peak value positive, U L1-N
5846 | float | RD/WR | _ULN_POS_PEAK_AVG_MAX[1] | V | Max. values of mean val., peak value positive, U L2-N
5848 | float | RD/WR | _ULN_POS_PEAK_AVG_MAX[2] | V | Max. values of mean val., peak value positive, U L3-N
5850 | float | RD/WR | _ULN_POS_PEAK_AVG_MAX[3] | V | Max. values of mean val., peak value positive, U L4-N
5852 | float | RD/WR | _ULN_PEAK_PEAK_AVG_MAX[0] | V | Max. values of mean val., peak-peak value, U L1-N
5854 | float | RD/WR | _ULN_PEAK_PEAK_AVG_MAX[1] | V | Max. values of mean val., peak-peak value, U L2-N
5856 | float | RD/WR | _ULN_PEAK_PEAK_AVG_MAX[2] | V | Max. values of mean val., peak-peak value, U L3-N
5858 | float | RD/WR | _ULN_PEAK_PEAK_AVG_MAX[3] | V | Max. values of mean val., peak-peak value, U L4-N
5860 | float | RD/WR | _THD_ULL_AVG_MAX[0] | % | Max. values of mean val., harmonic, THD,U L1-L2
5862 | float | RD/WR | _THD_ULL_AVG_MAX[1] | % | Max. values of mean val., harmonic, THD,U L2-L3
5864 | float | RD/WR | _THD_ULL_AVG_MAX[2] | % | Max. values of mean val., harmonic, THD,U L3-L1
5866 | float | RD/WR | _THD_ZLL_AVG_MAX[0] | % | Max. values of mean val., interharmonics, U L1-L2
5868 | float | RD/WR | _THD_ZLL_AVG_MAX[1] | % | Max. values of mean val., interharmonics, U L2-L3
5870 | float | RD/WR | _THD_ZLL_AVG_MAX[2] | % | Max. values of mean val., interharmonics, U L3-L1
5872 | float | RD/WR | _ULL_OVER_AVG_MAX[0] | % | Max. values of mean val., over difference, U L1-L2
5874 | float | RD/WR | _ULL_OVER_AVG_MAX[1] | % | Max. values of mean val., over difference, U L2-L3
5876 | float | RD/WR | _ULL_OVER_AVG_MAX[2] | % | Max. values of mean val., over difference, U L3-L1
5878 | float | RD/WR | _ULL_UNDER_AVG_MAX[0] | % | Max. values of mean val., under difference, U L1-L2
5880 | float | RD/WR | _ULL_UNDER_AVG_MAX[1] | % | Max. values of mean val., under difference, U L2-L3
5882 | float | RD/WR | _ULL_UNDER_AVG_MAX[2] | % | Max. values of mean val., under difference, U L3-L1
5884 | float | RD/WR | _ULL_NEG_PEAK_AVG_MAX[0] | V | Max. values of mean val., peak value negative, U L1-L2
5886 | float | RD/WR | _ULL_NEG_PEAK_AVG_MAX[1] | V | Max. values of mean val., peak value negative, U L2-L3
5888 | float | RD/WR | _ULL_NEG_PEAK_AVG_MAX[2] | V | Max. values of mean val., peak value negative, U L2-L3
5890 | float | RD/WR | _ULL_POS_PEAK_AVG_MAX[0] | V | Max. values of mean val., peak value positive, U L1-L2
5892 | float | RD/WR | _ULL_POS_PEAK_AVG_MAX[1] | V | Max. values of mean val., peak value positive, U L2-L3
5894 | float | RD/WR | _ULL_POS_PEAK_AVG_MAX[2] | V | Max. values of mean val., peak value positive, U L3-L1
5896 | float | RD/WR | _ULL_PEAK_PEAK_AVG_MAX[0] | V | Max. values of mean val., peak-peak value, U L1-L2
5898 | float | RD/WR | _ULL_PEAK_PEAK_AVG_MAX[1] | V | Max. values of mean val., peak-peak value, U L2-L3
5900 | float | RD/WR | _ULL_PEAK_PEAK_AVG_MAX[2] | V | Max. values of mean val., peak-peak value, U L3-L1
5902 | float | RD/WR | _U_STERN_AVG_MAX | V
5904 | float | RD/WR | _U_SYM_AVG_MAX | % | Max. values of mean val., unsymmetrical voltage
5906 | float | RD/WR | _FREQ_AVG_MAX | Hz | Max. values of mean val., measured frequency
5908 | float | RD/WR | _NORM_FREQ_AVG_MAX | Hz | Max. values of mean val., nominal frequency
5910 | float | RD/WR | _PLN_AVG_MAX[0] | W | Max. values of mean val., real power L1
5912 | float | RD/WR | _PLN_AVG_MAX[1] | W | Max. values of mean val., real power L2
5914 | float | RD/WR | _PLN_AVG_MAX[2] | W | Max. values of mean val., real power L3
5916 | float | RD/WR | _PLN_AVG_MAX[3] | W | Max. values of mean val., real power L4
5918 | float | RD/WR | _P_SUM_AVG_MAX | W | Max. values of mean val., sum P = P1 + P2 + P3 + P4
5920 | float | RD/WR | _Q_SUM_AVG_MAX | var | Max. values of mean val., sum Q = Q1 + Q2 + Q3 + Q4
5922 | float | RD/WR | _QLN_AVG_MAX[0] | var | Max. values of mean val., reactive power L1
5924 | float | RD/WR | _QLN_AVG_MAX[1] | var | Max. values of mean val., reactive power L2
5926 | float | RD/WR | _QLN_AVG_MAX[2] | var | Max. values of mean val., reactive power L3
5928 | float | RD/WR | _QLN_AVG_MAX[3] | var | Max. values of mean val., reactive power L4
5930 | float | RD/WR | _P_SUM3_AVG_MAX | W | Max. values of mean val., sum P = P1 + P2 + P3
5932 | float | RD/WR | _Q_SUM3_AVG_MAX | var | Max. values of mean val., sum Q = Q1 + Q2 + Q3
5934 | float | RD/WR | _ILN_AVG_MAX[0] | A | Max. values of mean val., apparent current, L1
5936 | float | RD/WR | _ILN_AVG_MAX[1] | A | Max. values of mean val., apparent current, L2
5938 | float | RD/WR | _ILN_AVG_MAX[2] | A | Max. values of mean val., apparent current, L3
5940 | float | RD/WR | _ILN_AVG_MAX[3] | A | Max. values of mean val., apparent current, L4
5942 | float | RD/WR | _SLN_AVG_MAX[0] | VA | Max. values of mean val., apparent power L1
5944 | float | RD/WR | _SLN_AVG_MAX[1] | VA | Max. values of mean val., apparent power L2
5946 | float | RD/WR | _SLN_AVG_MAX[2] | VA | Max. values of mean val., apparent power L3
5948 | float | RD/WR | _SLN_AVG_MAX[3] | VA | Max. values of mean val., apparent power L4
5950 | float | RD/WR | _I_SUM3_AVG_MAX | A | Max. values of mean val., vector sum; IN = I1 + I2 + I3
5952 | float | RD/WR | _I_SUM_AVG_MAX | A | Max. values of mean val., vector sum; I1 + I2 + I3 + I4
5954 | float | RD/WR | _S_SUM3_AVG_MAX | VA | Max. values of mean val., sum S = S1 + S2 + S3
5956 | float | RD/WR | _S_SUM_AVG_MAX | VA | Max. values of mean val., sum S = S1 + S2 + S3 + S4
5958 | float | RD/WR | _THD_IL_AVG_MAX[0] | % | Max. values of mean val., harmonic, THD, I L1
5960 | float | RD/WR | _THD_IL_AVG_MAX[1] | % | Max. values of mean val., harmonic, THD, I L2
5962 | float | RD/WR | _THD_IL_AVG_MAX[2] | % | Max. values of mean val., harmonic, THD, I L3
5964 | float | RD/WR | _THD_IL_AVG_MAX[3] | % | Max. values of mean val., harmonic, THD, I L4
5966 | float | RD/WR | _ZHD_IL_AVG_MAX[0] | % | Max. values of mean val., interharmonics, ZHD, I, L1
5968 | float | RD/WR | _ZHD_IL_AVG_MAX[1] | % | Max. values of mean val., interharmonics, ZHD, I, L2
5970 | float | RD/WR | _ZHD_IL_AVG_MAX[2] | % | Max. values of mean val., interharmonics, ZHD, I, L3
5972 | float | RD/WR | _ZHD_IL_AVG_MAX[3] | % | Max. values of mean val., interharmonics, ZHD, I, L4
5974 | float | RD/WR | _ILN_CF_AVG_MAX[0] |  | Max. values of mean val., crest factor, I L1
5976 | float | RD/WR | _ILN_CF_AVG_MAX[1] |  | Max. values of mean val., crest factor, I L2
5978 | float | RD/WR | _ILN_CF_AVG_MAX[2] |  | Max. values of mean val., crest factor, I L3
5980 | float | RD/WR | _ILN_CF_AVG_MAX[3] |  | Max. values of mean val., crest factor, I L4
5982 | float | RD/WR | _IN_AVG_MAX | A | Max. values of mean val., zero sequence, current
5984 | float | RD/WR | _IM_AVG_MAX | A | Max. values of mean val., positive sequence, current
5986 | float | RD/WR | _IG_AVG_MAX | A | Max. values of mean val., negative sequence, current
5988 | float | RD/WR | _I_SYM_AVG_MAX | % | Max. values of mean val., unsymmetrical; current
5990 | float | RD/WR | _ILN_OVER_AVG_MAX[0] | % | Max. values of mean val., over difference, I L1
5992 | float | RD/WR | _ILN_OVER_AVG_MAX[1] | % | Max. values of mean val., over difference, I L2
5994 | float | RD/WR | _ILN_OVER_AVG_MAX[2] | % | Max. values of mean val., over difference, I L3
5996 | float | RD/WR | _ILN_OVER_AVG_MAX[3] | % | Max. values of mean val., over difference, I L4
5998 | float | RD/WR | _ILN_UNDER_AVG_MAX[0] | % | Max. values of mean val., under difference, I L1
6000 | float | RD/WR | _ILN_UNDER_AVG_MAX[1] | % | Max. values of mean val., under difference, I L2
6002 | float | RD/WR | _ILN_UNDER_AVG_MAX[2] | % | Max. values of mean val., under difference, I L3
6004 | float | RD/WR | _ILN_UNDER_AVG_MAX[3] | % | Max. values of mean val., under difference, I L4
6006 | float | RD/WR | _ILN_NEG_PEAK_AVG_MAX[0] | A | Max. values of mean val., peak value negative, I L1
6008 | float | RD/WR | _ILN_NEG_PEAK_AVG_MAX[1] | A | Max. values of mean val., peak value negative, I L2
6010 | float | RD/WR | _ILN_NEG_PEAK_AVG_MAX[2] | A | Max. values of mean val., peak value negative, I L3
6012 | float | RD/WR | _ILN_NEG_PEAK_AVG_MAX[3] | A | Max. values of mean val., peak value negative, I L4
6014 | float | RD/WR | _ILN_POS_PEAK_AVG_MAX[0] | A | Max. values of mean val., peak value positive, I L1
6016 | float | RD/WR | _ILN_POS_PEAK_AVG_MAX[1] | A | Max. values of mean val., peak value positive, I L2
6018 | float | RD/WR | _ILN_POS_PEAK_AVG_MAX[2] | A | Max. values of mean val., peak value positive, I L3
6020 | float | RD/WR | _ILN_POS_PEAK_AVG_MAX[3] | A | Max. values of mean val., peak value positive, I L4
6022 | float | RD/WR | _ILN_PEAK_PEAK_AVG_MAX[0] | A | Max. values of mean val., peak-peak value, I L1
6024 | float | RD/WR | _ILN_PEAK_PEAK_AVG_MAX[1] | A | Max. values of mean val., peak-peak value, I L2
6026 | float | RD/WR | _ILN_PEAK_PEAK_AVG_MAX[2] | A | Max. values of mean val., peak-peak value, I L3
6028 | float | RD/WR | _ILN_PEAK_PEAK_AVG_MAX[3] | A | Max. values of mean val., peak-peak value, I L4
6030 | float | RD/WR | _FLI_PF5_AVG_MAX[0] |  | Max. values of mean val., current flicker Pf5, L1-N
6032 | float | RD/WR | _FLI_PF5_AVG_MAX[1] |  | Max. values of mean val., current flicker Pf5, L2-N
6034 | float | RD/WR | _FLI_PF5_AVG_MAX[2] |  | Max. values of mean val., current flicker Pf5, L3-N
6036 | float | RD/WR | _FLI_PF5_AVG_MAX[3] |  | Max. values of mean val., current flicker Pf5, L4-N
6038 | float | RD/WR | _FLI_ST_AVG_MAX[0]
6040 | float | RD/WR | _FLI_ST_AVG_MAX[1]
6042 | float | RD/WR | _FLI_ST_AVG_MAX[2]
6044 | float | RD/WR | _FLI_ST_AVG_MAX[3]
6046 | float | RD/WR | _FLI_LT_AVG_MAX[0]
6048 | float | RD/WR | _FLI_LT_AVG_MAX[1]
6050 | float | RD/WR | _FLI_LT_AVG_MAX[2]
6052 | float | RD/WR | _FLI_LT_AVG_MAX[3]
6054 | float | RD/WR | _ILN_RC_AVG_MAX[0] | A | Max. values of mean val., ripple control signal, I L1
6056 | float | RD/WR | _ILN_RC_AVG_MAX[1] | A | Max. values of mean val., ripple control signal, I L2
6058 | float | RD/WR | _ILN_RC_AVG_MAX[2] | A | Max. values of mean val., ripple control signal, I L3
6060 | float | RD/WR | _ILN_RC_AVG_MAX[3] | A | Max. values of mean val., ripple control signal, I L4
6062 | float | RD/WR | _ULL_RC_AVG_MAX[0] | V | Max. values of mean val., ripple control signal, U L1-L2
6064 | float | RD/WR | _ULL_RC_AVG_MAX[1] | V | Max. values of mean val., ripple control signal, U L2-L3
6066 | float | RD/WR | _ULL_RC_AVG_MAX[2] | V | Max. values of mean val., ripple control signal, U L3-L1
6078 | float | RD/WR | _PFLN_AVG_MAX[0] | % | Max. values of mean val., power factor; L1
6080 | float | RD/WR | _PFLN_AVG_MAX[1] | % | Max. values of mean val., power factor; L2
6082 | float | RD/WR | _PFLN_AVG_MAX[2] | % | Max. values of mean val., power factor; L3
6084 | float | RD/WR | _PFLN_AVG_MAX[3] | % | Max. values of mean val., power factor; L4
6086 | float | RD/WR | _DLN_AVG_MAX[0] | var | Max. values of mean val., distortion power factor; L1
6088 | float | RD/WR | _DLN_AVG_MAX[1] | var | Max. values of mean val., distortion power factor; L2
6090 | float | RD/WR | _DLN_AVG_MAX[2] | var | Max. values of mean val., distortion power factor; L3
6092 | float | RD/WR | _DLN_AVG_MAX[3] | var | Max. values of mean val., distortion power factor; L4
6094 | float | RD/WR | _KFACT_AVG_MAX[0] |  | Max. values of mean val., K-Factor, L1
6096 | float | RD/WR | _KFACT_AVG_MAX[1] |  | Max. values of mean val., K-Factor, L2
6098 | float | RD/WR | _KFACT_AVG_MAX[2] |  | Max. values of mean val., K-Factor, L3
6100 | float | RD/WR | _KFACT_AVG_MAX[3] |  | Max. values of mean val., K-Factor, L4
6102 | float | RD/WR | _S0_POWER_AVG_MAX[0] | W | Max. values of mean val., Input 1, measured value
6104 | float | RD/WR | _S0_POWER_AVG_MAX[1] | W | Max. values of mean val., Input 1, measured value
6106 | float | RD/WR | _TEMPERATUR_AVG_MAX | °C | Max. values of mean val., internal temperature
Maximum values of mean values, time stamp (uint type)
Address | Format | RD/WR | Designation | Unit | Note (Time: UTC)
6108 | uint | RD/WR | _THD_ULN_AVG_MAX_T[0] | s | Time of max. val. of mean val., THD, U L1
6110 | uint | RD/WR | _THD_ULN_AVG_MAX_T[1] | s | Time of max. val. of mean val., THD, U L2
6112 | uint | RD/WR | _THD_ULN_AVG_MAX_T[2] | s | Time of max. val. of mean val., THD, U L3
6114 | uint | RD/WR | _THD_ULN_AVG_MAX_T[3] | s | Time of max. val. of mean val., THD, U L4
6116 | uint | RD/WR | _ULN_AVG_MAX_T[0] | s | Time of max. val. of mean val., U L1-N
6118 | uint | RD/WR | _ULN_AVG_MAX_T[1] | s | Time of max. val. of mean val., U L2-N
6120 | uint | RD/WR | _ULN_AVG_MAX_T[2] | s | Time of max. val. of mean val., U L3-N
6122 | uint | RD/WR | _ULN_AVG_MAX_T[3] | s | Time of max. val. of mean val., U L4-N
6124 | uint | RD/WR | _ULL_AVG_MAX_T[0] | s | Time of max. val. of mean val., U L1-L2
6126 | uint | RD/WR | _ULL_AVG_MAX_T[1] | s | Time of max. val. of mean val., U L2-L3
6128 | uint | RD/WR | _ULL_AVG_MAX_T[2] | s | Time of max. val. of mean val., U L3-L1
6130 | uint | RD/WR | _ULN_CF_AVG_MAX_T[0] | s | Time of max. val. of mean val., crest factor, U L1-N
6132 | uint | RD/WR | _ULN_CF_AVG_MAX_T[1] | s | Time of max. val. of mean val., crest factor, U L2-N
6134 | uint | RD/WR | _ULN_CF_AVG_MAX_T[2] | s | Time of max. val. of mean val., crest factor, U L3-N
6136 | uint | RD/WR | _ULN_CF_AVG_MAX_T[3] | s | Time of max. val. of mean val., crest factor, U L4-N
6138 | uint | RD/WR | _ULL_CF_AVG_MAX_T[0] | s | Time of max. val. of mean val., crest factor, U L1-L2
6140 | uint | RD/WR | _ULL_CF_AVG_MAX_T[1] | s | Time of max. val. of mean val., crest factor, U L2-L3
6142 | uint | RD/WR | _ULL_CF_AVG_MAX_T[2] | s | Time of max. val. of mean val., crest factor, U L3-L1
6144 | uint | RD/WR | _UN_AVG_MAX_T | s | Time of max. val. of mean val., zero sequence
6146 | uint | RD/WR | _UM_AVG_MAX_T | s | Time of max. val. of mean val., positive sequence
6148 | uint | RD/WR | _UG_AVG_MAX_T | s | Time of max. val. of mean val., negative sequence
6150 | uint | RD/WR | _URC_AVG_MAX_T[0] | s | Time of max. val. of mean val., ripple control signal, U L1-N
6152 | uint | RD/WR | _URC_AVG_MAX_T[1] | s | Time of max. val. of mean val., ripple control signal, U L2-N
6154 | uint | RD/WR | _URC_AVG_MAX_T[2] | s | Time of max. val. of mean val., ripple control signal, U L3-N
6156 | uint | RD/WR | _URC_AVG_MAX_T[3] | s | Time of max. val. of mean val., ripple control signal, U L4-N
6158 | uint | RD/WR | _THD_ULN_AVG_MAX_T[0] | s | Time of max. val. of mean val., harmonics, THD, U L1-N
6160 | uint | RD/WR | _THD_ULN_AVG_MAX_T[1] | s | Time of max. val. of mean val., harmonics THD, U L2-N
6162 | uint | RD/WR | _THD_ULN_AVG_MAX_T[2] | s | Time of max. val. of mean val., harmonics THD, U L3-N
6164 | uint | RD/WR | _THD_ULN_AVG_MAX_T[3] | s | Time of max. val. of mean val., harmonics THD, U L4-N
6166 | uint | RD/WR | _THD_ZLN_AVG_MAX_T[0] | s | Time of max. val. of mean val., interharmonics, ZHD, U, L1
6168 | uint | RD/WR | _THD_ZLN_AVG_MAX_T[1] | s | Time of max. val. of mean val., interharmonics, ZHD, U, L2
6170 | uint | RD/WR | _THD_ZLN_AVG_MAX_T[2] | s | Time of max. val. of mean val., interharmonics, ZHD, U, L3
6172 | uint | RD/WR | _THD_ZLN_AVG_MAX_T[3] | s | Time of max. val. of mean val., interharmonics, ZHD, U, L4
6174 | uint | RD/WR | _ULN_OVER_AVG_MAX_T[0] | s | Time of max. val. of mean val., over difference, U L1
6176 | uint | RD/WR | _ULN_OVER_AVG_MAX_T[1] | s | Time of max. val. of mean val., over difference, U L2
6178 | uint | RD/WR | _ULN_OVER_AVG_MAX_T[2] | s | Time of max. val. of mean val., over difference, U L3
6180 | uint | RD/WR | _ULN_OVER_AVG_MAX_T[3] | s | Time of max. val. of mean val., over difference, U L4
6182 | uint | RD/WR | _ULN_UNDER_AVG_MAX_T[0] | s | Time of max. val. of mean val., under difference, U L1
6184 | uint | RD/WR | _ULN_UNDER_AVG_MAX_T[1] | s | Time of max. val. of mean val., under difference, U L2
6186 | uint | RD/WR | _ULN_UNDER_AVG_MAX_T[2] | s | Time of max. val. of mean val., under difference, U L3
6188 | uint | RD/WR | _ULN_UNDER_AVG_MAX_T[3] | s | Time of max. val. of mean val., under difference, U L4
6190 | uint | RD/WR | _ULN_NEG_PEAK_AVG_MAX_T[0] | s | Time of max. val. of mean val., peak val. negative, U L1
6192 | uint | RD/WR | _ULN_NEG_PEAK_AVG_MAX_T[1] | s | Time of max. val. of mean val., peak val. negative, U L2
6194 | uint | RD/WR | _ULN_NEG_PEAK_AVG_MAX_T[2] | s | Time of max. val. of mean val., peak val. negative, U L3
6196 | uint | RD/WR | _ULN_NEG_PEAK_AVG_MAX_T[3] | s | Time of max. val. of mean val., peak val. negative, U L4
6198 | uint | RD/WR | _ULN_POS_PEAK_AVG_MAX_T[0] | s | Time of max. val. of mean val., peak val. positive, U L1
6200 | uint | RD/WR | _ULN_POS_PEAK_AVG_MAX_T[1] | s | Time of max. val. of mean val., peak val. positive, U L2
6202 | uint | RD/WR | _ULN_POS_PEAK_AVG_MAX_T[2] | s | Time of max. val. of mean val., peak val. positive, U L3
6204 | uint | RD/WR | _ULN_POS_PEAK_AVG_MAX_T[3] | s | Time of max. val. of mean val., peak val. positive, U L4
6206 | uint | RD/WR | _ULN_PEAK_PEAK_AVG_MAX_T[0] | s | Time of max. val. of mean val., peak-peak value, U L1
6208 | uint | RD/WR | _ULN_PEAK_PEAK_AVG_MAX_T[1] | s | Time of max. val. of mean val., peak-peak value, U L2
6210 | uint | RD/WR | _ULN_PEAK_PEAK_AVG_MAX_T[2] | s | Time of max. val. of mean val., peak-peak value, U L3
6212 | uint | RD/WR | _ULN_PEAK_PEAK_AVG_MAX_T[3] | s | Time of max. val. of mean val., peak-peak value, U L4
6214 | uint | RD/WR | _THD_ULL_AVG_MAX_T[0] | s | Time of max. val. of mean val., THD, U L1-L2
6216 | uint | RD/WR | _THD_ULL_AVG_MAX_T[1] | s | Time of max. val. of mean val., THD, U L2-L3
6218 | uint | RD/WR | _THD_ULL_AVG_MAX_T[2] | s | Time of max. val. of mean val., THD, U L3-L1
6220 | uint | RD/WR | _THD_ZLL_AVG_MAX_T[0] | s | Time of max. val. of mean val., ZHD, U L1-L2
6222 | uint | RD/WR | _THD_ZLL_AVG_MAX_T[1] | s | Time of max. val. of mean val., ZHD, U L2-L3
6224 | uint | RD/WR | _THD_ZLL_AVG_MAX_T[2] | s | Time of max. val. of mean val., ZHD, U L3-L1
6226 | uint | RD/WR | _ULL_OVER_AVG_MAX_T[0] | s | Time of max. val. of mean val., over difference, U L1-L2
6228 | uint | RD/WR | _ULL_OVER_AVG_MAX_T[1] | s | Time of max. val. of mean val., over difference, U L2-L3
6230 | uint | RD/WR | _ULL_OVER_AVG_MAX_T[2] | s | Time of max. val. of mean val., over difference, U L3-L1
6232 | uint | RD/WR | _ULL_UNDER_AVG_MAX_T[0] | s | Time of max. val. of mean val., under difference, U L1-L2
6234 | uint | RD/WR | _ULL_UNDER_AVG_MAX_T[1] | s | Time of max. val. of mean val., under difference, U L2-L3
6236 | uint | RD/WR | _ULL_UNDER_AVG_MAX_T[2] | s | Time of max. val. of mean val., under difference, U L3-L1
6238 | uint | RD/WR | _ULL_NEG_PEAK_AVG_MAX_T[0] | s | Time of max. val. of mean val., peak value neg. U L1-L2
6240 | uint | RD/WR | _ULL_NEG_PEAK_AVG_MAX_T[1] | s | Time of max. val. of mean val., peak value neg., U L2-L3
6242 | uint | RD/WR | _ULL_NEG_PEAK_AVG_MAX_T[2] | s | Time of max. val. of mean val., peak value neg, U L3-L1
6244 | uint | RD/WR | _ULL_POS_PEAK_AVG_MAX_T[0] | s | Time of max. val. of mean val., peak value pos., U L1-L2
6246 | uint | RD/WR | _ULL_POS_PEAK_AVG_MAX_T[1] | s | Time of max. val. of mean val., peak value pos., U L2-L3
6248 | uint | RD/WR | _ULL_POS_PEAK_AVG_MAX_T[2] | s | Time of max. val. of mean val., peak value pos., U L3-L1
6250 | uint | RD/WR | _ULL_PEAK_PEAK_AVG_MAX_T[0] | s | Time of max. val. of mean val., peak-peak value, U L1-L2
6252 | uint | RD/WR | _ULL_PEAK_PEAK_AVG_MAX_T[1] | s | Time of max. val. of mean val., peak-peak value, U L2-L3
6254 | uint | RD/WR | _ULL_PEAK_PEAK_AVG_MAX_T[2] | s | Time of max. val. of mean val., peak-peak value, U L3-L1
6256 | uint | RD/WR | _U_STERN_AVG_MAX_T | s
6258 | uint | RD/WR | _U_SYM_AVG_MAX_T | s | Time of max. val. of mean val., unsymmetrical voltage
6260 | uint | RD/WR | _FREQ_AVG_MAX_T | s | Time of max. val. of mean val., measured frequency
6262 | uint | RD/WR | _NORM_FREQ_AVG_MAX_T | s | Time of max. val. of mean val., nominal frequency
6264 | uint | RD/WR | _PLN_AVG_MAX_T[0] | s | Time of max. val. of mean val., real power L1
6266 | uint | RD/WR | _PLN_AVG_MAX_T[1] | s | Time of max. val. of mean val., real power L2
6268 | uint | RD/WR | _PLN_AVG_MAX_T[2] | s | Time of max. val. of mean val., real power L3
6270 | uint | RD/WR | _PLN_AVG_MAX_T[3] | s | Time of max. val. of mean val., real power L4
6272 | uint | RD/WR | _P_SUM_AVG_MAX_T | s | Time of max. val. of mean val., sum P = P1+P2+P3+P4
6274 | uint | RD/WR | _Q_SUM_AVG_MAX_T | s | Time of max. val. of mean val., sum Q = Q1+Q2+Q3+Q4
6276 | uint | RD/WR | _QLN_AVG_MAX_T[0] | s | Time of max. val. of mean val., reactive power L1
6278 | uint | RD/WR | _QLN_AVG_MAX_T[1] | s | Time of max. val. of mean val., reactive power L2
6280 | uint | RD/WR | _QLN_AVG_MAX_T[2] | s | Time of max. val. of mean val., reactive power L3
6282 | uint | RD/WR | _QLN_AVG_MAX_T[3] | s | Time of max. val. of mean val., reactive power L4
6284 | uint | RD/WR | _P_SUM3_AVG_MAX_T | s | Time of max. val. of mean val., sum P = P1+P2+P3
6286 | uint | RD/WR | _Q_SUM3_AVG_MAX_T | s | Time of max. val. of mean val., sum Q = Q1+Q2+Q3+Q4
6288 | uint | RD/WR | _ILN_AVG_MAX_T[0] | s | Time of max. val. of mean val., apparent current, L1
6290 | uint | RD/WR | _ILN_AVG_MAX_T[1] | s | Time of max. val. of mean val., apparent current, L2
6292 | uint | RD/WR | _ILN_AVG_MAX_T[2] | s | Time of max. val. of mean val., apparent current, L3
6294 | uint | RD/WR | _ILN_AVG_MAX_T[3] | s | Time of max. val. of mean val., apparent current, L4
6296 | uint | RD/WR | _SLN_AVG_MAX_T[0] | s | Time of max. val. of mean val., apparent power L1
6298 | uint | RD/WR | _SLN_AVG_MAX_T[1] | s | Time of max. val. of mean val., apparent power L2
6300 | uint | RD/WR | _SLN_AVG_MAX_T[2] | s | Time of max. val. of mean val., apparent power L3
6302 | uint | RD/WR | _SLN_AVG_MAX_T[3] | s | Time of max. val. of mean val., apparent power L4
6304 | uint | RD/WR | _I_SUM3_AVG_MAX_T | s | Time of max. val. of mean val., vector sum; IN = I1+I2+I3
6306 | uint | RD/WR | _I_SUM_AVG_MAX_T | s | Time of max. val. of mean val., vector sum; I1+I2+I3+I4
6308 | uint | RD/WR | _S_SUM3_AVG_MAX_T | s | Time of max. val. of mean val., sum S = S1+S2+S3
6310 | uint | RD/WR | _S_SUM_AVG_MAX_T | s | Time of max. val. of mean val., sum S = S1+S2+S3+S4
6312 | uint | RD/WR | _THD_IL_AVG_MAX_T[0] | s | Time of max. val. of mean val., harmonic, THD, I L1
6314 | uint | RD/WR | _THD_IL_AVG_MAX_T[1] | s | Time of max. val. of mean val., harmonic, THD, I L2
6316 | uint | RD/WR | _THD_IL_AVG_MAX_T[2] | s | Time of max. val. of mean val., harmonic, THD, I L3
6318 | uint | RD/WR | _THD_IL_AVG_MAX_T[3] | s | Time of max. val. of mean val., harmonic, THD, I L4
6320 | uint | RD/WR | _ZHD_IL_AVG_MAX_T[0] | s | Time of max. val. of mean val., interharmonic, ZHD, I L1
6322 | uint | RD/WR | _ZHD_IL_AVG_MAX_T[1] | s | Time of max. val. of mean val., interharmonic, ZHD, I L2
6324 | uint | RD/WR | _ZHD_IL_AVG_MAX_T[2] | s | Time of max. val. of mean val., interharmonic, ZHD, I L3
6326 | uint | RD/WR | _ZHD_IL_AVG_MAX_T[3] | s | Time of max. val. of mean val., interharmonic, ZHD, I L4
6328 | uint | RD/WR | _ILN_CF_AVG_MAX_T[0] | s | Time of max. val. of mean val., crest factor, I L1
6330 | uint | RD/WR | _ILN_CF_AVG_MAX_T[1] | s | Time of max. val. of mean val., crest factor, I L2
6332 | uint | RD/WR | _ILN_CF_AVG_MAX_T[2] | s | Time of max. val. of mean val., crest factor, I L3
6334 | uint | RD/WR | _ILN_CF_AVG_MAX_T[3] | s | Time of max. val. of mean val., crest factor, I L4
6336 | uint | RD/WR | _IN_AVG_MAX_T | s | Time of max. val. of mean val., zero sequence, current
6338 | uint | RD/WR | _IM_AVG_MAX_T | s | Time of max. val. of mean val., positive sequence, current
6340 | uint | RD/WR | _IG_AVG_MAX_T | s | Time of max. val. of mean val., negative sequence, current
6342 | uint | RD/WR | _I_SYM_AVG_MAX_T | s | Time of max. val. of mean val., unsymmetrical; current
6344 | uint | RD/WR | _ILN_OVER_AVG_MAX_T[0] | s | Time of max. val. of mean val., over difference, I L1
6346 | uint | RD/WR | _ILN_OVER_AVG_MAX_T[1] | s | Time of max. val. of mean val., over difference, I L2
6348 | uint | RD/WR | _ILN_OVER_AVG_MAX_T[2] | s | Time of max. val. of mean val., over difference, I L3
6350 | uint | RD/WR | _ILN_OVER_AVG_MAX_T[3] | s | Time of max. val. of mean val., over difference, I L4
6352 | uint | RD/WR | _ILN_UNDER_AVG_MAX_T[0] | s | Time of max. val. of mean val., under difference, I L1
6354 | uint | RD/WR | _ILN_UNDER_AVG_MAX_T[1] | s | Time of max. val. of mean val., under difference, I L2
6356 | uint | RD/WR | _ILN_UNDER_AVG_MAX_T[2] | s | Time of max. val. of mean val., under difference, I L3
6358 | uint | RD/WR | _ILN_UNDER_AVG_MAX_T[3] | s | Time of max. val. of mean val., under difference, I L4
6360 | uint | RD/WR | _ILN_NEG_PEAK_AVG_MAX_T[0] | s | Time of max. val. of mean val., peak value neg., I L1
6362 | uint | RD/WR | _ILN_NEG_PEAK_AVG_MAX_T[1] | s | Time of max. val. of mean val., peak value neg., I L2
6364 | uint | RD/WR | _ILN_NEG_PEAK_AVG_MAX_T[2] | s | Time of max. val. of mean val., peak value neg., I L3
6366 | uint | RD/WR | _ILN_NEG_PEAK_AVG_MAX_T[3] | s | Time of max. val. of mean val., peak value neg., I L4
6368 | uint | RD/WR | _ILN_POS_PEAK_AVG_MAX_T[0] | s | Time of max. val. of mean val., peak value pos., I L1
6370 | uint | RD/WR | _ILN_POS_PEAK_AVG_MAX_T[1] | s | Time of max. val. of mean val., peak value pos., I L2
6372 | uint | RD/WR | _ILN_POS_PEAK_AVG_MAX_T[2] | s | Time of max. val. of mean val., peak value pos., I L3
6374 | uint | RD/WR | _ILN_POS_PEAK_AVG_MAX_T[3] | s | Time of max. val. of mean val., peak value pos., I L4
6376 | uint | RD/WR | _ILN_PEAK_PEAK_AVG_MAX_T[0] | s | Time of max. val. of mean val., peak-peak value, I L1
6378 | uint | RD/WR | _ILN_PEAK_PEAK_AVG_MAX_T[1] | s | Time of max. val. of mean val., peak-peak value, I L2
6380 | uint | RD/WR | _ILN_PEAK_PEAK_AVG_MAX_T[2] | s | Time of max. val. of mean val., peak-peak value, I L3
6382 | uint | RD/WR | _ILN_PEAK_PEAK_AVG_MAX_T[3] | s | Time of max. val. of mean val., peak-peak value, I L4
6384 | uint | RD/WR | _FLI_PF5_AVG_MAX_T[0] | s | Time of max. val. of mean val., current flicker Pf5, L1-N
6386 | uint | RD/WR | _FLI_PF5_AVG_MAX_T[1] | s | Time of max. val. of mean val., current flicker Pf5, L2-N
6388 | uint | RD/WR | _FLI_PF5_AVG_MAX_T[2] | s | Time of max. val. of mean val., current flicker Pf5, L3-N
6390 | uint | RD/WR | _FLI_PF5_AVG_MAX_T[3] | s | Time of max. val. of mean val., current flicker Pf5, L4-N
6392 | uint | RD/WR | _FLI_ST_AVG_MAX_T[0] | s
6394 | uint | RD/WR | _FLI_ST_AVG_MAX_T[1] | s
6396 | uint | RD/WR | _FLI_ST_AVG_MAX_T[2] | s
6398 | uint | RD/WR | _FLI_ST_AVG_MAX_T[3] | s
6400 | uint | RD/WR | _FLI_LT_AVG_MAX_T[0] | s
6402 | uint | RD/WR | _FLI_LT_AVG_MAX_T[1] | s
6404 | uint | RD/WR | _FLI_LT_AVG_MAX_T[2] | s
6406 | uint | RD/WR | _FLI_LT_AVG_MAX_T[3] | s
6408 | uint | RD/WR | _ILN_RC_AVG_MAX_T[0] | s | Time of max. val. of mean val., ripple control signal, I L1
6410 | uint | RD/WR | _ILN_RC_AVG_MAX_T[1] | s | Time of max. val. of mean val., ripple control signal, I L2
6412 | uint | RD/WR | _ILN_RC_AVG_MAX_T[2] | s | Time of max. val. of mean val., ripple control signal, I L3
6414 | uint | RD/WR | _ILN_RC_AVG_MAX_T[3] | s | Time of max. val. of mean val., ripple control signal, I L4
6416 | uint | RD/WR | _ULL_RC_AVG_MAX_T[0] | s | Time of max. val. of mean val., ripple control signal, U L1-L2
6418 | uint | RD/WR | _ULL_RC_AVG_MAX_T[1] | s | Time of max. val. of mean val., ripple control signal, U L2-L3
6420 | uint | RD/WR | _ULL_RC_AVG_MAX_T[2] | s | Time of max. val. of mean val., ripple control signal, U L3-L1
6432 | uint | RD/WR | _PFLN_AVG_MAX_T[0] | s | Time of max. val. of mean val., power factor; L1
6434 | uint | RD/WR | _PFLN_AVG_MAX_T[1] | s | Time of max. val. of mean val., power factor; L2
6436 | uint | RD/WR | _PFLN_AVG_MAX_T[2] | s | Time of max. val. of mean val., power factor; L3
6438 | uint | RD/WR | _PFLN_AVG_MAX_T[3] | s | Time of max. val. of mean val., power factor; L4
6440 | uint | RD/WR | _DLN_AVG_MAX_T[0] | s | Time of max. val. of mean val., distortion power factor; L1
6442 | uint | RD/WR | _DLN_AVG_MAX_T[1] | s | Time of max. val. of mean val., distortion power factor; L2
6444 | uint | RD/WR | _DLN_AVG_MAX_T[2] | s | Time of max. val. of mean val., distortion power factor; L3
6446 | uint | RD/WR | _DLN_AVG_MAX_T[3] | s | Time of max. val. of mean val., distortion power factor; L4
6448 | uint | RD/WR | _KFACT_AVG_MAX_T[0] | s | Time of max. val. of mean val., K-Factor, L1
6450 | uint | RD/WR | _KFACT_AVG_MAX_T[1] | s | Time of max. val. of mean val., K-Factor, L2
6452 | uint | RD/WR | _KFACT_AVG_MAX_T[2] | s | Time of max. val. of mean val., K-Factor, L3
6454 | uint | RD/WR | _KFACT_AVG_MAX_T[3] | s | Time of max. val. of mean val., K-Factor, L4
6456 | uint | RD/WR | _S0_POWER_AVG_MAX_T[0] | s | Time of max. val. of mean val., Input 1, measured value
6458 | uint | RD/WR | _S0_POWER_AVG_MAX_T[1] | s | Time of max. val. of mean val., Input 1, measured value
6460 | uint | RD/WR | _TEMPERATUR_AVG_MAX_T | s | Time of max. val. of mean val., Input 1, internal temperature
Energy
Address | Format | RD/WR | Designation | Unit | Note
6462 | short | RD/WR | _W_TARIF |  | Current rate, real/apparent energy
6463 | short | RD/WR | _Q_TARIF |  | Current rate, reactive energy
6464 | float | RD/WR | _WH_S[0] | VAh | Apparent energy L1
6466 | float | RD/WR | _WH_S[1] | VAh | Apparent energy L2
6468 | float | RD/WR | _WH_S[2] | VAh | Apparent energy L3
6470 | float | RD/WR | _WH_S[3] | VAh | Apparent energy L4
6472 | float | RD/WR | _WH_S[4] | VAh | Apparent energy L1..L3
6474 | float | RD/WR | _WH_S[5] | VAh | Apparent energy L1..L4
6476 | float | RD/WR | _WH[0] | Wh | Real energy L1
6478 | float | RD/WR | _WH[1] | Wh | Real energy L2
6480 | float | RD/WR | _WH[2] | Wh | Real energy L3
6482 | float | RD/WR | _WH[3] | Wh | Real energy L4
6484 | float | RD/WR | _WH[4] | Wh | Real energy L1..L3
6486 | float | RD/WR | _WH[5] | Wh | Real energy L1..L4
6488 | float | RD/WR | _QH[0] | varh | Reaktive energy L1
6490 | float | RD/WR | _QH[1] | varh | Reaktive energy L2
6492 | float | RD/WR | _QH[2] | varh | Reaktive energy L3
6494 | float | RD/WR | _QH[3] | varh | Reaktive energy L4
6496 | float | RD/WR | _QH[4] | varh | Reaktive energy L1..L3
6498 | float | RD/WR | _QH[5] | varh | Reaktive energy L1..L4
6500 | float | RD/WR | _WH_V[0] | Wh | Real energy L1, consumed
6502 | float | RD/WR | _WH_V[1] | Wh | Real energy L2, consumed
6504 | float | RD/WR | _WH_V[2] | Wh | Real energy L3, consumed
6506 | float | RD/WR | _WH_V[3] | Wh | Real energy L4, consumed
6508 | float | RD/WR | _WH_V[4] | Wh | Real energy L1..L3, consumed
6510 | float | RD/WR | _WH_V[5] | Wh | Real energy L1..L4, consumed
6512 | float | RD/WR | _WH_Z[0] | Wh | Real energy L1, delivered
6514 | float | RD/WR | _WH_Z[1] | Wh | Real energy L2, delivered
6516 | float | RD/WR | _WH_Z[2] | Wh | Real energy L3, delivered
6518 | float | RD/WR | _WH_Z[3] | Wh | Real energy L4, delivered
6520 | float | RD/WR | _WH_Z[4] | Wh | Real energy L1..L3, delivered
6522 | float | RD/WR | _WH_Z[5] | Wh | Real energy L1..L4, delivered
6524 | float | RD/WR | _WH_V_HT[0] | Wh | Real energy L1, consumed, rate 1
6526 | float | RD/WR | _WH_V_HT[1] | Wh | Real energy L2, consumed, rate 1
6528 | float | RD/WR | _WH_V_HT[2] | Wh | Real energy L3, consumed, rate 1
6530 | float | RD/WR | _WH_V_HT[3] | Wh | Real energy L4, consumed, rate 1
6532 | float | RD/WR | _WH_V_HT[4] | Wh | Real energy L1..L3, consumed, rate 1
6534 | float | RD/WR | _WH_V_HT[5] | Wh | Real energy L1..L4, consumed, rate 1
6536 | float | RD/WR | _WH_V_NT[0] | Wh | Real energy L1, consumed, rate 2
6538 | float | RD/WR | _WH_V_NT[1] | Wh | Real energy L3, consumed, rate 2
6540 | float | RD/WR | _WH_V_NT[2] | Wh | Real energy L3, consumed, rate 2
6542 | float | RD/WR | _WH_V_NT[3] | Wh | Real energy L4, consumed, rate 2
6544 | float | RD/WR | _WH_V_NT[4] | Wh | Real energy L1..L3, consumed, rate 2
6546 | float | RD/WR | _WH_V_NT[5] | Wh | Real energy L1..L4, consumed, rate 2
6548 | float | RD/WR | _WH_Z_HT[0] | Wh | Real energy L1, delivered, rate 1
6550 | float | RD/WR | _WH_Z_HT[1] | Wh | Real energy L2, delivered, rate 1
6552 | float | RD/WR | _WH_Z_HT[2] | Wh | Real energy L3, delivered, rate 1
6554 | float | RD/WR | _WH_Z_HT[3] | Wh | Real energy L4, delivered, rate 1
6556 | float | RD/WR | _WH_Z_HT[4] | Wh | Real energy L1..L3, delivered, rate 1
6558 | float | RD/WR | _WH_Z_HT[5] | Wh | Real energy L1..L4, delivered, rate 1
6560 | float | RD/WR | _WH_Z_NT[0] | Wh | Real energy L1, delivered, rate 2
6562 | float | RD/WR | _WH_Z_NT[1] | Wh | Real energy L2, delivered, rate 2
6564 | float | RD/WR | _WH_Z_NT[2] | Wh | Real energy L3, delivered, rate 2
6566 | float | RD/WR | _WH_Z_NT[3] | Wh | Real energy L4, delivered, rate 2
6568 | float | RD/WR | _WH_Z_NT[4] | Wh | Real energy L1..L3, delivered, rate 2
6570 | float | RD/WR | _WH_Z_NT[5] | Wh | Real energy L1..L4, delivered, rate 2
6572 | float | RD/WR | _IQH[0] | varh | Reactive energy L1, inductive
6574 | float | RD/WR | _IQH[1] | varh | Reactive energy L2, inductive
6576 | float | RD/WR | _IQH[2] | varh | Reactive energy L3, inductive
6578 | float | RD/WR | _IQH[3] | varh | Reactive energy L4, inductive
6580 | float | RD/WR | _IQH[4] | varh | Reactive energy L1..L3, inductive
6582 | float | RD/WR | _IQH[5] | varh | Reactive energy L1..L4, inductive
6584 | float | RD/WR | _CQH[0] | varh | Reactive energy L1, capacitive
6586 | float | RD/WR | _CQH[1] | varh | Reactive energy L2, capacitive
6588 | float | RD/WR | _CQH[2] | varh | Reactive energy L3, capacitive
6590 | float | RD/WR | _CQH[3] | varh | Reactive energy L4, capacitive
6592 | float | RD/WR | _CQH[4] | varh | Reactive energy L1..L3, capacitive
6594 | float | RD/WR | _CQH[5] | varh | Reactive energy L1..L4, capacitive
6596 | float | RD/WR | _IQH_HT[0] | varh | Reactive energy L1, inductive, rate 1
6598 | float | RD/WR | _IQH_HT[1] | varh | Reactive energy L2, inductive, rate 1
6600 | float | RD/WR | _IQH_HT[2] | varh | Reactive energy L3, inductive, rate 1
6602 | float | RD/WR | _IQH_HT[3] | varh | Reactive energy L4, inductive, rate 1
6604 | float | RD/WR | _IQH_HT[4] | varh | Reactive energy L1..L3, inductive, rate 1
6606 | float | RD/WR | _IQH_HT[5] | varh | Reactive energy L1..L4, inductive, rate 1
6608 | float | RD/WR | _IQH_NT[0] | varh | Reactive energy L1, inductive, rate 2
6610 | float | RD/WR | _IQH_NT[1] | varh | Reactive energy L2, inductive, rate 2
6612 | float | RD/WR | _IQH_NT[2] | varh | Reactive energy L3, inductive, rate 2
6614 | float | RD/WR | _IQH_NT[3] | varh | Reactive energy L4, inductive, rate 2
6616 | float | RD/WR | _IQH_NT[4] | varh | Reactive energy L1..L3, inductive, rate 2
6618 | float | RD/WR | _IQH_NT[5] | varh | Reactive energy L1..L4, inductive, rate 2
6620 | float | RD/WR | _S0_CNT[0] |  | Energy meter (counter, not scaled), impulse input 1
6622 | float | RD/WR | _S0_CNT[1] |  | Energy meter (counter, not scaled), impulse input 2
6624 | float | RD/WR | _TIME_WH | s | Runtime of real and apparent energy meas.
6626 | float | RD/WR | _TIME_QH | s | Runtime of real and reactive energy meas.
6654 | short | RD/WR | _DEL_WH |  | 1=delete all real energy counters
6655 | short | RD/WR | _DEL_QH |  | 1=delete all reactive energy counters
11756 | float | RD/WR | _WH_V_T3[0] | Wh | Real energy L1, consumed, rate 3
11758 | float | RD/WR | _WH_V_T3[1] | Wh | Real energy L2, consumed, rate 3
11760 | float | RD/WR | _WH_V_T3[2] | Wh | Real energy L3, consumed, rate 3
11762 | float | RD/WR | _WH_V_T3[3] | Wh | Real energy L4, consumed, rate 3
11764 | float | RD/WR | _WH_V_T3[4] | Wh | Real energy L1..L3, consumed, rate 3
11766 | float | RD/WR | _WH_V_T3[5] | Wh | Real energy L1..L4, consumed, rate 3
11768 | float | RD/WR | _WH_V_T4[0] | Wh | Real energy L1, consumed, rate 4
11770 | float | RD/WR | _WH_V_T4[1] | Wh | Real energy L2, consumed, rate 4
11772 | float | RD/WR | _WH_V_T4[2] | Wh | Real energy L3, consumed, rate 4
11774 | float | RD/WR | _WH_V_T4[3] | Wh | Real energy L4, consumed, rate 4
11776 | float | RD/WR | _WH_V_T4[4] | Wh | Real energy L1..L3, consumed, rate 4
11778 | float | RD/WR | _WH_V_T4[5] | Wh | Real energy L1..L4, consumed, rate 4
11780 | float | RD/WR | _WH_Z_T3[0] | Wh | Real energy L1, delivered, rate 3
11782 | float | RD/WR | _WH_Z_T3[1] | Wh | Real energy L2, delivered, rate 3
11784 | float | RD/WR | _WH_Z_T3[2] | Wh | Real energy L3, delivered, rate 3
11786 | float | RD/WR | _WH_Z_T3[3] | Wh | Real energy L4, delivered, rate 3
11788 | float | RD/WR | _WH_Z_T3[4] | Wh | Real energy L1..L3, delivered, rate 3
11790 | float | RD/WR | _WH_Z_T3[5] | Wh | Real energy L1..L4, delivered, rate 3
11792 | float | RD/WR | _WH_Z_T4[0] | Wh | Real energy L1, delivered, rate 4
11794 | float | RD/WR | _WH_Z_T4[1] | Wh | Real energy L2, delivered, rate 4
11796 | float | RD/WR | _WH_Z_T4[2] | Wh | Real energy L3, delivered, rate 4
11798 | float | RD/WR | _WH_Z_T4[3] | Wh | Real energy L4, delivered, rate 4
11800 | float | RD/WR | _WH_Z_T4[4] | Wh | Real energy L1..L3, delivered, rate 4
11802 | float | RD/WR | _WH_Z_T4[5] | Wh | Real energy L1..L4, delivered, rate 4
11804 | float | RD/WR | _IQH_T3[0] | varh | Reactive energy L1, inductive, rate 3
11806 | float | RD/WR | _IQH_T3[1] | varh | Reactive energy L2, inductive, rate 3
11808 | float | RD/WR | _IQH_T3[2] | varh | Reactive energy L3, inductive, rate 3
11810 | float | RD/WR | _IQH_T3[3] | varh | Reactive energy L4, inductive, rate 3
11812 | float | RD/WR | _IQH_T3[4] | varh | Reactive energy L1..L3, inductive, rate 3
11814 | float | RD/WR | _IQH_T3[5] | varh | Reactive energy L1..L4, inductive, rate 3
11816 | float | RD/WR | _IQH_T4[0] | varh | Reactive energy L1, inductive, rate 4
11818 | float | RD/WR | _IQH_T4[1] | varh | Reactive energy L2, inductive, rate 4
11820 | float | RD/WR | _IQH_T4[2] | varh | Reactive energy L3, inductive, rate 4
11822 | float | RD/WR | _IQH_T4[3] | varh | Reactive energy L4, inductive, rate 4
11824 | float | RD/WR | _IQH_T4[4] | varh | Reactive energy L1..L3, inductive, rate 4
11826 | float | RD/WR | _IQH_T4[5] | varh | Reactive energy L1..L4, inductive, rate 4
12038 | float | RD | _S0_POWER[0] | W | Input 1, measured value
12040 | float | RD | _S0_POWER[1] | W | Input 2, measured value
12042 | float | RD/WR | _VWH_MONTH[0] | Wh | Real energy, month high, january, even year
12044 | float | RD/WR | _VWH_MONTH[1] | Wh | Real energy, month high, february, even year
12046 | float | RD/WR | _VWH_MONTH[2] | Wh | Real energy, month high, march, even year
12048 | float | RD/WR | _VWH_MONTH[3] | Wh | Real energy, month high, april, even year
12050 | float | RD/WR | _VWH_MONTH[4] | Wh | Real energy, month high, may, even year
12052 | float | RD/WR | _VWH_MONTH[5] | Wh | Real energy, month high, june, even year
12054 | float | RD/WR | _VWH_MONTH[6] | Wh | Real energy, month high, july, even year
12056 | float | RD/WR | _VWH_MONTH[7] | Wh | Real energy, month high, august, even year
12058 | float | RD/WR | _VWH_MONTH[8] | Wh | Real energy, month high, september, even year
12060 | float | RD/WR | _VWH_MONTH[9] | Wh | Real energy, month high, october, even year
12062 | float | RD/WR | _VWH_MONTH[10] | Wh | Real energy, month high, november, even year
12064 | float | RD/WR | _VWH_MONTH[11] | Wh | Real energy, month high, december, even year
12066 | float | RD/WR | _VWH_MONTH[12] | Wh | Real energy, month high, january, uneven year
12068 | float | RD/WR | _VWH_MONTH[13] | Wh | Real energy, month high, february, uneven year
12070 | float | RD/WR | _VWH_MONTH[14] | Wh | Real energy, month high, march, uneven year
12072 | float | RD/WR | _VWH_MONTH[15] | Wh | Real energy, month high, april, uneven year
12074 | float | RD/WR | _VWH_MONTH[16] | Wh | Real energy, month high, may, uneven year
12076 | float | RD/WR | _VWH_MONTH[17] | Wh | Real energy, month high, june, uneven year
12078 | float | RD/WR | _VWH_MONTH[18] | Wh | Real energy, month high, july, uneven year
12080 | float | RD/WR | _VWH_MONTH[19] | Wh | Real energy, month high, august, uneven year
12082 | float | RD/WR | _VWH_MONTH[20] | Wh | Real energy, month high, september, uneven year
12084 | float | RD/WR | _VWH_MONTH[21] | Wh | Real energy, month high, october, uneven year
12086 | float | RD/WR | _VWH_MONTH[22] | Wh | Real energy, month high, november, uneven year
12088 | float | RD/WR | _VWH_MONTH[23] | Wh | Real energy, month high, december, uneven year
12090 | float | RD/WR | _SH_MONTH[0] | VAh | Apparent energy, month high, january, even year
12092 | float | RD/WR | _SH_MONTH[1] | VAh | Apparent energy, month high, february, even year
12094 | float | RD/WR | _SH_MONTH[2] | VAh | Apparent energy, month high, march, even year
12096 | float | RD/WR | _SH_MONTH[3] | VAh | Apparent energy, month high, april, even year
12098 | float | RD/WR | _SH_MONTH[4] | VAh | Apparent energy, month high, may, even year
12100 | float | RD/WR | _SH_MONTH[5] | VAh | Apparent energy, month high, june, even year
12102 | float | RD/WR | _SH_MONTH[6] | VAh | Apparent energy, month high, july, even year
12104 | float | RD/WR | _SH_MONTH[7] | VAh | Apparent energy, month high, august, even year
12106 | float | RD/WR | _SH_MONTH[8] | VAh | Apparent energy, month high, september, even year
12108 | float | RD/WR | _SH_MONTH[9] | VAh | Apparent energy, month high, october, even year
12110 | float | RD/WR | _SH_MONTH[10] | VAh | Apparent energy, month high, november, even year
12112 | float | RD/WR | _SH_MONTH[11] | VAh | Apparent energy, month high, december, even year
12114 | float | RD/WR | _SH_MONTH[12] | VAh | Apparent energy, month high, january, uneven year
12116 | float | RD/WR | _SH_MONTH[13] | VAh | Apparent energy, month high, february, uneven year
12118 | float | RD/WR | _SH_MONTH[14] | VAh | Apparent energy, month high, march, uneven year
12120 | float | RD/WR | _SH_MONTH[15] | VAh | Apparent energy, month high, april, uneven year
12122 | float | RD/WR | _SH_MONTH[16] | VAh | Apparent energy, month high, may, uneven year
12124 | float | RD/WR | _SH_MONTH[17] | VAh | Apparent energy, month high, june, uneven year
12126 | float | RD/WR | _SH_MONTH[18] | VAh | Apparent energy, month high, july, uneven year
12128 | float | RD/WR | _SH_MONTH[19] | VAh | Apparent energy, month high, august, uneven year
12130 | float | RD/WR | _SH_MONTH[20] | VAh | Apparent energy, month high, september, uneven year
12132 | float | RD/WR | _SH_MONTH[21] | VAh | Apparent energy, month high, october, uneven year
12134 | float | RD/WR | _SH_MONTH[22] | VAh | Apparent energy, month high, november, uneven year
12136 | float | RD/WR | _SH_MONTH[23] | VAh | Apparent energy, month high, december, uneven year
12138 | float | RD/WR | _IQH_MONTH[0] | Varh | Reactive energy, month high, january, even year
12140 | float | RD/WR | _IQH_MONTH[1] | Varh | Reactive energy, month high, february, even year
12142 | float | RD/WR | _IQH_MONTH[2] | Varh | Reactive energy, month high, march, even year
12144 | float | RD/WR | _IQH_MONTH[3] | Varh | Reactive energy, month high, april, even year
12146 | float | RD/WR | _IQH_MONTH[4] | Varh | Reactive energy, month high, may, even year
12148 | float | RD/WR | _IQH_MONTH[5] | Varh | Reactive energy, month high, june, even year
12150 | float | RD/WR | _IQH_MONTH[6] | Varh | Reactive energy, month high, july, even year
12152 | float | RD/WR | _IQH_MONTH[7] | Varh | Reactive energy, month high, august, even year
12154 | float | RD/WR | _IQH_MONTH[8] | Varh | Reactive energy, month high, september, even year
12156 | float | RD/WR | _IQH_MONTH[9] | Varh | Reactive energy, month high, october, even year
12158 | float | RD/WR | _IQH_MONTH[10] | Varh | Reactive energy, month high, november, even year
12160 | float | RD/WR | _IQH_MONTH[11] | Varh | Reactive energy, month high, december, even year
12162 | float | RD/WR | _IQH_MONTH[12] | Varh | Reactive energy, month high, january, uneven year
12164 | float | RD/WR | _IQH_MONTH[13] | Varh | Reactive energy, month high, february, uneven year
12166 | float | RD/WR | _IQH_MONTH[14] | Varh | Reactive energy, month high, march, uneven year
12168 | float | RD/WR | _IQH_MONTH[15] | Varh | Reactive energy, month high, april, uneven year
12170 | float | RD/WR | _IQH_MONTH[16] | Varh | Reactive energy, month high, may, uneven year
12172 | float | RD/WR | _IQH_MONTH[17] | Varh | Reactive energy, month high, june, uneven year
12174 | float | RD/WR | _IQH_MONTH[18] | Varh | Reactive energy, month high, july, uneven year
12176 | float | RD/WR | _IQH_MONTH[19] | Varh | Reactive energy, month high, august, uneven year
12178 | float | RD/WR | _IQH_MONTH[20] | Varh | Reactive energy, month high, september, uneven year
12180 | float | RD/WR | _IQH_MONTH[21] | Varh | Reactive energy, month high, october, uneven year
12182 | float | RD/WR | _IQH_MONTH[22] | Varh | Reactive energy, month high, november, uneven year
12184 | float | RD/WR | _IQH_MONTH[23] | Varh | Reactive energy, month high, december, uneven year
12186 | float | RD/WR | _P15_MONTH[0] | W | EMAX, 15minutes month 1st high, jan., even year
12188 | float | RD/WR | _P15_MONTH[1] | W | EMAX, 15minutes month 1st high, feb., even year
12190 | float | RD/WR | _P15_MONTH[2] | W | EMAX, 15minutes month 1st high, march, even year
12192 | float | RD/WR | _P15_MONTH[3] | W | EMAX, 15minutes month 1st high, april, even year
12194 | float | RD/WR | _P15_MONTH[4] | W | EMAX, 15minutes month 1st high, may, even year
12196 | float | RD/WR | _P15_MONTH[5] | W | EMAX, 15minutes month 1st high, june, even year
12198 | float | RD/WR | _P15_MONTH[6] | W | EMAX, 15minutes month 1st high, july, even year
12200 | float | RD/WR | _P15_MONTH[7] | W | EMAX, 15minutes month 1st high, aug., even year
12202 | float | RD/WR | _P15_MONTH[8] | W | EMAX, 15minutes month 1st high, sep., even year
12204 | float | RD/WR | _P15_MONTH[9] | W | EMAX, 15minutes month 1st high, oct., even year
12206 | float | RD/WR | _P15_MONTH[10] | W | EMAX, 15minutes month 1st high, nov., even year
12208 | float | RD/WR | _P15_MONTH[11] | W | EMAX, 15minutes month 1st high, dec., even year
12210 | float | RD/WR | _P15_MONTH[12] | W | EMAX, 15minutes month 1st high, jan., uneven year
12212 | float | RD/WR | _P15_MONTH[13] | W | EMAX, 15minutes month 1st high, feb., uneven year
12214 | float | RD/WR | _P15_MONTH[14] | W | EMAX, 15minutes month 1st high, march, uneven year
12216 | float | RD/WR | _P15_MONTH[15] | W | EMAX, 15minutes month 1st high, april, uneven year
12218 | float | RD/WR | _P15_MONTH[16] | W | EMAX, 15minutes month 1st high, may, uneven year
12220 | float | RD/WR | _P15_MONTH[17] | W | EMAX, 15minutes month 1st high, june., uneven year
12222 | float | RD/WR | _P15_MONTH[18] | W | EMAX, 15minutes month 1st high, july, uneven year
12224 | float | RD/WR | _P15_MONTH[19] | W | EMAX, 15minutes month 1st high, aug., uneven year
12226 | float | RD/WR | _P15_MONTH[20] | W | EMAX, 15minutes month 1st high, sep., uneven year
12228 | float | RD/WR | _P15_MONTH[21] | W | EMAX, 15minutes month 1st high, oct., uneven year
12230 | float | RD/WR | _P15_MONTH[22] | W | EMAX, 15minutes month 1st high, nov., uneven year
12232 | float | RD/WR | _P15_MONTH[23] | W | EMAX, 15minutes month 1st high, dec., uneven year
12234 | float | RD/WR | _P15_MONTH[24] | W | EMAX, 15minutes month 2nd high, jan., even year
12236 | float | RD/WR | _P15_MONTH[25] | W | EMAX, 15minutes month 2nd high, feb., even year
12238 | float | RD/WR | _P15_MONTH[26] | W | EMAX, 15minutes month 2nd high, march, even year
12240 | float | RD/WR | _P15_MONTH[27] | W | EMAX, 15minutes month 2nd high, april, even year
12242 | float | RD/WR | _P15_MONTH[28] | W | EMAX, 15minutes month 2nd high, may, even year
12244 | float | RD/WR | _P15_MONTH[29] | W | EMAX, 15minutes month 2nd high, june, even year
12246 | float | RD/WR | _P15_MONTH[30] | W | EMAX, 15minutes month 2nd high, july, even year
12248 | float | RD/WR | _P15_MONTH[31] | W | EMAX, 15minutes month 2nd high, aug., even year
12250 | float | RD/WR | _P15_MONTH[32] | W | EMAX, 15minutes month 2nd high, sep., even year
12252 | float | RD/WR | _P15_MONTH[33] | W | EMAX, 15minutes month 2nd high, oct., even year
12254 | float | RD/WR | _P15_MONTH[34] | W | EMAX, 15minutes month 2nd high, nov., even year
12256 | float | RD/WR | _P15_MONTH[35] | W | EMAX, 15minutes month 2nd high, dec., even year
12258 | float | RD/WR | _P15_MONTH[36] | W | EMAX, 15minutes month 2nd high, jan., uneven year
12260 | float | RD/WR | _P15_MONTH[37] | W | EMAX, 15minutes month 2nd high, feb., uneven year
12262 | float | RD/WR | _P15_MONTH[38] | W | EMAX, 15minutes month 2nd high, march, uneven year
12264 | float | RD/WR | _P15_MONTH[39] | W | EMAX, 15minutes month 2nd high, april., uneven year
12266 | float | RD/WR | _P15_MONTH[40] | W | EMAX, 15minutes month 2nd high, may, uneven year
12268 | float | RD/WR | _P15_MONTH[41] | W | EMAX, 15minutes month 2nd high, june., uneven year
12270 | float | RD/WR | _P15_MONTH[42] | W | EMAX, 15minutes month 2nd high, july, uneven year
12272 | float | RD/WR | _P15_MONTH[43] | W | EMAX, 15minutes month 2nd high, aug., uneven year
12274 | float | RD/WR | _P15_MONTH[44] | W | EMAX, 15minutes month 2nd high, sep., uneven year
12276 | float | RD/WR | _P15_MONTH[45] | W | EMAX, 15minutes month 2nd high, oct., uneven year
12278 | float | RD/WR | _P15_MONTH[46] | W | EMAX, 15minutes month 2nd high, nov., uneven year
12280 | float | RD/WR | _P15_MONTH[47] | W | EMAX, 15minutes month 2nd high, dec., uneven year
12282 | float | RD/WR | _P15_MONTH[48] | W | EMAX, 15minutes month 3rd high, jan., even year
12284 | float | RD/WR | _P15_MONTH[49] | W | EMAX, 15minutes month 3rd high, feb., even year
12286 | float | RD/WR | _P15_MONTH[50] | W | EMAX, 15minutes month 3rd high, march., even year
12288 | float | RD/WR | _P15_MONTH[51] | W | EMAX, 15minutes month 3rd high, april, even year
12290 | float | RD/WR | _P15_MONTH[52] | W | EMAX, 15minutes month 3rd high, may., even year
12292 | float | RD/WR | _P15_MONTH[53] | W | EMAX, 15minutes month 3rd high, june, even year
12294 | float | RD/WR | _P15_MONTH[54] | W | EMAX, 15minutes month 3rd high, july, even year
12296 | float | RD/WR | _P15_MONTH[55] | W | EMAX, 15minutes month 3rd high, aug., even year
12298 | float | RD/WR | _P15_MONTH[56] | W | EMAX, 15minutes month 3rd high, sep., even year
12300 | float | RD/WR | _P15_MONTH[57] | W | EMAX, 15minutes month 3rd high, oct., even year
12302 | float | RD/WR | _P15_MONTH[58] | W | EMAX, 15minutes month 3rd high, nov., even year
12304 | float | RD/WR | _P15_MONTH[59] | W | EMAX, 15minutes month 3rd high, dec., even year
12306 | float | RD/WR | _P15_MONTH[60] | W | EMAX, 15minutes month 3rd high, jan., uneven year
12308 | float | RD/WR | _P15_MONTH[61] | W | EMAX, 15minutes month 3rd high, feb., uneven year
12310 | float | RD/WR | _P15_MONTH[62] | W | EMAX, 15minutes month 3rd high, march, uneven year
12312 | float | RD/WR | _P15_MONTH[63] | W | EMAX, 15minutes month 3rd high, april, uneven year
12314 | float | RD/WR | _P15_MONTH[64] | W | EMAX, 15minutes month 3rd high, may, uneven year
12316 | float | RD/WR | _P15_MONTH[65] | W | EMAX, 15minutes month 3rd high, june, uneven year
12318 | float | RD/WR | _P15_MONTH[66] | W | EMAX, 15minutes month 3rd high, july, uneven year
12320 | float | RD/WR | _P15_MONTH[67] | W | EMAX, 15minutes month 3rd high, aug., uneven year
12322 | float | RD/WR | _P15_MONTH[68] | W | EMAX, 15minutes month 3rd high, sep., uneven year
12324 | float | RD/WR | _P15_MONTH[69] | W | EMAX, 15minutes month 3rd high, oct., uneven year
12326 | float | RD/WR | _P15_MONTH[70] | W | EMAX, 15minutes month 3rd high, nov., uneven year
12328 | float | RD/WR | _P15_MONTH[71] | W | EMAX, 15minutes month 3rd high, dec., uneven year
12330 | uint | RD/WR | _P15_T_MONTH[0] | s | Time of 15min. month 1st high (UTC), jan., even year
12332 | uint | RD/WR | _P15_T_MONTH[1] | s | Time of 15min. month 1st high (UTC), feb., even year
12334 | uint | RD/WR | _P15_T_MONTH[2] | s | Time of 15min. month 1st high (UTC), march, even year
12336 | uint | RD/WR | _P15_T_MONTH[3] | s | Time of 15min. month 1st high (UTC), april, even year
12338 | uint | RD/WR | _P15_T_MONTH[4] | s | Time of 15min. month 1st high (UTC), may, even year
12340 | uint | RD/WR | _P15_T_MONTH[5] | s | Time of 15min. month 1st high (UTC), june, even year
12342 | uint | RD/WR | _P15_T_MONTH[6] | s | Time of 15min. month 1st high (UTC), july, even year
12344 | uint | RD/WR | _P15_T_MONTH[7] | s | Time of 15min. month 1st high (UTC), aug., even year
12346 | uint | RD/WR | _P15_T_MONTH[8] | s | Time of 15min. month 1st high (UTC), sep., even year
12348 | uint | RD/WR | _P15_T_MONTH[9] | s | Time of 15min. month 1st high (UTC), oct., even year
12350 | uint | RD/WR | _P15_T_MONTH[10] | s | Time of 15min. month 1st high (UTC), nov., even year
12352 | uint | RD/WR | _P15_T_MONTH[11] | s | Time of 15min. month 1st high (UTC), dec., even year
12354 | uint | RD/WR | _P15_T_MONTH[12] | s | Time of 15min. month 1st high (UTC), jan., uneven year
12356 | uint | RD/WR | _P15_T_MONTH[13] | s | Time of 15min. month 1st high (UTC), feb., uneven year
12358 | uint | RD/WR | _P15_T_MONTH[14] | s | Time of 15min. month 1st high (UTC), march, uneven year
12360 | uint | RD/WR | _P15_T_MONTH[15] | s | Time of 15min. month 1st high (UTC), april, uneven year
12362 | uint | RD/WR | _P15_T_MONTH[16] | s | Time of 15min. month 1st high (UTC), may, uneven year
12364 | uint | RD/WR | _P15_T_MONTH[17] | s | Time of 15min. month 1st high (UTC), june, uneven year
12366 | uint | RD/WR | _P15_T_MONTH[18] | s | Time of 15min. month 1st high (UTC), july, uneven year
12368 | uint | RD/WR | _P15_T_MONTH[19] | s | Time of 15min. month 1st high (UTC), aug., uneven year
12370 | uint | RD/WR | _P15_T_MONTH[20] | s | Time of 15min. month 1st high (UTC), sep., uneven year
12372 | uint | RD/WR | _P15_T_MONTH[21] | s | Time of 15min. month 1st high (UTC), oct., uneven year
12374 | uint | RD/WR | _P15_T_MONTH[22] | s | Time of 15min. month 1st high (UTC), nov., uneven year
12376 | uint | RD/WR | _P15_T_MONTH[23] | s | Time of 15min. month 1st high (UTC), dec., uneven year
12378 | uint | RD/WR | _P15_T_MONTH[24] | s | Time of 15min. month 2nd high (UTC), jan., even year
12380 | uint | RD/WR | _P15_T_MONTH[25] | s | Time of 15min. month 2nd high (UTC), feb., even year
12382 | uint | RD/WR | _P15_T_MONTH[26] | s | Time of 15min. month 2nd high (UTC), march, even year
12384 | uint | RD/WR | _P15_T_MONTH[27] | s | Time of 15min. month 2nd high (UTC), april, even year
12386 | uint | RD/WR | _P15_T_MONTH[28] | s | Time of 15min. month 2nd high (UTC), may, even year
12388 | uint | RD/WR | _P15_T_MONTH[29] | s | Time of 15min. month 2nd high (UTC), june, even year
12390 | uint | RD/WR | _P15_T_MONTH[30] | s | Time of 15min. month 2nd high (UTC), july, even year
12392 | uint | RD/WR | _P15_T_MONTH[31] | s | Time of 15min. month 2nd high (UTC), aug., even year
12394 | uint | RD/WR | _P15_T_MONTH[32] | s | Time of 15min. month 2nd high (UTC), sep., even year
12396 | uint | RD/WR | _P15_T_MONTH[33] | s | Time of 15min. month 2nd high (UTC), oct., even year
12398 | uint | RD/WR | _P15_T_MONTH[34] | s | Time of 15min. month 2nd high (UTC), nov., even year
12400 | uint | RD/WR | _P15_T_MONTH[35] | s | Time of 15min. month 2nd high (UTC), dec., even year
12402 | uint | RD/WR | _P15_T_MONTH[36] | s | Time of 15min. month 2nd high (UTC), jan., uneven year
12404 | uint | RD/WR | _P15_T_MONTH[37] | s | Time of 15min. month 2nd high (UTC), feb., uneven year
12406 | uint | RD/WR | _P15_T_MONTH[38] | s | Time of 15min. month 2nd high (UTC), march, uneven year
12408 | uint | RD/WR | _P15_T_MONTH[39] | s | Time of 15min. month 2nd high (UTC), april, uneven year
12410 | uint | RD/WR | _P15_T_MONTH[40] | s | Time of 15min. month 2nd high (UTC), may, uneven year
12412 | uint | RD/WR | _P15_T_MONTH[41] | s | Time of 15min. month 2nd high (UTC), june, uneven year
12414 | uint | RD/WR | _P15_T_MONTH[42] | s | Time of 15min. month 2nd high (UTC), july, uneven year
12416 | uint | RD/WR | _P15_T_MONTH[43] | s | Time of 15min. month 2nd high (UTC), aug., uneven year
12418 | uint | RD/WR | _P15_T_MONTH[44] | s | Time of 15min. month 2nd high (UTC), sep., uneven year
12420 | uint | RD/WR | _P15_T_MONTH[45] | s | Time of 15min. month 2nd high (UTC), oct., uneven year
12422 | uint | RD/WR | _P15_T_MONTH[46] | s | Time of 15min. month 2nd high (UTC), nov., uneven year
12424 | uint | RD/WR | _P15_T_MONTH[47] | s | Time of 15min. month 2nd high (UTC), dec., uneven year
12426 | uint | RD/WR | _P15_T_MONTH[48] | s | Time of 15min. month 3nd high (UTC), jan., even year
12428 | uint | RD/WR | _P15_T_MONTH[49] | s | Time of 15min. month 3nd high (UTC), feb., even year
12430 | uint | RD/WR | _P15_T_MONTH[50] | s | Time of 15min. month 3nd high (UTC), march, even year
12432 | uint | RD/WR | _P15_T_MONTH[51] | s | Time of 15min. month 3nd high (UTC), april, even year
12434 | uint | RD/WR | _P15_T_MONTH[52] | s | Time of 15min. month 3nd high (UTC), may, even year
12436 | uint | RD/WR | _P15_T_MONTH[53] | s | Time of 15min. month 3nd high (UTC), june, even year
12438 | uint | RD/WR | _P15_T_MONTH[54] | s | Time of 15min. month 3nd high (UTC), july, even year
12440 | uint | RD/WR | _P15_T_MONTH[55] | s | Time of 15min. month 3nd high (UTC), aug., even year
12442 | uint | RD/WR | _P15_T_MONTH[56] | s | Time of 15min. month 3nd high (UTC), sep., even year
12444 | uint | RD/WR | _P15_T_MONTH[57] | s | Time of 15min. month 3nd high (UTC), oct., even year
12446 | uint | RD/WR | _P15_T_MONTH[58] | s | Time of 15min. month 3nd high (UTC), nov., even year
12448 | uint | RD/WR | _P15_T_MONTH[59] | s | Time of 15min. month 3nd high (UTC), dec., even year
12450 | uint | RD/WR | _P15_T_MONTH[60] | s | Time of 15min. month 3nd high (UTC), jan., uneven year
12452 | uint | RD/WR | _P15_T_MONTH[61] | s | Time of 15min. month 3nd high (UTC), feb., uneven year
12454 | uint | RD/WR | _P15_T_MONTH[62] | s | Time of 15min. month 3nd high (UTC), march, uneven year
12456 | uint | RD/WR | _P15_T_MONTH[63] | s | Time of 15min. month 3nd high (UTC), april, uneven year
12458 | uint | RD/WR | _P15_T_MONTH[64] | s | Time of 15min. month 3nd high (UTC), may, uneven year
12460 | uint | RD/WR | _P15_T_MONTH[65] | s | Time of 15min. month 3nd high (UTC), june, uneven year
12462 | uint | RD/WR | _P15_T_MONTH[66] | s | Time of 15min. month 3nd high (UTC), july, uneven year
12464 | uint | RD/WR | _P15_T_MONTH[67] | s | Time of 15min. month 3nd high (UTC), aug., uneven year
12466 | uint | RD/WR | _P15_T_MONTH[68] | s | Time of 15min. month 3nd high (UTC), sep., uneven year
12468 | uint | RD/WR | _P15_T_MONTH[69] | s | Time of 15min. month 3nd high (UTC), oct., uneven year
12470 | uint | RD/WR | _P15_T_MONTH[70] | s | Time of 15min. month 3nd high (UTC), nov., uneven year
12472 | uint | RD/WR | _P15_T_MONTH[71] | s | Time of 15min. month 3nd high (UTC), dec., uneven year
12474 | short | RD/WR | _MONTHLY_YEAR[0] |  | Year, real energy, bar graph, jan., even year
12475 | short | RD/WR | _MONTHLY_YEAR[1] |  | Year, real energy, bar graph, feb., even year
12476 | short | RD/WR | _MONTHLY_YEAR[2] |  | Year, real energy, bar graph, march, even year
12477 | short | RD/WR | _MONTHLY_YEAR[3] |  | Year, real energy, bar graph, april, even year
12478 | short | RD/WR | _MONTHLY_YEAR[4] |  | Year, real energy, bar graph, may, even year
12479 | short | RD/WR | _MONTHLY_YEAR[5] |  | Year, real energy, bar graph, june, even year
12480 | short | RD/WR | _MONTHLY_YEAR[6] |  | Year, real energy, bar graph, july, even year
12481 | short | RD/WR | _MONTHLY_YEAR[7] |  | Year, real energy, bar graph, aug., even year
12482 | short | RD/WR | _MONTHLY_YEAR[8] |  | Year, real energy, bar graph, sep., even year
12483 | short | RD/WR | _MONTHLY_YEAR[9] |  | Year, real energy, bar graph, oct., even year
12484 | short | RD/WR | _MONTHLY_YEAR[10] |  | Year, real energy, bar graph, nov., even year
12485 | short | RD/WR | _MONTHLY_YEAR[11] |  | Year, real energy, bar graph, dec., even year
12486 | short | RD/WR | _MONTHLY_YEAR[12] |  | Year, real energy, bar graph, jan., uneven year
12487 | short | RD/WR | _MONTHLY_YEAR[13] |  | Year, real energy, bar graph, feb., uneven year
12488 | short | RD/WR | _MONTHLY_YEAR[14] |  | Year, real energy, bar graph, march, uneven year
12489 | short | RD/WR | _MONTHLY_YEAR[15] |  | Year, real energy, bar graph, april, uneven year
12490 | short | RD/WR | _MONTHLY_YEAR[16] |  | Year, real energy, bar graph, may, uneven year
12491 | short | RD/WR | _MONTHLY_YEAR[17] |  | Year, real energy, bar graph, june, uneven year
12492 | short | RD/WR | _MONTHLY_YEAR[18] |  | Year, real energy, bar graph, july, uneven year
12493 | short | RD/WR | _MONTHLY_YEAR[19] |  | Year, real energy, bar graph, aug., uneven year
12494 | short | RD/WR | _MONTHLY_YEAR[20] |  | Year, real energy, bar graph, sep., uneven year
12495 | short | RD/WR | _MONTHLY_YEAR[21] |  | Year, real energy, bar graph, oct., uneven year
12496 | short | RD/WR | _MONTHLY_YEAR[22] |  | Year, real energy, bar graph, nov., uneven year
12497 | short | RD/WR | _MONTHLY_YEAR[23] |  | Year, real energy, bar graph, dec., uneven year
13939 | dfloat | RD/WR | _IVQH[0] | varh | Reactive energy L1 (inductive), consumed
13941 | dfloat | RD/WR | _IVQH[1] | varh | Reactive energy L2 (inductive), consumed
13943 | dfloat | RD/WR | _IVQH[2] | varh | Reactive energy L3 (inductive), consumed
13945 | dfloat | RD/WR | _IVQH[3] | varh | Reactive energy L4 (inductive), consumed
13947 | dfloat | RD/WR | _IVQH[4] | varh | Reactive energy L1..L3 (inductive), consumed
13949 | dfloat | RD/WR | _IVQH[5] | varh | Reactive energy L1..L4 (inductive), consumed
13951 | dfloat | RD/WR | _IZQH[0] | varh | Reactive energy L1 (inductive), delivered
13953 | dfloat | RD/WR | _IZQH[1] | varh | Reactive energy L2 (inductive), delivered
13955 | dfloat | RD/WR | _IZQH[2] | varh | Reactive energy L3 (inductive), delivered
13957 | dfloat | RD/WR | _IZQH[3] | varh | Reactive energy L4 (inductive), delivered
13959 | dfloat | RD/WR | _IZQH[4] | varh | Reactive energy L1..L3 (inductive), delivered
13961 | dfloat | RD/WR | _IZQH[5] | varh | Reactive energy L1..L4 (inductive), delivered
13963 | dfloat | RD/WR | _CVQH[0] | varh | Reactive energy L1 (capacitive), consumed
13965 | dfloat | RD/WR | _CVQH[1] | varh | Reactive energy L2 (capacitive), consumed
13967 | dfloat | RD/WR | _CVQH[2] | varh | Reactive energy L3 (capacitive), consumed
13969 | dfloat | RD/WR | _CVQH[3] | varh | Reactive energy L4 (capacitive), consumed
13971 | dfloat | RD/WR | _CVQH[4] | varh | Reactive energy L1..L3 (capacitive), consumed
13973 | dfloat | RD/WR | _CVQH[5] | varh | Reactive energy L1..L4 (capacitive), consumed
13975 | dfloat | RD/WR | _CZQH[0] | varh | Reactive energy L1 (capacitive), delivered
13977 | dfloat | RD/WR | _CZQH[1] | varh | Reactive energy L2 (capacitive), delivered
13979 | dfloat | RD/WR | _CZQH[2] | varh | Reactive energy L3 (capacitive), delivered
13981 | dfloat | RD/WR | _CZQH[3] | varh | Reactive energy L4 (capacitive), delivered
13983 | dfloat | RD/WR | _CZQH[4] | varh | Reactive energy L1..L3 (capacitive), delivered
13985 | dfloat | RD/WR | _CZQH[5] | varh | Reactive energy L1..L4 (capacitive), delivered
Other values
Address | Format | RD/WR | Designation | Unit | Note
6628 | float | RD | _SPU012 | V | Star connection voltage
6630 | short | RD/WR | _DIGOUT_STAT[0] |  | Status digital output 1, 0=not active, 1=active
6631 | short | RD/WR | _DIGOUT_STAT[1] |  | Status digital output 2, 0=not active, 1=active
6632 | short | RD | _DIGIN_STAT[0] |  | Status digital input 1, 0=not active, 1=active
6633 | short | RD | _DIGIN_STAT[1] |  | Status digital input 2, 0=not active, 1=active
6634 | uint | RD/WR | _EVT_COUNT |  | Event counter
6636 | uint | RD/WR | _FLAG_COUNT |  | Flag counter
6638 | uint | RD/WR | _TRANS_COUNT |  | Error counter, transients
6640 | uint | RD/WR | _HWW_COUNT |  | Error counter, half-cycle effektive val.
6642 | uint | RD/WR | _RX232_COUNT |  | Error counter, receive RS232
6644 | uint | RD/WR | _TX232_COUNT |  | Error counter, send RS232
6646 | uint | RD/WR | _ERR232_COUNT |  | Error counter, RS232
6648 | uint | RD/WR | _RX485_COUNT |  | Error counter, receive RS485
6650 | uint | RD/WR | _TX485_COUNT |  | Error counter, send RS485
6652 | uint | RD/WR | _ERR485_COUNT |  | Error counter, RS485
6656 | short | RD/WR | _INIT_MAX |  | Only for internal use
6657 | string | RD/WR | _RUN | 64 | Only for internal use
6689 | float | RD/WR | _CTPRIM[0] | A | L1, L2, L3; Current transformer, primary
6691 | float | RD/WR | _CTPRIM[1] | A | L4; Current transformer, primary
6693 | float | RD/WR | _CTSEC[0] | A | L1, L2, L3; Current transf., secondary
6695 | float | RD/WR | _CTSEC[1] | A | L4; Current transformer, secondary
6697 | float | RD/WR | _VTPRIM[0] | V | L1, L2, L3; Voltage transformer, primary
6699 | float | RD/WR | _VTPRIM[1] | V | L4; Voltage transformer, primary
6701 | float | RD/WR | _VTSEC[0] | V | L1, L2, L3; Voltage transformer, secondary
6703 | float | RD/WR | _VTSEC[1] | V | L4; Voltage transformer, secondary
6705 | float | RD/WR | _IRATED[0] | A | Nominal current transf.; I L1, I L2, I L3
6707 | float | RD/WR | _IRATED[1] | A | Nominal current transformer; I L4
6709 | float | RD/WR | _NOMINAL_U[0] | V | Nominal voltage; L1, L2, L3
6711 | float | RD/WR | _NOMINAL_U[1] | V | Nominal voltage; L4
6713 | float | RD/WR | _NOMINAL_I[0] | A | Nominal current; L1, L2, L3
6715 | float | RD/WR | _NOMINAL_I[1] | A | Nominal current; L4
6717 | float | RD/WR | _TRNS_DELTA[0] | % | Only for internal use
6719 | float | RD/WR | _TRNS_DELTA[1] | % | Only for internal use
6721 | float | RD/WR | _TRNS_I_ABS[0] | % | Only for internal use
6723 | float | RD/WR | _TRNS_I_ABS[1] | % | Only for internal use
6725 | float | RD/WR | _TRNS_U_ABS[0] | % | Only for internal use
6727 | float | RD/WR | _TRNS_U_ABS[1] | % | Only for internal use
6729 | float | RD/WR | _I_EVT_MAX[0] | % | Only for internal use
6731 | float | RD/WR | _I_EVT_MAX[1] | % | Only for internal use
6733 | float | RD/WR | _U_EVT_MAX[0] | % | Only for internal use
6735 | float | RD/WR | _U_EVT_MAX[1] | % | Only for internal use
6737 | float | RD/WR | _U_EVT_MIN[0] | % | Only for internal use
6739 | float | RD/WR | _U_EVT_MIN[1] | % | Only for internal use
6741 | float | RD/WR | _U_EVT_OFF[0] | % | Only for internal use
6743 | float | RD/WR | _U_EVT_OFF[1] | % | Only for internal use
6745 | float | RD/WR | _NOMINAL_F | Hz | Nominal frequency 50Hz or 60Hz
6747 | short | RD/WR | _FLICKER_SYSTEM |  | Only for internal use
6750 | string | RD/WR | _DEV_NAME | 64 | Only for internal use
6782 | string | RD/WR | _DEV_DESC | 128 | Only for internal use
6846 | string | RD/WR | _LANGUAGE | 16 | Only for internal use
6854 | int | RD/WR | _DISP_LANGUAGE |  | Only for internal use
6856 | uint | RD | _SERNR |  | Only for internal use
6858 | uint | RD | _PRODNR |  | Only for internal use
6860 | int | RD/WR | _MBUSADDR |  | Only for internal use
6862 | int | RD/WR | _MODE485 |  | Only for internal use
6864 | int | RD/WR | _BAUD485 |  | Only for internal use
6866 | uint | RD | _IP_ADDR |  | Network address
6868 | uint | RD | _IP_MASK |  | Network mask
6870 | uint | RD | _IP_GATE |  | Gateway
6872 | int | RD/WR | _DHCPMODE |  | Bootp = 1; off = 0; DHCP = 2
6874 | int | RD/WR | _BRIGHTNESS |  | Brightness display
6876 | short | RD/WR | _STBY_TIME |  | Standby time
6877 | short | RD/WR | _STBY_CONTRAST |  | Standby contrast
6878 | short | RD/WR | _SCREENSASVE |  | Screensaver, 1=on, 0=off
6879 | short | RD/WR | _DISP_SPEED |  | Display change time
6880 | short | RD/WR | _DISP_ROT |  | 0= Autom. display change on
6881 | short | RD/WR | _ROT_TIME |  | Rotation time display
6882 | int | RD/WR | _KEY1 |  | Status button 1
6884 | int | RD/WR | _KEY2 |  | Status button 2
6886 | int | RD/WR | _KEY3 |  | Status button 3
6888 | int | RD/WR | _KEY4 |  | Status button 4
6890 | int | RD/WR | _KEY5 |  | Status button 5
6892 | int | RD/WR | _KEY6 |  | Status button 6
6894 | uint | RD/WR | _DEBUG_IP |  | Only for internal use
6896 | int | RD/WR | _TIME_ZONE | s | Time zone
6898 | int | RD/WR | _STIME | s | Only for internal use
6900 | short | RD/WR | _SDAY |  | Start day of summer/winter switchover (spring)
6901 | short | RD/WR | _SHOUR | h | Start hour of summer/winter switchover
6902 | short | RD/WR | _SMON |  | Start month of summer/winter switchover
6903 | short | RD/WR | _SMIN | min | Start minute of summer/winter switchover
6904 | short | RD/WR | _SDOW |  | Summer/winter switchover (spring)
6905 | short | RD/WR | _EDAY |  | Start day of summer/winter switchover (autumn)
6906 | short | RD/WR | _EHOUR | h | Start hour of summer/winter switchover
6907 | short | RD/WR | _EMON |  | Start month of summer/winter switchover
6908 | short | RD/WR | _EMIN | min | Start minute of summer/winter switchover
6909 | short | RD/WR | _EDOW |  | Summer/winter switchover (autumn)
6910 | int | RD/WR | _WAVE_START_PRE |  | Only for internal use
6912 | int | RD/WR | _WAVE_START_POST |  | Only for internal use
6916 | int | RD/WR | _EVT_VAL_PRE |  | Only for internal use
6918 | int | RD/WR | _EVT_VAL_POST |  | Only for internal use
6920 | int | RD/WR | _TRNS_MODE |  | Only for internal use
6922 | int | RD/WR | _CON_AUX_MODE |  | Only for internal use
6924 | int | RD/WR | _CON_MODE |  | Only for internal use
6926 | int | RD/WR | _PHASE_MODE |  | Only for internal use
6928 | short | RD/WR | _COLOR[0] |  | Only for internal use
6929 | short | RD/WR | _COLOR[1] |  | Only for internal use
6930 | short | RD/WR | _COLOR[2] |  | Only for internal use
6931 | short | RD/WR | _COLOR[3] |  | Only for internal use
6932 | short | RD/WR | _COLOR[4] |  | Only for internal use
6933 | short | RD/WR | _COLOR[5] |  | Only for internal use
6934 | short | RD/WR | _COLOR[6] |  | Only for internal use
6935 | short | RD/WR | _COLOR[7] |  | Only for internal use
6936 | string | RD/WR | _MMENU | 32 | Only for internal use
6952 | string | RD/WR | _LANG | 32 | Only for internal use
6968 | string | RD/WR | _COMM | 32 | Only for internal use
6984 | string | RD/WR | _MMEAS | 32 | Only for internal use
7000 | string | RD/WR | _AMEAS | 32 | Only for internal use
7016 | string | RD/WR | _RECOS | 32 | Only for internal use
7032 | string | RD/WR | _SYST | 32 | Only for internal use
7048 | string | RD/WR | _DISPM | 32 | Only for internal use
7064 | string | RD/WR | _COLORM | 32 | Only for internal use
7080 | string | RD/WR | _FB_BAUD | 32 | Only for internal use
7096 | string | RD/WR | _TCPIP | 32 | Only for internal use
7112 | string | RD/WR | _COMMENU | 32 | Only for internal use
7128 | string | RD/WR | _DHCP | 32 | Only for internal use
7144 | string | RD/WR | _IPNO | 32 | Only for internal use
7160 | string | RD/WR | _NETMASK | 32 | Only for internal use
7176 | string | RD/WR | _GATEWAY | 32 | Only for internal use
7192 | string | RD/WR | _FIELDBUS | 32 | Only for internal use
7208 | string | RD/WR | _COMPORT | 32 | Only for internal use
7224 | string | RD/WR | _PROTOCOL | 32 | Only for internal use
7240 | string | RD/WR | _FBPROT_0 | 32 | Only for internal use
7256 | string | RD/WR | _FBPROT_1 | 32 | Only for internal use
7272 | string | RD/WR | _FBPROT_2 | 32 | Only for internal use
7288 | string | RD/WR | _FB_ADDR | 32 | Only for internal use
7304 | string | RD/WR | _DHCP_0 | 32 | Only for internal use
7320 | string | RD/WR | _DHCP_1 | 32 | Only for internal use
7336 | string | RD/WR | _DHCP_2 | 32 | Only for internal use
7352 | string | RD/WR | _MCIRC | 32 | Only for internal use
7368 | string | RD/WR | _RVOLT | 32 | Only for internal use
7384 | string | RD/WR | _MRF | 32 | Only for internal use
7400 | string | RD/WR | _MVT | 32 | Only for internal use
7416 | string | RD/WR | _MCT | 32 | Only for internal use
7432 | string | RD/WR | _MRV | 32 | Only for internal use
7448 | string | RD/WR | _MRC | 32 | Only for internal use
7464 | string | RD/WR | _FLISYS | 32 | Only for internal use
7480 | string | RD/WR | _EVENTS | 32 | Only for internal use
7496 | string | RD/WR | _TRANS | 32 | Only for internal use
7512 | string | RD/WR | _COLOR | 32 | Only for internal use
7528 | string | RD/WR | _CURRENT | 32 | Only for internal use
7544 | string | RD/WR | _VOLTAGE | 32 | Only for internal use
7560 | string | RD/WR | _RMSLOW | 32 | Only for internal use
7576 | string | RD/WR | _RMSHIGH | 32 | Only for internal use
7592 | string | RD/WR | _RMSINTR | 32 | Only for internal use
7608 | string | RD/WR | _RMSIMAX | 32 | Only for internal use
7624 | string | RD/WR | _OFF_STR | 32 | Only for internal use
7640 | string | RD/WR | _TRNSUPK | 32 | Only for internal use
7656 | string | RD/WR | _TRNSUTR | 32 | Only for internal use
7672 | string | RD/WR | _TRNSIPK | 32 | Only for internal use
7688 | string | RD/WR | _STOPR | 32 | Only for internal use
7704 | string | RD/WR | _STARTR1 | 32 | Only for internal use
7720 | string | RD/WR | _STARTR2 | 32 | Only for internal use
7736 | string | RD/WR | _DELWORK | 32 | Only for internal use
7752 | string | RD/WR | _L_BRIGHTNESS | 32 | Only for internal use
7768 | string | RD/WR | _STANDBY | 32 | Only for internal use
7784 | string | RD/WR | _BRIGHTNESS_LOW | 32 | Only for internal use
7800 | string | RD/WR | _SCREENSAVE | 32 | Only for internal use
7816 | string | RD/WR | _DISP_MODE | 32 | Only for internal use
7832 | string | RD/WR | _ROTATE | 32 | Only for internal use
7848 | string | RD/WR | _ROTATE_TIME | 32 | Only for internal use
7864 | string | RD/WR | _SPEED_LOW | 32 | Only for internal use
7880 | string | RD/WR | _SPEED_HIGH | 32 | Only for internal use
7896 | string | RD/WR | _RECNO | 32 | Only for internal use
7912 | string | RD/WR | _NO_STR | 32 | Only for internal use
7928 | string | RD/WR | _YES_STR | 32 | Only for internal use
7944 | string | RD/WR | _DONE_STR | 32 | Only for internal use
7960 | string | RD/WR | _RUN_STR | 32 | Only for internal use
7976 | string | RD/WR | _STOP_STR | 32 | Only for internal use
7992 | string | RD/WR | _VERSION | 32 | Only for internal use
8008 | string | RD/WR | _IDNO | 32 | Only for internal use
8024 | string | RD/WR | _SERNO | 32 | Only for internal use
8040 | string | RD/WR | _MACADR | 32 | Only for internal use
8056 | string | RD/WR | _PASSW | 32 | Only for internal use
8072 | string | RD/WR | _LANGUAGE_1 | 32 | Only for internal use
8088 | string | RD/WR | _LANGUAGE_2 | 32 | Only for internal use
8104 | string | RD/WR | _LANGUAGE_3 | 32 | Only for internal use
8120 | string | RD/WR | _LANGUAGE_4 | 32 | Only for internal use
8136 | string | RD/WR | _LANGUAGE_5 | 32 | Only for internal use
8152 | string | RD/WR | _LANGUAGE_6 | 32 | Only for internal use
8168 | string | RD/WR | _LANGUAGE_7 | 32 | Only for internal use
8184 | string | RD/WR | _LANGUAGE_8 | 32 | Only for internal use
8200 | string | RD/WR | _LANGUAGE_9 | 32 | Only for internal use
8216 | string | RD/WR | _LANGUAGE_10 | 32 | Only for internal use
8232 | string | RD/WR | _LANGUAGE_11 | 32 | Only for internal use
8248 | string | RD/WR | _LANGUAGE_12 | 32 | Only for internal use
8264 | string | RD/WR | _LANGUAGE_13 | 32 | Only for internal use
8280 | string | RD/WR | _LANGUAGE_14 | 32 | Only for internal use
8296 | string | RD/WR | _LANGUAGE_15 | 32 | Only for internal use
8312 | string | RD/WR | _LANGUAGE_16 | 32 | Only for internal use
8328 | string | RD/WR | _GUEST_PASSWD | 64 | Password, guest
8360 | string | RD/WR | _USER_PASSWD | 64 | Password, user
8392 | string | RD/WR | _ADMIN_PASSWD | 64 | Password, admin
8424 | float | RD/WR | _PULSWERT[0] | Wh/n | Pulse value for input 1
8426 | float | RD/WR | _PULSWERT[1] | Wh/n | Pulse value for input 2
8428 | float | RD/WR | _MAXSIZE_REC | % | Only for internal use
8430 | float | RD/WR | _MAXSIZE_TRNS | % | Only for internal use
8432 | float | RD/WR | _MAXSIZE_VWW | % | Only for internal use
8434 | float | RD/WR | _MAXSIZE_EVT | % | Only for internal use
8436 | float | RD/WR | _MAXSIZE_FLAGS | % | Only for internal use
8438 | int | RD/WR | _TFTP_FILE_NR |  | Only for internal use
8440 | int | RD/WR | _TFTP_NEWFILE |  | Only for internal use
8442 | int | RD/WR | _DIGOUTEVT[0] | bin | Only for internal use
8444 | int | RD/WR | _DIGOUTEVT[1] | bin | Only for internal use
8446 | int | RD/WR | _DIGOUTEVT_TIME[0] | 0.01s | Only for internal use
8448 | int | RD/WR | _DIGOUTEVT_TIME[1] | 0.01s | Only for internal use
8450 | short | RD/WR | _INVERT_DIGOUT[0] | bool | Only for internal use
8451 | short | RD/WR | _INVERT_DIGOUT[1] | bool | Only for internal use
10254 | int | RD | _KORR_INT |  | Only for internal use
10256 | int | RD/WR | _QUARZ_KORR_NTP | ppm | Only for internal use
10258 | float | RD/WR | _RC_FREQ | Hz | Only for internal use
10260 | int | RD/WR | _BACNET_SENDIAM_TIME | s | Only for internal use
10262 | ushort | RD/WR | _HTML_PORT |  | Only for internal use
10263 | string | RD/WR | _IP_ADDR_STR | 32 | Only for internal use
10279 | string | RD/WR | _IP_GATEWAY_STR | 32 | Only for internal use
10295 | string | RD/WR | _IP_MASK_STR | 32 | Only for internal use
10311 | string | RD/WR | _NAMESRV_IP | 32 | Only for internal use
10327 | string | RD/WR | _NTPSRV_IP | 128 | Only for internal use
10391 | string | RD/WR | _HOSTNAME | 64 | Only for internal use
10423 | string | RD/WR | _EVT_NAME | 16 | Only for internal use
10431 | string | RD/WR | _FL_NAME | 16 | Only for internal use
10439 | string | RD/WR | _TR_NAME | 16 | Only for internal use
10447 | string | RD/WR | _HWW_NAME | 16 | Only for internal use
10455 | int | RD/WR | _FILEMAGIC |  | Only for internal use
10457 | int | RD/WR | _MODE_NTP |  | Only for internal use
10459 | int | RD/WR | _QUARZ_KORR | ppm | Only for internal use
10461 | string | RD/WR | _TFTP_PRG1 | 256 | Only for internal use
10589 | string | RD/WR | _TFTP_PRG2 | 256 | Only for internal use
10717 | string | RD/WR | _TFTP_PRG3 | 256 | Only for internal use
10845 | string | RD/WR | _TFTP_PRG4 | 256 | Only for internal use
10973 | string | RD/WR | _TFTP_PRG5 | 256 | Only for internal use
11101 | string | RD/WR | _TFTP_PRG6 | 256 | Only for internal use
11229 | string | RD/WR | _TFTP_REC | 256 | Only for internal use
11357 | string | RD/WR | _TFTP_DISPLAY | 256 | Only for internal use
11485 | string | RD | _RELEASE | 16 | Only for internal use
11493 | string | RD/WR | _DOWNLOAD | 64 | Only for internal use
11525 | int | RD/WR | _JASIC_VAR |  | Only for internal use
11527 | int |  | _DUMMY |  | Only for internal use
11529 | uint | RD/WR | _MASTER_TIMEOUT | msec | Only for internal use
11531 | int | RD/WR | _ED_PASSWD |  | Only for internal use
11533 | int | RD/WR | _HTML_PASSWD |  | Password HTML
11535 | int | RD/WR | _PASSWD_MODE |  | Password mode
11537 | float | RD | _CHALLENGE |  | Only for internal use
11539 | uint | RD | _EMAX_PASSWORD |  | Passwort EMAX
11541 | uint | RD | _BACNET_PASSWORD |  | Passwort BACnet
11543 | short | RD | _FORBID_HTML |  | Only for internal use
11544 | short | RD | _FORBID_CFG_HTML |  | Only for internal use
11545 | short | RD | _FORBID_FTP |  | Only for internal use
11546 | short | RD | _FORBID_CFG_FTP |  | Only for internal use
11547 | short | RD | _FORBID_MODETH |  | Only for internal use
11548 | short | RD | _FORBID_CFG_MODETH |  | Only for internal use
11549 | short | RD | _FORBID_BACNET |  | Only for internal use
11550 | short | RD | _IP_UP |  | Only for internal use
11551 | short | RD | _SYSVAR_CNT |  | Only for internal use
11552 | string | RD/WR | _SEQ_IP0 | 32 | Only for internal use
11568 | string | RD/WR | _SEQ_IP1 | 32 | Only for internal use
11584 | string | RD/WR | _SEQ_IP2 | 32 | Only for internal use
11600 | string | RD/WR | _SEQ_IP3 | 32 | Only for internal use
11616 | string | RD/WR | _SEQ_IP4 | 32 | Only for internal use
11632 | string | RD/WR | _SEQ_IP5 | 32 | Only for internal use
11648 | string | RD/WR | _SEQ_IP6 | 32 | Only for internal use
11664 | string | RD/WR | _SEQ_IP7 | 32 | Only for internal use
11680 | short | RD/WR | _CH_MAP[0] |  | Only for internal use
11681 | short | RD/WR | _CH_MAP[1] |  | Only for internal use
11682 | short | RD/WR | _CH_MAP[2] |  | Only for internal use
11683 | short | RD/WR | _CH_MAP[3] |  | Only for internal use
11684 | short | RD/WR | _CH_MAP[4] |  | Only for internal use
11685 | short | RD/WR | _CH_MAP[5] |  | Only for internal use
11686 | short | RD/WR | _CH_MAP[6] |  | Only for internal use
11687 | short | RD/WR | _CH_MAP[7] |  | Only for internal use
11688 | float | RD | _NTP_DIV | s | Only for internal use
11690 | float | RD | _NTP_TURNAROUND | s | Only for internal use
11692 | float | RD | _NTP_KORR | ppm | Only for internal use
11694 | long64 | RD/WR | _RX_ETH_COUNT |  | Only for internal use
11698 | long64 | RD/WR | _TX_ETH_COUNT |  | Only for internal use
11702 | long64 | RD/WR | _ERR_ETH_COUNT |  | Only for internal use
11706 | long64 | RD/WR | _RX_NTP_COUNT |  | Only for internal use
11710 | long64 | RD/WR | _TX_NTP_COUNT |  | Only for internal use
11714 | long64 | RD/WR | _ERR_NTP_COUNT |  | Only for internal use
11718 | long64 | RD/WR | _RX_DNS_COUNT |  | Only for internal use
11722 | long64 | RD/WR | _TX_DNS_COUNT |  | Only for internal use
11726 | long64 | RD/WR | _ERR_DNS_COUNT |  | Only for internal use
11730 | long64 | RD/WR | _RX_DHCP_COUNT |  | Only for internal use
11734 | long64 | RD/WR | _TX_DHCP_COUNT |  | Only for internal use
11738 | long64 | RD/WR | _ERR_DHCP_COUNT |  | Only for internal use
11742 | long64 | RD/WR | _TX_EMAIL_COUNT |  | Only for internal use
11746 | long64 | RD/WR | _ERR_EMAIL_COUNT |  | Only for internal use
11750 | int | RD/WR | _MTU_SIZE |  | Only for internal use
11752 | long64 | RD | _SYSTIMEUP | 10ms | Only for internal use
11828 | float | RD/WR | _SNMP_USERVAR[0] |  | Only for internal use
11830 | float | RD/WR | _SNMP_USERVAR[1] |  | Only for internal use
11832 | float | RD/WR | _SNMP_USERVAR[2] |  | Only for internal use
11834 | float | RD/WR | _SNMP_USERVAR[3] |  | Only for internal use
11836 | float | RD/WR | _SNMP_USERVAR[4] |  | Only for internal use
11838 | float | RD/WR | _SNMP_USERVAR[5] |  | Only for internal use
11840 | float | RD/WR | _SNMP_USERVAR[6] |  | Only for internal use
11842 | float | RD/WR | _SNMP_USERVAR[7] |  | Only for internal use
11844 | float | RD/WR | _SNMP_USERVAR[8] |  | Only for internal use
11846 | float | RD/WR | _SNMP_USERVAR[9] |  | Only for internal use
11848 | float | RD/WR | _SNMP_USERVAR[10] |  | Only for internal use
11850 | float | RD/WR | _SNMP_USERVAR[11] |  | Only for internal use
11852 | float | RD/WR | _SNMP_USERVAR[12] |  | Only for internal use
11854 | float | RD/WR | _SNMP_USERVAR[13] |  | Only for internal use
11856 | float | RD/WR | _SNMP_USERVAR[14] |  | Only for internal use
11858 | float | RD/WR | _SNMP_USERVAR[15] |  | Only for internal use
11860 | double | RD | _AKT_EVT_START[0] | s | Only for internal use
11864 | double | RD | _AKT_EVT_START[1] | s | Only for internal use
11868 | double | RD | _AKT_EVT_START[2] | s | Only for internal use
11872 | double | RD | _AKT_EVT_START[3] | s | Only for internal use
11876 | double | RD | _AKT_EVT_START[4] | s | Only for internal use
11880 | double | RD | _AKT_EVT_START[5] | s | Only for internal use
11884 | double | RD | _AKT_EVT_START[6] | s | Only for internal use
11888 | double | RD | _AKT_EVT_START[7] | s | Only for internal use
11892 | double | RD | _AKT_EVT_STOP[0] | s | Only for internal use
11896 | double | RD | _AKT_EVT_STOP[1] | s | Only for internal use
11900 | double | RD | _AKT_EVT_STOP[2] | s | Only for internal use
11904 | double | RD | _AKT_EVT_STOP[3] | s | Only for internal use
11908 | double | RD | _AKT_EVT_STOP[4] | s | Only for internal use
11912 | double | RD | _AKT_EVT_STOP[5] | s | Only for internal use
11916 | double | RD | _AKT_EVT_STOP[6] | s | Only for internal use
11920 | double | RD | _AKT_EVT_STOP[7] | s | Only for internal use
11924 | float | RD | _AKT_EVT_BOUND[0] |  | Only for internal use
11926 | float | RD | _AKT_EVT_BOUND[1] |  | Only for internal use
11928 | float | RD | _AKT_EVT_BOUND[2] |  | Only for internal use
11930 | float | RD | _AKT_EVT_BOUND[3] |  | Only for internal use
11932 | float | RD | _AKT_EVT_BOUND[4] |  | Only for internal use
11934 | float | RD | _AKT_EVT_BOUND[5] |  | Only for internal use
11936 | float | RD | _AKT_EVT_BOUND[6] |  | Only for internal use
11938 | float | RD | _AKT_EVT_BOUND[7] |  | Only for internal use
11940 | float | RD | _AKT_EVT_MAXVAL[0] |  | Only for internal use
11942 | float | RD | _AKT_EVT_MAXVAL[1] |  | Only for internal use
11944 | float | RD | _AKT_EVT_MAXVAL[2] |  | Only for internal use
11946 | float | RD | _AKT_EVT_MAXVAL[3] |  | Only for internal use
11948 | float | RD | _AKT_EVT_MAXVAL[4] |  | Only for internal use
11950 | float | RD | _AKT_EVT_MAXVAL[5] |  | Only for internal use
11952 | float | RD | _AKT_EVT_MAXVAL[6] |  | Only for internal use
11954 | float | RD | _AKT_EVT_MAXVAL[7] |  | Only for internal use
11956 | float | RD | _AKT_EVT_MINVAL[0] |  | Only for internal use
11958 | float | RD | _AKT_EVT_MINVAL[1] |  | Only for internal use
11960 | float | RD | _AKT_EVT_MINVAL[2] |  | Only for internal use
11962 | float | RD | _AKT_EVT_MINVAL[3] |  | Only for internal use
11964 | float | RD | _AKT_EVT_MINVAL[4] |  | Only for internal use
11966 | float | RD | _AKT_EVT_MINVAL[5] |  | Only for internal use
11968 | float | RD | _AKT_EVT_MINVAL[6] |  | Only for internal use
11970 | float | RD | _AKT_EVT_MINVAL[7] |  | Only for internal use
11972 | float | RD | _AKT_EVT_AVG[0] |  | Only for internal use
11974 | float | RD | _AKT_EVT_AVG[1] |  | Only for internal use
11976 | float | RD | _AKT_EVT_AVG[2] |  | Only for internal use
11978 | float | RD | _AKT_EVT_AVG[3] |  | Only for internal use
11980 | float | RD | _AKT_EVT_AVG[4] |  | Only for internal use
11982 | float | RD | _AKT_EVT_AVG[5] |  | Only for internal use
11984 | float | RD | _AKT_EVT_AVG[6] |  | Only for internal use
11986 | float | RD | _AKT_EVT_AVG[7] |  | Only for internal use
11988 | long64 | RD | _AKT_EVT_REASON[0] |  | Only for internal use
11992 | long64 | RD | _AKT_EVT_REASON[1] |  | Only for internal use
11996 | long64 | RD | _AKT_EVT_REASON[2] |  | Only for internal use
12000 | long64 | RD | _AKT_EVT_REASON[3] |  | Only for internal use
12004 | long64 | RD | _AKT_EVT_REASON[4] |  | Only for internal use
12008 | long64 | RD | _AKT_EVT_REASON[5] |  | Only for internal use
12012 | long64 | RD | _AKT_EVT_REASON[6] |  | Only for internal use
12016 | long64 | RD | _AKT_EVT_REASON[7] |  | Only for internal use
12020 | int | RD | _AKT_EVT_CNT[0] |  | Only for internal use
12022 | int | RD | _AKT_EVT_CNT[1] |  | Only for internal use
12024 | int | RD | _AKT_EVT_CNT[2] |  | Only for internal use
12026 | int | RD | _AKT_EVT_CNT[3] |  | Only for internal use
12028 | int | RD | _AKT_EVT_CNT[4] |  | Only for internal use
12030 | int | RD | _AKT_EVT_CNT[5] |  | Only for internal use
12032 | int | RD | _AKT_EVT_CNT[6] |  | Only for internal use
12034 | int | RD | _AKT_EVT_CNT[7] |  | Only for internal use
12036 | int | RD/WR | _HW_INDEX |  | Device hardware index
12498 | string | RD/WR | _PASSWDM | 32 | Only for internal use
12514 | string | RD/WR | _BACNET_PW | 32 | Only for internal use
12530 | string | RD/WR | _EMAX_PW | 32 | Only for internal use
12546 | string | RD/WR | _HTML_PW | 32 | Only for internal use
12562 | string | RD/WR | _HTML_PW_MODE | 32 | Only for internal use
12578 | int | RD/WR | _SET_BACNAME_INSTACE |  | Only for internal use
12580 | string | RD/WR | _ALLOCATIONS | 32 | Only for internal use
12596 | string | RD/WR | _PRIMARY | 32 | Only for internal use
12612 | string | RD/WR | _SECONDARY | 32 | Only for internal use
12628 | string | RD/WR | _CT_TRANSFORMER | 32 | Only for internal use
12644 | string | RD/WR | _VT_TRANSFORMER | 32 | Only for internal use
12660 | string | RD/WR | _NOMINAL_CURRENT | 32 | Only for internal use
12676 | string | RD/WR | _NOMINAL_VOLTAGE | 32 | Only for internal use
12692 | string | RD/WR | _TRANSFER | 32 | Only for internal use
12708 | string | RD/WR | _STR_PHASE | 32 | Only for internal use
12724 | string | RD/WR | _TRANSFORMER | 32 | Only for internal use
12740 | string | RD/WR | _EVENTS | 32 | Only for internal use
12756 | string | RD/WR | _TRANSIENTS | 32 | Only for internal use
12772 | string | RD/WR | _MODE_ABS | 32 | Only for internal use
12788 | string | RD/WR | _MODE_ABS_I | 32 | Only for internal use
12804 | string | RD/WR | _MODE_DELTA | 32 | Only for internal use
12820 | string | RD/WR | _NO_STR | 32 | Only for internal use
12836 | string | RD/WR | _YES_STR | 32 | Only for internal use
12852 | string | RD/WR | _DONE | 32 | Only for internal use
12868 | string | RD/WR | _MANUALLY | 32 | Only for internal use
12884 | string | RD/WR | _AUTOMATICALLY | 32 | Only for internal use
12900 | string | RD/WR | _OFF | 32 | Only for internal use
12916 | short | RD/WR | _PULS_WIDTH |  | Only for internal use
12917 | string | RD/WR | _RVOLT_0 | 32 | Only for internal use
12933 | string | RD/WR | _RVOLT_1 | 32 | Only for internal use
12949 | string | RD/WR | _FREQ_STR_0 | 32 | Only for internal use
12965 | string | RD/WR | _FREQ_STR_1 | 32 | Only for internal use
12981 | string | RD/WR | _FREQ_STR_2 | 32 | Only for internal use
12997 | string | RD/WR | _FLI_STR_0 | 32 | Only for internal use
13013 | string | RD/WR | _FLI_STR_1 | 32 | Only for internal use
13029 | string | RD/WR | _FLI_STR_2 | 32 | Only for internal use
13045 | string | RD/WR | _FLI_STR_3 | 32 | Only for internal use
13061 | string | RD/WR | _MODE_ENV | 32 | Only for internal use
13077 | string | RD/WR | _TRNSENV | 32 | Only for internal use
13093 | float | RD/WR | _TRNS_ENVELOPE[0] | % | Only for internal use
13095 | float | RD/WR | _TRNS_ENVELOPE[1] | % | Only for internal use
13111 | float | RD | _U_SYM_AVG_U0 | % | Only for internal use
13113 | float | RD | _U_SYM_MIN_U0 | % | Only for internal use
13115 | float | RD | _U_SYM_MAX_U0 | % | Only for internal use
13117 | short | RD/WR | _U_SYM_AVG_T_U0 |  | Only for internal use
13118 | short | RD/WR | _U_SYM_MIN_T_U0 |  | Only for internal use
13119 | short | RD/WR | _U_SYM_MAX_T_U0 |  | Only for internal use
13120 | string | RD/WR | _MAIN_STR | 32 | Only for internal use
13136 | string | RD/WR | _AUX_STR | 32 | Only for internal use
13152 | string | RD/WR | _CP_DEL_MINMAX | 32 | Only for internal use
13168 | string | RD/WR | _CP_BACNET | 32 | Only for internal use
13184 | string | RD/WR | _CP_COLOR | 32 | Only for internal use
13200 | string | RD/WR | _CP_RELEASE | 32 | Only for internal use
13216 | string | RD/WR | _CP_MEASURMENT | 32 | Only for internal use
13232 | string | RD/WR | _CP_DELIVERY_STATE | 32 | Only for internal use
13248 | string | RD/WR | _CP_RE_INIT | 32 | Only for internal use
13264 | string | RD/WR | _CP_RESET | 32 | Only for internal use
13280 | string | RD/WR | _CP_DATE_TIME | 32 | Only for internal use
13296 | string | RD/WR | _CP_JASIC | 32 | Only for internal use
13312 | string | RD/WR | _CP_RECORD | 32 | Only for internal use
13328 | string | RD/WR | _CP_EXTENSION | 32 | Only for internal use
13344 | string | RD/WR | _CP_EMAX | 32 | Only for internal use
13360 | string | RD/WR | _TRNSENV | 32 | Only for internal use
13376 | string | RD/WR | _MODE_ENV | 32 | Only for internal use
13392 | uint | RD/WR | _MB_STATUS |  | Only for internal use
13394 | int | RD/WR | _SET_SYSTIME | sec | Only for internal use
13396 | string | RD | _SNMP_OID | 32 | Only for internal use
13412 | ushort | RD/WR | _SMTP_PORT | n | Only for internal use
13413 | float | RD | _IND_CAP_SUM3 |  | Sign, Q1 + Q2 + Q3
13415 | float | RD | _IND_CAP_SUM |  | Sign, Q1 + Q2 + Q3 + Q4
13417 | string | RD/WR | _CP_DREILEITER | 32 | Only for internal use
13433 | string | RD/WR | _CP_ARON | 32 | Only for internal use
13449 | float | RD/WR | _I_EVT_MAX_HYST[0] | % | Only for internal use
13451 | float | RD/WR | _I_EVT_MAX_HYST[1] | % | Only for internal use
13453 | float | RD/WR | _U_EVT_MAX_HYST[0] | % | Only for internal use
13455 | float | RD/WR | _U_EVT_MAX_HYST[1] | % | Only for internal use
13457 | float | RD/WR | _U_EVT_MIN_HYST[0] | % | Only for internal use
13459 | float | RD/WR | _U_EVT_MIN_HYST[1] | % | Only for internal use
13461 | float | RD/WR | _U_EVT_OFF_HYST[0] | % | Only for internal use
13463 | float | RD/WR | _U_EVT_OFF_HYST[1] | % | Only for internal use
13533 | int | RD/WR | _ETERNET_TIMEOUT |  | Only for internal use
13535 | int | RD/WR | _FIREWALL |  | Only for internal use
13537 | short | RD/WR | _MAC_01 |  | Only for internal use
13538 | short | RD/WR | _MAC_23 |  | Only for internal use
13539 | short | RD/WR | _MAC_45 |  | Only for internal use
13540 | short | RD/WR | _FLUSH_DEV |  | Only for internal use
13541 | uint | RD/WR | _RECORD_TIME |  | Only for internal use
13543 | int | RD/WR | _CONFIG_P15_VAL |  | Only for internal use
13545 | int | RD/WR | _CONFIG_P15_TIME |  | Only for internal use
13547 | uint | RD/WR | _BACNET_BBMD_IP |  | Configure bacnet foreign device registration:
BBMD IP
13549 | ushort | RD/WR | _BACNET_BBMD_PORT |  | Configure bacnet foreign device registration:
BBMD Port
13550 | ushort | RD/WR | _BACNET_VNET |  | BACnet network number for vnet.
Set to 0 to reset to unique value
13551 | ushort | RD/WR | _BACNET_NAMEPREFIX |  | Disable underscore before object names (1)
13552 | string | RD/WR | _DIGIN_NAME0 | 32 | Name, Input 1
13568 | string | RD/WR | _DIGIN_UNIT0 | 32 | Unit, Input 1
13584 | string | RD/WR | _DIGIN_DESCRIPTION0 | 128 | Description, Input 1
13648 | string | RD/WR | _DIGIN_NAME1 | 32 | Name, Input 2
13664 | string | RD/WR | _DIGIN_UNIT1 | 32 | Unit, Input 2
13680 | string | RD/WR | _DIGIN_DESCRIPTION1 | 128 | Description, Input 2
13744 | float | RD/WR | _ULL_EVT_MAX | % | Only for internal use
13746 | float | RD/WR | _ULL_EVT_MIN | % | Only for internal use
13748 | float | RD/WR | _ULL_EVT_OFF | % | Only for internal use
13750 | float | RD/WR | _ULL_EVT_MAX_HYST | % | Only for internal use
13752 | float | RD/WR | _ULL_EVT_MIN_HYST | % | Only for internal use
13754 | float | RD/WR | _ULL_EVT_OFF_HYST | % | Only for internal use
13756 | float | RD/WR | _FREQ_EVT_MAX[0] | % | Only for internal use
13758 | float | RD/WR | _FREQ_EVT_MAX[1] | % | Only for internal use
13760 | float | RD/WR | _FREQ_EVT_MIN[0] | % | Only for internal use
13762 | float | RD/WR | _FREQ_EVT_MIN[1] | % | Only for internal use
13764 | float | RD/WR | _FREQ_EVT_DT[0] | % | Only for internal use
13766 | float | RD/WR | _FREQ_EVT_DT[1] | % | Only for internal use
13768 | float | RD/WR | _FREQ_EVT_MAX_HYST[0] | % | Only for internal use
13770 | float | RD/WR | _FREQ_EVT_MAX_HYST[1] | % | Only for internal use
13772 | float | RD/WR | _FREQ_EVT_MIN_HYST[0] | % | Only for internal use
13774 | float | RD/WR | _FREQ_EVT_MIN_HYST[1] | % | Only for internal use
13776 | float | RD/WR | _FREQ_EVT_DT_HYST[0] | % | Only for internal use
13778 | float | RD/WR | _FREQ_EVT_DT_HYST[1] | % | Only for internal use
13780 | short | RD/WR | _TRANS_PROTECTION | % | Only for internal use
13781 | int | RD/WR | _FREQ_PHASE_COUNT |  | Only for internal use
13783 | float | RD/WR | _IDIFF_PRIM[0] | A | RC transformer, primary 1
13785 | float | RD/WR | _IDIFF_PRIM[1] | A | RC transformer, primary 2
13787 | float | RD/WR | _IDIFF_SEC[0] | A | RC transformer, secondary 1
13789 | float | RD/WR | _IDIFF_SEC[1] | A | RC transformer, secondary 2
13791 | float | RD/WR | _TEMPERATUR_OFFSET | °C | Temperatur offset
13793 | int | RD/WR | _IDIFF_MODE[0] | A | Failure monitoring, diff 1
0 = deactivate, 1 = activate
13795 | int | RD/WR | _IDIFF_MODE[1] | A | Failure monitoring, diff 2
0 = deactivate, 1 = activate
13797 | int | RD/WR | _THERMOELEMENT |  | Thermal element
13799 | float | RD/WR | _IDIFF[0] | A
13801 | float | RD/WR | _IDIFF[1] | A
13803 | float | RD/WR | _EXT_TEMP | V | external temperatur
13805 | short | RD/WR | _IDIFF_BREAK[0] |  | Connection to RC transformer, diff 1
0 = error free, 1 = error
13806 | short | RD/WR | _IDIFF_BREAK[1] |  | Connection to RC transformer, diff 2
0 = error free, 1 = error
13807 | short | RD/WR | _COMP_DIFF_TYPE0 | s | Only for internal use
13808 | ushort | RD/WR | _COMP_DIFF_REF_ADDR0 | s | Only for internal use
13809 | float | RD/WR | _COMP_DIFF_PER_DEV0 | s | Only for internal use
13811 | short | RD/WR | _COMP_DIFF_DEV_CNT0 | s | Only for internal use
13812 | float | RD/WR | _COMP_DIFF_CUR_PER0 | s | Only for internal use
13814 | float | RD/WR | _COMP_DIFF_CUR_OFFSET0 | s | Only for internal use
13816 | float | RD/WR | _COMP_DIFF_TOLERANCE0 | s | Only for internal use
13818 | float | RD/WR | _COMP_DIFF_WARNLEVEL0 | s | Only for internal use
13820 | float | RD/WR | _COMP_DIFF_STEP_THRESHOLD0[0] | s | Only for internal use
13822 | float | RD/WR | _COMP_DIFF_STEP_THRESHOLD0[1] | s | Only for internal use
13824 | float | RD/WR | _COMP_DIFF_STEP_THRESHOLD0[2] | s | Only for internal use
13826 | float | RD/WR | _COMP_DIFF_STEP_THRESHOLD0[3] | s | Only for internal use
13828 | float | RD/WR | _COMP_DIFF_STEP_THRESHOLD0[4] | s | Only for internal use
13830 | float | RD/WR | _COMP_DIFF_STEP_THRESHOLD0[5] | s | Only for internal use
13832 | float | RD/WR | _COMP_DIFF_STEP_THRESHOLD0[6] | s | Only for internal use
13834 | float | RD/WR | _COMP_DIFF_STEP_THRESHOLD0[7] | s | Only for internal use
13836 | float | RD/WR | _COMP_DIFF_STEP_THRESHOLD0[8] | s | Only for internal use
13838 | float | RD/WR | _COMP_DIFF_STEP_THRESHOLD0[9] | s | Only for internal use
13840 | float | RD/WR | _COMP_DIFF_STEPS0[0] | s | Only for internal use
13842 | float | RD/WR | _COMP_DIFF_STEPS0[1] | s | Only for internal use
13844 | float | RD/WR | _COMP_DIFF_STEPS0[2] | s | Only for internal use
13846 | float | RD/WR | _COMP_DIFF_STEPS0[3] | s | Only for internal use
13848 | float | RD/WR | _COMP_DIFF_STEPS0[4] | s | Only for internal use
13850 | float | RD/WR | _COMP_DIFF_STEPS0[5] | s | Only for internal use
13852 | float | RD/WR | _COMP_DIFF_STEPS0[6] | s | Only for internal use
13854 | float | RD/WR | _COMP_DIFF_STEPS0[7] | s | Only for internal use
13856 | float | RD/WR | _COMP_DIFF_STEPS0[8] | s | Only for internal use
13858 | float | RD/WR | _COMP_DIFF_STEPS0[9] | s | Only for internal use
13860 | float | RD/WR | _COMP_DIFF_CUR_THRESHOLD0 | s | Only for internal use
13862 | float | RD/WR | _COMP_DIFF_MIN_TIME0 | s | Only for internal use
13864 | short | RD/WR | _COMP_DIFF_TYPE1 | s | Only for internal use
13865 | ushort | RD/WR | _COMP_DIFF_REF_ADDR1 | s | Only for internal use
13866 | float | RD/WR | _COMP_DIFF_PER_DEV1 | s | Only for internal use
13868 | short | RD/WR | _COMP_DIFF_DEV_CNT1 | s | Only for internal use
13869 | float | RD/WR | _COMP_DIFF_CUR_PER1 | s | Only for internal use
13871 | float | RD/WR | _COMP_DIFF_CUR_OFFSET1 | s | Only for internal use
13873 | float | RD/WR | _COMP_DIFF_TOLERANCE1 | s | Only for internal use
13875 | float | RD/WR | _COMP_DIFF_WARNLEVEL1 | s | Only for internal use
13877 | float | RD/WR | _COMP_DIFF_STEP_THRESHOLD1[0] | s | Only for internal use
13879 | float | RD/WR | _COMP_DIFF_STEP_THRESHOLD1[1] | s | Only for internal use
13881 | float | RD/WR | _COMP_DIFF_STEP_THRESHOLD1[2] | s | Only for internal use
13883 | float | RD/WR | _COMP_DIFF_STEP_THRESHOLD1[3] | s | Only for internal use
13885 | float | RD/WR | _COMP_DIFF_STEP_THRESHOLD1[4] | s | Only for internal use
13887 | float | RD/WR | _COMP_DIFF_STEP_THRESHOLD1[5] | s | Only for internal use
13889 | float | RD/WR | _COMP_DIFF_STEP_THRESHOLD1[6] | s | Only for internal use
13891 | float | RD/WR | _COMP_DIFF_STEP_THRESHOLD1[7] | s | Only for internal use
13893 | float | RD/WR | _COMP_DIFF_STEP_THRESHOLD1[8] | s | Only for internal use
13895 | float | RD/WR | _COMP_DIFF_STEP_THRESHOLD1[9] | s | Only for internal use
13897 | float | RD/WR | _COMP_DIFF_STEPS1[0] | s | Only for internal use
13899 | float | RD/WR | _COMP_DIFF_STEPS1[1] | s | Only for internal use
13901 | float | RD/WR | _COMP_DIFF_STEPS1[2] | s | Only for internal use
13903 | float | RD/WR | _COMP_DIFF_STEPS1[3] | s | Only for internal use
13905 | float | RD/WR | _COMP_DIFF_STEPS1[4] | s | Only for internal use
13907 | float | RD/WR | _COMP_DIFF_STEPS1[5] | s | Only for internal use
13909 | float | RD/WR | _COMP_DIFF_STEPS1[6] | s | Only for internal use
13911 | float | RD/WR | _COMP_DIFF_STEPS1[7] | s | Only for internal use
13913 | float | RD/WR | _COMP_DIFF_STEPS1[8] | s | Only for internal use
13915 | float | RD/WR | _COMP_DIFF_STEPS1[9] | s | Only for internal use
13917 | float | RD/WR | _COMP_DIFF_CUR_THRESHOLD1 | s | Only for internal use
13919 | float | RD/WR | _COMP_DIFF_MIN_TIME1 | s | Only for internal use
13921 | short | RD/WR | _COMP_DIFF_STATUS[0] | s | Alarm status for diff 1 with:
[6 empty] | Bit 0 | = | Warning
[6 empty] | Bit 1 | = | Overcurrent
[6 empty] | Bit 2 | = | Alarm
[6 empty] | Bit 0 | = | CT not connected
13922 | short | RD/WR | _COMP_DIFF_STATUS[1] | s | Alarm status for diff 2 with:
[6 empty] | Bit 0 | = | Warning
[6 empty] | Bit 1 | = | Overcurrent
[6 empty] | Bit 2 | = | Alarm
[6 empty] | Bit 0 | = | CT not connected
13923 | float | RD/WR | _COMP_DIFF_RUN_TIME[0] | s | Overcurrent duration, diff 1
13925 | float | RD/WR | _COMP_DIFF_RUN_TIME[1] | s | Overcurrent duration, diff 2
13927 | float | RD/WR | _COMP_DIFF_LIMIT[0] | A | Real threshold diff 1
13929 | float | RD/WR | _COMP_DIFF_LIMIT[1] | A | Real threshold diff 2
13931 | short | RD/WR | _BLACKOUT_EVT_PHASE |  | Only for internal use
13932 | short | RD/WR | _BLACKOUT_EVT_DELAY |  | Only for internal use
13933 | float | RD/WR | _BLACKOUT_EVT_LEVEL |  | Only for internal use
13935 | int | RD/WR | _EVT_STOP_PRE |  | Only for internal use
13937 | int | RD/WR | _EVT_STOP_POST |  | Only for internal use
14083 | int | RD/WR | _DC_IDFF[0] |  | Only for internal use
14085 | int | RD/WR | _DC_IDFF[1] |  | Only for internal use
14087 | int | RD/WR | _INIT_CUSTOMKEY |  | Only for internal use
14089 | int | RD/WR | _WAVE_STOP_PRE |  | Only for internal use
14091 | int | RD/WR | _WAVE_STOP_POST |  | Only for internal use
14093 | int | RD/WR | _TRNS_PRE |  | Only for internal use
14095 | int | RD/WR | _TRNS_POST |  | Only for internal use
Fourier analysis
Measured values, fourier analysis
Address | Format | RD/WR | Designation | Unit | Note
13 | float | RD | _FFT_ULL1[0] | V | 1. Harmonic U L1..L2
15 | float | RD | _FFT_ULL1[1] | V | 2. Harmonic U L1..L2
17 | float | RD | _FFT_ULL1[2] | V | 3. Harmonic U L1..L2
19 | float | RD | _FFT_ULL1[3] | V | 4. Harmonic U L1..L2
21 | float | RD | _FFT_ULL1[4] | V | 5. Harmonic U L1..L2
23 | float | RD | _FFT_ULL1[5] | V | 6. Harmonic U L1..L2
25 | float | RD | _FFT_ULL1[6] | V | 7. Harmonic U L1..L2
27 | float | RD | _FFT_ULL1[7] | V | 8. Harmonic U L1..L2
29 | float | RD | _FFT_ULL1[8] | V | 9. Harmonic U L1..L2
31 | float | RD | _FFT_ULL1[9] | V | 10. Harmonic U L1..L2
33 | float | RD | _FFT_ULL1[10] | V | 11. Harmonic U L1..L2
35 | float | RD | _FFT_ULL1[11] | V | 12. Harmonic U L1..L2
37 | float | RD | _FFT_ULL1[12] | V | 13. Harmonic U L1..L2
39 | float | RD | _FFT_ULL1[13] | V | 14. Harmonic U L1..L2
41 | float | RD | _FFT_ULL1[14] | V | 15. Harmonic U L1..L2
43 | float | RD | _FFT_ULL1[15] | V | 16. Harmonic U L1..L2
45 | float | RD | _FFT_ULL1[16] | V | 17. Harmonic U L1..L2
47 | float | RD | _FFT_ULL1[17] | V | 18. Harmonic U L1..L2
49 | float | RD | _FFT_ULL1[18] | V | 19. Harmonic U L1..L2
51 | float | RD | _FFT_ULL1[19] | V | 20. Harmonic U L1..L2
53 | float | RD | _FFT_ULL1[20] | V | 21. Harmonic U L1..L2
55 | float | RD | _FFT_ULL1[21] | V | 22. Harmonic U L1..L2
57 | float | RD | _FFT_ULL1[22] | V | 23. Harmonic U L1..L2
59 | float | RD | _FFT_ULL1[23] | V | 24. Harmonic U L1..L2
61 | float | RD | _FFT_ULL1[24] | V | 25. Harmonic U L1..L2
63 | float | RD | _FFT_ULL1[25] | V | 26. Harmonic U L1..L2
65 | float | RD | _FFT_ULL1[26] | V | 27. Harmonic U L1..L2
67 | float | RD | _FFT_ULL1[27] | V | 28. Harmonic U L1..L2
69 | float | RD | _FFT_ULL1[28] | V | 29. Harmonic U L1..L2
71 | float | RD | _FFT_ULL1[29] | V | 30. Harmonic U L1..L2
73 | float | RD | _FFT_ULL1[30] | V | 31. Harmonic U L1..L2
75 | float | RD | _FFT_ULL1[31] | V | 32. Harmonic U L1..L2
77 | float | RD | _FFT_ULL1[32] | V | 33. Harmonic U L1..L2
79 | float | RD | _FFT_ULL1[33] | V | 34. Harmonic U L1..L2
81 | float | RD | _FFT_ULL1[34] | V | 35. Harmonic U L1..L2
83 | float | RD | _FFT_ULL1[35] | V | 36. Harmonic U L1..L2
85 | float | RD | _FFT_ULL1[36] | V | 37. Harmonic U L1..L2
87 | float | RD | _FFT_ULL1[37] | V | 38. Harmonic U L1..L2
89 | float | RD | _FFT_ULL1[38] | V | 39. Harmonic U L1..L2
91 | float | RD | _FFT_ULL1[39] | V | 40. Harmonic U L1..L2
93 | float | RD | _FFT_ULL1[40] | V | 41. Harmonic U L1..L2
95 | float | RD | _FFT_ULL1[41] | V | 42. Harmonic U L1..L2
97 | float | RD | _FFT_ULL1[42] | V | 43. Harmonic U L1..L2
99 | float | RD | _FFT_ULL1[43] | V | 44. Harmonic U L1..L2
101 | float | RD | _FFT_ULL1[44] | V | 45. Harmonic U L1..L2
103 | float | RD | _FFT_ULL1[45] | V | 46. Harmonic U L1..L2
105 | float | RD | _FFT_ULL1[46] | V | 47. Harmonic U L1..L2
107 | float | RD | _FFT_ULL1[47] | V | 48. Harmonic U L1..L2
109 | float | RD | _FFT_ULL1[48] | V | 49. Harmonic U L1..L2
111 | float | RD | _FFT_ULL1[49] | V | 50. Harmonic U L1..L2
113 | float | RD | _FFT_ULL1[50] | V | 51. Harmonic U L1..L2
115 | float | RD | _FFT_ULL1[51] | V | 52. Harmonic U L1..L2
117 | float | RD | _FFT_ULL1[52] | V | 53. Harmonic U L1..L2
119 | float | RD | _FFT_ULL1[53] | V | 54. Harmonic U L1..L2
121 | float | RD | _FFT_ULL1[54] | V | 55. Harmonic U L1..L2
123 | float | RD | _FFT_ULL1[55] | V | 56. Harmonic U L1..L2
125 | float | RD | _FFT_ULL1[56] | V | 57. Harmonic U L1..L2
127 | float | RD | _FFT_ULL1[57] | V | 58. Harmonic U L1..L2
129 | float | RD | _FFT_ULL1[58] | V | 59. Harmonic U L1..L2
131 | float | RD | _FFT_ULL1[59] | V | 60. Harmonic U L1..L2
133 | float | RD | _FFT_ULL1[60] | V | 61. Harmonic U L1..L2
135 | float | RD | _FFT_ULL1[61] | V | 62. Harmonic U L1..L2
137 | float | RD | _FFT_ULL1[62] | V | 62. Harmonic U L1..L2
139 | float | RD | _FFT_ULL2[0] | V | 1. Harmonic U L2..L3
141 | float | RD | _FFT_ULL2[1] | V | 2. Harmonic U L2..L3
143 | float | RD | _FFT_ULL2[2] | V | 3. Harmonic U L2..L3
145 | float | RD | _FFT_ULL2[3] | V | 4. Harmonic U L2..L3
147 | float | RD | _FFT_ULL2[4] | V | 5. Harmonic U L2..L3
149 | float | RD | _FFT_ULL2[5] | V | 6. Harmonic U L2..L3
151 | float | RD | _FFT_ULL2[6] | V | 7. Harmonic U L2..L3
153 | float | RD | _FFT_ULL2[7] | V | 8. Harmonic U L2..L3
155 | float | RD | _FFT_ULL2[8] | V | 9. Harmonic U L2..L3
157 | float | RD | _FFT_ULL2[9] | V | 10. Harmonic U L2..L3
159 | float | RD | _FFT_ULL2[10] | V | 11. Harmonic U L2..L3
161 | float | RD | _FFT_ULL2[11] | V | 12. Harmonic U L2..L3
163 | float | RD | _FFT_ULL2[12] | V | 13. Harmonic U L2..L3
165 | float | RD | _FFT_ULL2[13] | V | 14. Harmonic U L2..L3
167 | float | RD | _FFT_ULL2[14] | V | 15. Harmonic U L2..L3
169 | float | RD | _FFT_ULL2[15] | V | 16. Harmonic U L2..L3
171 | float | RD | _FFT_ULL2[16] | V | 17. Harmonic U L2..L3
173 | float | RD | _FFT_ULL2[17] | V | 18. Harmonic U L2..L3
175 | float | RD | _FFT_ULL2[18] | V | 19. Harmonic U L2..L3
177 | float | RD | _FFT_ULL2[19] | V | 20. Harmonic U L2..L3
179 | float | RD | _FFT_ULL2[20] | V | 21. Harmonic U L2..L3
181 | float | RD | _FFT_ULL2[21] | V | 22. Harmonic U L2..L3
183 | float | RD | _FFT_ULL2[22] | V | 23. Harmonic U L2..L3
185 | float | RD | _FFT_ULL2[23] | V | 24. Harmonic U L2..L3
187 | float | RD | _FFT_ULL2[24] | V | 25. Harmonic U L2..L3
189 | float | RD | _FFT_ULL2[25] | V | 26. Harmonic U L2..L3
191 | float | RD | _FFT_ULL2[26] | V | 27. Harmonic U L2..L3
193 | float | RD | _FFT_ULL2[27] | V | 28. Harmonic U L2..L3
195 | float | RD | _FFT_ULL2[28] | V | 29. Harmonic U L2..L3
197 | float | RD | _FFT_ULL2[29] | V | 30. Harmonic U L2..L3
199 | float | RD | _FFT_ULL2[30] | V | 31. Harmonic U L2..L3
201 | float | RD | _FFT_ULL2[31] | V | 32. Harmonic U L2..L3
203 | float | RD | _FFT_ULL2[32] | V | 33. Harmonic U L2..L3
205 | float | RD | _FFT_ULL2[33] | V | 34. Harmonic U L2..L3
207 | float | RD | _FFT_ULL2[34] | V | 35. Harmonic U L2..L3
209 | float | RD | _FFT_ULL2[35] | V | 36. Harmonic U L2..L3
211 | float | RD | _FFT_ULL2[36] | V | 37. Harmonic U L2..L3
213 | float | RD | _FFT_ULL2[37] | V | 38. Harmonic U L2..L3
215 | float | RD | _FFT_ULL2[38] | V | 39. Harmonic U L2..L3
217 | float | RD | _FFT_ULL2[39] | V | 40. Harmonic U L2..L3
219 | float | RD | _FFT_ULL2[40] | V | 41. Harmonic U L2..L3
221 | float | RD | _FFT_ULL2[41] | V | 42. Harmonic U L2..L3
223 | float | RD | _FFT_ULL2[42] | V | 43. Harmonic U L2..L3
225 | float | RD | _FFT_ULL2[43] | V | 44. Harmonic U L2..L3
227 | float | RD | _FFT_ULL2[44] | V | 45. Harmonic U L2..L3
229 | float | RD | _FFT_ULL2[45] | V | 46. Harmonic U L2..L3
231 | float | RD | _FFT_ULL2[46] | V | 47. Harmonic U L2..L3
233 | float | RD | _FFT_ULL2[47] | V | 48. Harmonic U L2..L3
235 | float | RD | _FFT_ULL2[48] | V | 49. Harmonic U L2..L3
237 | float | RD | _FFT_ULL2[49] | V | 50. Harmonic U L2..L3
239 | float | RD | _FFT_ULL2[50] | V | 51. Harmonic U L2..L3
241 | float | RD | _FFT_ULL2[51] | V | 52. Harmonic U L2..L3
243 | float | RD | _FFT_ULL2[52] | V | 53. Harmonic U L2..L3
245 | float | RD | _FFT_ULL2[53] | V | 54. Harmonic U L2..L3
247 | float | RD | _FFT_ULL2[54] | V | 55. Harmonic U L2..L3
249 | float | RD | _FFT_ULL2[55] | V | 56. Harmonic U L2..L3
251 | float | RD | _FFT_ULL2[56] | V | 57. Harmonic U L2..L3
253 | float | RD | _FFT_ULL2[57] | V | 58. Harmonic U L2..L3
255 | float | RD | _FFT_ULL2[58] | V | 59. Harmonic U L2..L3
257 | float | RD | _FFT_ULL2[59] | V | 60. Harmonic U L2..L3
259 | float | RD | _FFT_ULL2[60] | V | 61. Harmonic U L2..L3
261 | float | RD | _FFT_ULL2[61] | V | 62. Harmonic U L2..L3
263 | float | RD | _FFT_ULL2[62] | V | 63. Harmonic U L2..L3
265 | float | RD | _FFT_ULL3[0] | V | 1. Harmonic U L3..L1
267 | float | RD | _FFT_ULL3[1] | V | 2. Harmonic U L3..L1
269 | float | RD | _FFT_ULL3[2] | V | 3. Harmonic U L3..L1
271 | float | RD | _FFT_ULL3[3] | V | 4. Harmonic U L3..L1
273 | float | RD | _FFT_ULL3[4] | V | 5. Harmonic U L3..L1
275 | float | RD | _FFT_ULL3[5] | V | 6. Harmonic U L3..L1
277 | float | RD | _FFT_ULL3[6] | V | 7. Harmonic U L3..L1
279 | float | RD | _FFT_ULL3[7] | V | 8. Harmonic U L3..L1
281 | float | RD | _FFT_ULL3[8] | V | 9. Harmonic U L3..L1
283 | float | RD | _FFT_ULL3[9] | V | 10. Harmonic U L3..L1
285 | float | RD | _FFT_ULL3[10] | V | 11. Harmonic U L3..L1
287 | float | RD | _FFT_ULL3[11] | V | 12. Harmonic U L3..L1
289 | float | RD | _FFT_ULL3[12] | V | 13. Harmonic U L3..L1
291 | float | RD | _FFT_ULL3[13] | V | 14. Harmonic U L3..L1
293 | float | RD | _FFT_ULL3[14] | V | 15. Harmonic U L3..L1
295 | float | RD | _FFT_ULL3[15] | V | 16. Harmonic U L3..L1
297 | float | RD | _FFT_ULL3[16] | V | 17. Harmonic U L3..L1
299 | float | RD | _FFT_ULL3[17] | V | 18. Harmonic U L3..L1
301 | float | RD | _FFT_ULL3[18] | V | 19. Harmonic U L3..L1
303 | float | RD | _FFT_ULL3[19] | V | 20. Harmonic U L3..L1
305 | float | RD | _FFT_ULL3[20] | V | 21. Harmonic U L3..L1
307 | float | RD | _FFT_ULL3[21] | V | 22. Harmonic U L3..L1
309 | float | RD | _FFT_ULL3[22] | V | 23. Harmonic U L3..L1
311 | float | RD | _FFT_ULL3[23] | V | 24. Harmonic U L3..L1
313 | float | RD | _FFT_ULL3[24] | V | 25. Harmonic U L3..L1
315 | float | RD | _FFT_ULL3[25] | V | 26. Harmonic U L3..L1
317 | float | RD | _FFT_ULL3[26] | V | 27. Harmonic U L3..L1
319 | float | RD | _FFT_ULL3[27] | V | 28. Harmonic U L3..L1
321 | float | RD | _FFT_ULL3[28] | V | 29. Harmonic U L3..L1
323 | float | RD | _FFT_ULL3[29] | V | 30. Harmonic U L3..L1
325 | float | RD | _FFT_ULL3[30] | V | 31. Harmonic U L3..L1
327 | float | RD | _FFT_ULL3[31] | V | 32. Harmonic U L3..L1
329 | float | RD | _FFT_ULL3[32] | V | 33. Harmonic U L3..L1
331 | float | RD | _FFT_ULL3[33] | V | 34. Harmonic U L3..L1
333 | float | RD | _FFT_ULL3[34] | V | 35. Harmonic U L3..L1
335 | float | RD | _FFT_ULL3[35] | V | 36. Harmonic U L3..L1
337 | float | RD | _FFT_ULL3[36] | V | 37. Harmonic U L3..L1
339 | float | RD | _FFT_ULL3[37] | V | 38. Harmonic U L3..L1
341 | float | RD | _FFT_ULL3[38] | V | 39. Harmonic U L3..L1
343 | float | RD | _FFT_ULL3[39] | V | 40. Harmonic U L3..L1
345 | float | RD | _FFT_ULL3[40] | V | 41. Harmonic U L3..L1
347 | float | RD | _FFT_ULL3[41] | V | 42. Harmonic U L3..L1
349 | float | RD | _FFT_ULL3[42] | V | 43. Harmonic U L3..L1
351 | float | RD | _FFT_ULL3[43] | V | 44. Harmonic U L3..L1
353 | float | RD | _FFT_ULL3[44] | V | 45. Harmonic U L3..L1
355 | float | RD | _FFT_ULL3[45] | V | 46. Harmonic U L3..L1
357 | float | RD | _FFT_ULL3[46] | V | 47. Harmonic U L3..L1
359 | float | RD | _FFT_ULL3[47] | V | 48. Harmonic U L3..L1
361 | float | RD | _FFT_ULL3[48] | V | 49. Harmonic U L3..L1
363 | float | RD | _FFT_ULL3[49] | V | 50. Harmonic U L3..L1
365 | float | RD | _FFT_ULL3[50] | V | 51. Harmonic U L3..L1
367 | float | RD | _FFT_ULL3[51] | V | 52. Harmonic U L3..L1
369 | float | RD | _FFT_ULL3[52] | V | 53. Harmonic U L3..L1
371 | float | RD | _FFT_ULL3[53] | V | 54. Harmonic U L3..L1
373 | float | RD | _FFT_ULL3[54] | V | 55. Harmonic U L3..L1
375 | float | RD | _FFT_ULL3[55] | V | 56. Harmonic U L3..L1
377 | float | RD | _FFT_ULL3[56] | V | 57. Harmonic U L3..L1
379 | float | RD | _FFT_ULL3[57] | V | 58. Harmonic U L3..L1
381 | float | RD | _FFT_ULL3[58] | V | 59. Harmonic U L3..L1
383 | float | RD | _FFT_ULL3[59] | V | 60. Harmonic U L3..L1
385 | float | RD | _FFT_ULL3[60] | V | 61. Harmonic U L3..L1
387 | float | RD | _FFT_ULL3[61] | V | 62. Harmonic U L3..L1
389 | float | RD | _FFT_ULL3[62] | V | 63. Harmonic U L3..L1
391 | float | RD | _FFT_UL1[0] | V | 1. Harmonic U L1
393 | float | RD | _FFT_UL1[1] | V | 2. Harmonic U L1
395 | float | RD | _FFT_UL1[2] | V | 3. Harmonic U L1
397 | float | RD | _FFT_UL1[3] | V | 4. Harmonic U L1
399 | float | RD | _FFT_UL1[4] | V | 5. Harmonic U L1
401 | float | RD | _FFT_UL1[5] | V | 6. Harmonic U L1
403 | float | RD | _FFT_UL1[6] | V | 7. Harmonic U L1
405 | float | RD | _FFT_UL1[7] | V | 8. Harmonic U L1
407 | float | RD | _FFT_UL1[8] | V | 9. Harmonic U L1
409 | float | RD | _FFT_UL1[9] | V | 10. Harmonic U L1
411 | float | RD | _FFT_UL1[10] | V | 11. Harmonic U L1
413 | float | RD | _FFT_UL1[11] | V | 12. Harmonic U L1
415 | float | RD | _FFT_UL1[12] | V | 13. Harmonic U L1
417 | float | RD | _FFT_UL1[13] | V | 14. Harmonic U L1
419 | float | RD | _FFT_UL1[14] | V | 15. Harmonic U L1
421 | float | RD | _FFT_UL1[15] | V | 16. Harmonic U L1
423 | float | RD | _FFT_UL1[16] | V | 17. Harmonic U L1
425 | float | RD | _FFT_UL1[17] | V | 18. Harmonic U L1
427 | float | RD | _FFT_UL1[18] | V | 19. Harmonic U L1
429 | float | RD | _FFT_UL1[19] | V | 20. Harmonic U L1
431 | float | RD | _FFT_UL1[20] | V | 21. Harmonic U L1
433 | float | RD | _FFT_UL1[21] | V | 22. Harmonic U L1
435 | float | RD | _FFT_UL1[22] | V | 23. Harmonic U L1
437 | float | RD | _FFT_UL1[23] | V | 24. Harmonic U L1
439 | float | RD | _FFT_UL1[24] | V | 25. Harmonic U L1
441 | float | RD | _FFT_UL1[25] | V | 26. Harmonic U L1
443 | float | RD | _FFT_UL1[26] | V | 27. Harmonic U L1
445 | float | RD | _FFT_UL1[27] | V | 28. Harmonic U L1
447 | float | RD | _FFT_UL1[28] | V | 29. Harmonic U L1
449 | float | RD | _FFT_UL1[29] | V | 30. Harmonic U L1
451 | float | RD | _FFT_UL1[30] | V | 31. Harmonic U L1
453 | float | RD | _FFT_UL1[31] | V | 32. Harmonic U L1
455 | float | RD | _FFT_UL1[32] | V | 33. Harmonic U L1
457 | float | RD | _FFT_UL1[33] | V | 34. Harmonic U L1
459 | float | RD | _FFT_UL1[34] | V | 35. Harmonic U L1
461 | float | RD | _FFT_UL1[35] | V | 36. Harmonic U L1
463 | float | RD | _FFT_UL1[36] | V | 37. Harmonic U L1
465 | float | RD | _FFT_UL1[37] | V | 38. Harmonic U L1
467 | float | RD | _FFT_UL1[38] | V | 39. Harmonic U L1
469 | float | RD | _FFT_UL1[39] | V | 40. Harmonic U L1
471 | float | RD | _FFT_UL1[40] | V | 41. Harmonic U L1
473 | float | RD | _FFT_UL1[41] | V | 42. Harmonic U L1
475 | float | RD | _FFT_UL1[42] | V | 43. Harmonic U L1
477 | float | RD | _FFT_UL1[43] | V | 44. Harmonic U L1
479 | float | RD | _FFT_UL1[44] | V | 45. Harmonic U L1
481 | float | RD | _FFT_UL1[45] | V | 46. Harmonic U L1
483 | float | RD | _FFT_UL1[46] | V | 47. Harmonic U L1
485 | float | RD | _FFT_UL1[47] | V | 48. Harmonic U L1
487 | float | RD | _FFT_UL1[48] | V | 49. Harmonic U L1
489 | float | RD | _FFT_UL1[49] | V | 50. Harmonic U L1
491 | float | RD | _FFT_UL1[50] | V | 51. Harmonic U L1
493 | float | RD | _FFT_UL1[51] | V | 52. Harmonic U L1
495 | float | RD | _FFT_UL1[52] | V | 53. Harmonic U L1
497 | float | RD | _FFT_UL1[53] | V | 54. Harmonic U L1
499 | float | RD | _FFT_UL1[54] | V | 55. Harmonic U L1
501 | float | RD | _FFT_UL1[55] | V | 56. Harmonic U L1
503 | float | RD | _FFT_UL1[56] | V | 57. Harmonic U L1
505 | float | RD | _FFT_UL1[57] | V | 58. Harmonic U L1
507 | float | RD | _FFT_UL1[58] | V | 59. Harmonic U L1
509 | float | RD | _FFT_UL1[59] | V | 60. Harmonic U L1
511 | float | RD | _FFT_UL1[60] | V | 61. Harmonic U L1
513 | float | RD | _FFT_UL1[61] | V | 62. Harmonic U L1
515 | float | RD | _FFT_UL1[62] | V | 63. Harmonic U L1
517 | float | RD | _FFT_UL2[0] | V | 1. Harmonic U L2
519 | float | RD | _FFT_UL2[1] | V | 2. Harmonic U L2
521 | float | RD | _FFT_UL2[2] | V | 3. Harmonic U L2
523 | float | RD | _FFT_UL2[3] | V | 4. Harmonic U L2
525 | float | RD | _FFT_UL2[4] | V | 5. Harmonic U L2
527 | float | RD | _FFT_UL2[5] | V | 6. Harmonic U L2
529 | float | RD | _FFT_UL2[6] | V | 7. Harmonic U L2
531 | float | RD | _FFT_UL2[7] | V | 8. Harmonic U L2
533 | float | RD | _FFT_UL2[8] | V | 9. Harmonic U L2
535 | float | RD | _FFT_UL2[9] | V | 10. Harmonic U L2
537 | float | RD | _FFT_UL2[10] | V | 11. Harmonic U L2
539 | float | RD | _FFT_UL2[11] | V | 12. Harmonic U L2
541 | float | RD | _FFT_UL2[12] | V | 13. Harmonic U L2
543 | float | RD | _FFT_UL2[13] | V | 14. Harmonic U L2
545 | float | RD | _FFT_UL2[14] | V | 15. Harmonic U L2
547 | float | RD | _FFT_UL2[15] | V | 16. Harmonic U L2
549 | float | RD | _FFT_UL2[16] | V | 17. Harmonic U L2
551 | float | RD | _FFT_UL2[17] | V | 18. Harmonic U L2
553 | float | RD | _FFT_UL2[18] | V | 19. Harmonic U L2
555 | float | RD | _FFT_UL2[19] | V | 20. Harmonic U L2
557 | float | RD | _FFT_UL2[20] | V | 21. Harmonic U L2
559 | float | RD | _FFT_UL2[21] | V | 22. Harmonic U L2
561 | float | RD | _FFT_UL2[22] | V | 23. Harmonic U L2
563 | float | RD | _FFT_UL2[23] | V | 24. Harmonic U L2
565 | float | RD | _FFT_UL2[24] | V | 25. Harmonic U L2
567 | float | RD | _FFT_UL2[25] | V | 26. Harmonic U L2
569 | float | RD | _FFT_UL2[26] | V | 27. Harmonic U L2
571 | float | RD | _FFT_UL2[27] | V | 28. Harmonic U L2
573 | float | RD | _FFT_UL2[28] | V | 29. Harmonic U L2
575 | float | RD | _FFT_UL2[29] | V | 30. Harmonic U L2
577 | float | RD | _FFT_UL2[30] | V | 31. Harmonic U L2
579 | float | RD | _FFT_UL2[31] | V | 32. Harmonic U L2
581 | float | RD | _FFT_UL2[32] | V | 33. Harmonic U L2
583 | float | RD | _FFT_UL2[33] | V | 34. Harmonic U L2
585 | float | RD | _FFT_UL2[34] | V | 35. Harmonic U L2
587 | float | RD | _FFT_UL2[35] | V | 36. Harmonic U L2
589 | float | RD | _FFT_UL2[36] | V | 37. Harmonic U L2
591 | float | RD | _FFT_UL2[37] | V | 38. Harmonic U L2
593 | float | RD | _FFT_UL2[38] | V | 39. Harmonic U L2
595 | float | RD | _FFT_UL2[39] | V | 40. Harmonic U L2
597 | float | RD | _FFT_UL2[40] | V | 41. Harmonic U L2
599 | float | RD | _FFT_UL2[41] | V | 42. Harmonic U L2
601 | float | RD | _FFT_UL2[42] | V | 43. Harmonic U L2
603 | float | RD | _FFT_UL2[43] | V | 44. Harmonic U L2
605 | float | RD | _FFT_UL2[44] | V | 45. Harmonic U L2
607 | float | RD | _FFT_UL2[45] | V | 46. Harmonic U L2
609 | float | RD | _FFT_UL2[46] | V | 47. Harmonic U L2
611 | float | RD | _FFT_UL2[47] | V | 48. Harmonic U L2
613 | float | RD | _FFT_UL2[48] | V | 49. Harmonic U L2
615 | float | RD | _FFT_UL2[49] | V | 50. Harmonic U L2
617 | float | RD | _FFT_UL2[50] | V | 51. Harmonic U L2
619 | float | RD | _FFT_UL2[51] | V | 52. Harmonic U L2
621 | float | RD | _FFT_UL2[52] | V | 53. Harmonic U L2
623 | float | RD | _FFT_UL2[53] | V | 54. Harmonic U L2
625 | float | RD | _FFT_UL2[54] | V | 55. Harmonic U L2
627 | float | RD | _FFT_UL2[55] | V | 56. Harmonic U L2
629 | float | RD | _FFT_UL2[56] | V | 57. Harmonic U L2
631 | float | RD | _FFT_UL2[57] | V | 58. Harmonic U L2
633 | float | RD | _FFT_UL2[58] | V | 59. Harmonic U L2
635 | float | RD | _FFT_UL2[59] | V | 60. Harmonic U L2
637 | float | RD | _FFT_UL2[60] | V | 61. Harmonic U L2
639 | float | RD | _FFT_UL2[61] | V | 62. Harmonic U L2
641 | float | RD | _FFT_UL2[62] | V | 63. Harmonic U L2
643 | float | RD | _FFT_UL3[0] | V | 1. Harmonic U L3
645 | float | RD | _FFT_UL3[1] | V | 2. Harmonic U L3
647 | float | RD | _FFT_UL3[2] | V | 3. Harmonic U L3
649 | float | RD | _FFT_UL3[3] | V | 4. Harmonic U L3
651 | float | RD | _FFT_UL3[4] | V | 5. Harmonic U L3
653 | float | RD | _FFT_UL3[5] | V | 6. Harmonic U L3
655 | float | RD | _FFT_UL3[6] | V | 7. Harmonic U L3
657 | float | RD | _FFT_UL3[7] | V | 8. Harmonic U L3
659 | float | RD | _FFT_UL3[8] | V | 9. Harmonic U L3
661 | float | RD | _FFT_UL3[9] | V | 10. Harmonic U L3
663 | float | RD | _FFT_UL3[10] | V | 11. Harmonic U L3
665 | float | RD | _FFT_UL3[11] | V | 12. Harmonic U L3
667 | float | RD | _FFT_UL3[12] | V | 13. Harmonic U L3
669 | float | RD | _FFT_UL3[13] | V | 14. Harmonic U L3
671 | float | RD | _FFT_UL3[14] | V | 15. Harmonic U L3
673 | float | RD | _FFT_UL3[15] | V | 16. Harmonic U L3
675 | float | RD | _FFT_UL3[16] | V | 17. Harmonic U L3
677 | float | RD | _FFT_UL3[17] | V | 18. Harmonic U L3
679 | float | RD | _FFT_UL3[18] | V | 19. Harmonic U L3
681 | float | RD | _FFT_UL3[19] | V | 20. Harmonic U L3
683 | float | RD | _FFT_UL3[20] | V | 21. Harmonic U L3
685 | float | RD | _FFT_UL3[21] | V | 22. Harmonic U L3
687 | float | RD | _FFT_UL3[22] | V | 23. Harmonic U L3
689 | float | RD | _FFT_UL3[23] | V | 24. Harmonic U L3
691 | float | RD | _FFT_UL3[24] | V | 25. Harmonic U L3
693 | float | RD | _FFT_UL3[25] | V | 26. Harmonic U L3
695 | float | RD | _FFT_UL3[26] | V | 27. Harmonic U L3
697 | float | RD | _FFT_UL3[27] | V | 28. Harmonic U L3
699 | float | RD | _FFT_UL3[28] | V | 29. Harmonic U L3
701 | float | RD | _FFT_UL3[29] | V | 30. Harmonic U L3
703 | float | RD | _FFT_UL3[30] | V | 31. Harmonic U L3
705 | float | RD | _FFT_UL3[31] | V | 32. Harmonic U L3
707 | float | RD | _FFT_UL3[32] | V | 33. Harmonic U L3
709 | float | RD | _FFT_UL3[33] | V | 34. Harmonic U L3
711 | float | RD | _FFT_UL3[34] | V | 35. Harmonic U L3
713 | float | RD | _FFT_UL3[35] | V | 36. Harmonic U L3
715 | float | RD | _FFT_UL3[36] | V | 37. Harmonic U L3
717 | float | RD | _FFT_UL3[37] | V | 38. Harmonic U L3
719 | float | RD | _FFT_UL3[38] | V | 39. Harmonic U L3
721 | float | RD | _FFT_UL3[39] | V | 40. Harmonic U L3
723 | float | RD | _FFT_UL3[40] | V | 41. Harmonic U L3
725 | float | RD | _FFT_UL3[41] | V | 42. Harmonic U L3
727 | float | RD | _FFT_UL3[42] | V | 43. Harmonic U L3
729 | float | RD | _FFT_UL3[43] | V | 44. Harmonic U L3
731 | float | RD | _FFT_UL3[44] | V | 45. Harmonic U L3
733 | float | RD | _FFT_UL3[45] | V | 46. Harmonic U L3
735 | float | RD | _FFT_UL3[46] | V | 47. Harmonic U L3
737 | float | RD | _FFT_UL3[47] | V | 48. Harmonic U L3
739 | float | RD | _FFT_UL3[48] | V | 49. Harmonic U L3
741 | float | RD | _FFT_UL3[49] | V | 50. Harmonic U L3
743 | float | RD | _FFT_UL3[50] | V | 51. Harmonic U L3
745 | float | RD | _FFT_UL3[51] | V | 52. Harmonic U L3
747 | float | RD | _FFT_UL3[52] | V | 53. Harmonic U L3
749 | float | RD | _FFT_UL3[53] | V | 54. Harmonic U L3
751 | float | RD | _FFT_UL3[54] | V | 55. Harmonic U L3
753 | float | RD | _FFT_UL3[55] | V | 56. Harmonic U L3
755 | float | RD | _FFT_UL3[56] | V | 57. Harmonic U L3
757 | float | RD | _FFT_UL3[57] | V | 58. Harmonic U L3
759 | float | RD | _FFT_UL3[58] | V | 59. Harmonic U L3
761 | float | RD | _FFT_UL3[59] | V | 60. Harmonic U L3
763 | float | RD | _FFT_UL3[60] | V | 61. Harmonic U L3
765 | float | RD | _FFT_UL3[61] | V | 62. Harmonic U L3
767 | float | RD | _FFT_UL3[62] | V | 63. Harmonic U L3
769 | float | RD | _FFT_UL4[0] | V | 1. Harmonic U L4
771 | float | RD | _FFT_UL4[1] | V | 2. Harmonic U L4
773 | float | RD | _FFT_UL4[2] | V | 3. Harmonic U L4
775 | float | RD | _FFT_UL4[3] | V | 4. Harmonic U L4
777 | float | RD | _FFT_UL4[4] | V | 5. Harmonic U L4
779 | float | RD | _FFT_UL4[5] | V | 6. Harmonic U L4
781 | float | RD | _FFT_UL4[6] | V | 7. Harmonic U L4
783 | float | RD | _FFT_UL4[7] | V | 8. Harmonic U L4
785 | float | RD | _FFT_UL4[8] | V | 9. Harmonic U L4
787 | float | RD | _FFT_UL4[9] | V | 10. Harmonic U L4
789 | float | RD | _FFT_UL4[10] | V | 11. Harmonic U L4
791 | float | RD | _FFT_UL4[11] | V | 12. Harmonic U L4
793 | float | RD | _FFT_UL4[12] | V | 13. Harmonic U L4
795 | float | RD | _FFT_UL4[13] | V | 14. Harmonic U L4
797 | float | RD | _FFT_UL4[14] | V | 15. Harmonic U L4
799 | float | RD | _FFT_UL4[15] | V | 16. Harmonic U L4
801 | float | RD | _FFT_UL4[16] | V | 17. Harmonic U L4
803 | float | RD | _FFT_UL4[17] | V | 18. Harmonic U L4
805 | float | RD | _FFT_UL4[18] | V | 19. Harmonic U L4
807 | float | RD | _FFT_UL4[19] | V | 20. Harmonic U L4
809 | float | RD | _FFT_UL4[20] | V | 21. Harmonic U L4
811 | float | RD | _FFT_UL4[21] | V | 22. Harmonic U L4
813 | float | RD | _FFT_UL4[22] | V | 23. Harmonic U L4
815 | float | RD | _FFT_UL4[23] | V | 24. Harmonic U L4
817 | float | RD | _FFT_UL4[24] | V | 25. Harmonic U L4
819 | float | RD | _FFT_UL4[25] | V | 26. Harmonic U L4
821 | float | RD | _FFT_UL4[26] | V | 27. Harmonic U L4
823 | float | RD | _FFT_UL4[27] | V | 28. Harmonic U L4
825 | float | RD | _FFT_UL4[28] | V | 29. Harmonic U L4
827 | float | RD | _FFT_UL4[29] | V | 30. Harmonic U L4
829 | float | RD | _FFT_UL4[30] | V | 31. Harmonic U L4
831 | float | RD | _FFT_UL4[31] | V | 32. Harmonic U L4
833 | float | RD | _FFT_UL4[32] | V | 33. Harmonic U L4
835 | float | RD | _FFT_UL4[33] | V | 34. Harmonic U L4
837 | float | RD | _FFT_UL4[34] | V | 35. Harmonic U L4
839 | float | RD | _FFT_UL4[35] | V | 36. Harmonic U L4
841 | float | RD | _FFT_UL4[36] | V | 37. Harmonic U L4
843 | float | RD | _FFT_UL4[37] | V | 38. Harmonic U L4
845 | float | RD | _FFT_UL4[38] | V | 39. Harmonic U L4
847 | float | RD | _FFT_UL4[39] | V | 40. Harmonic U L4
849 | float | RD | _FFT_UL4[40] | V | 41. Harmonic U L4
851 | float | RD | _FFT_UL4[41] | V | 42. Harmonic U L4
853 | float | RD | _FFT_UL4[42] | V | 43. Harmonic U L4
855 | float | RD | _FFT_UL4[43] | V | 44. Harmonic U L4
857 | float | RD | _FFT_UL4[44] | V | 45. Harmonic U L4
859 | float | RD | _FFT_UL4[45] | V | 46. Harmonic U L4
861 | float | RD | _FFT_UL4[46] | V | 47. Harmonic U L4
863 | float | RD | _FFT_UL4[47] | V | 48. Harmonic U L4
865 | float | RD | _FFT_UL4[48] | V | 49. Harmonic U L4
867 | float | RD | _FFT_UL4[49] | V | 50. Harmonic U L4
869 | float | RD | _FFT_UL4[50] | V | 51. Harmonic U L4
871 | float | RD | _FFT_UL4[51] | V | 52. Harmonic U L4
873 | float | RD | _FFT_UL4[52] | V | 53. Harmonic U L4
875 | float | RD | _FFT_UL4[53] | V | 54. Harmonic U L4
877 | float | RD | _FFT_UL4[54] | V | 55. Harmonic U L4
879 | float | RD | _FFT_UL4[55] | V | 56. Harmonic U L4
881 | float | RD | _FFT_UL4[56] | V | 57. Harmonic U L4
883 | float | RD | _FFT_UL4[57] | V | 58. Harmonic U L4
885 | float | RD | _FFT_UL4[58] | V | 59. Harmonic U L4
887 | float | RD | _FFT_UL4[59] | V | 60. Harmonic U L4
889 | float | RD | _FFT_UL4[60] | V | 61. Harmonic U L4
891 | float | RD | _FFT_UL4[61] | V | 62. Harmonic U L4
893 | float | RD | _FFT_UL4[62] | V | 63. Harmonic U L4
895 | float | RD | _FFT_IL1[0] | A | Harmonic I L1
897 | float | RD | _FFT_IL1[1] | A | Harmonic I L1
899 | float | RD | _FFT_IL1[2] | A | Harmonic I L1
901 | float | RD | _FFT_IL1[3] | A | Harmonic I L1
903 | float | RD | _FFT_IL1[4] | A | Harmonic I L1
905 | float | RD | _FFT_IL1[5] | A | Harmonic I L1
907 | float | RD | _FFT_IL1[6] | A | Harmonic I L1
909 | float | RD | _FFT_IL1[7] | A | Harmonic I L1
911 | float | RD | _FFT_IL1[8] | A | Harmonic I L1
913 | float | RD | _FFT_IL1[9] | A | Harmonic I L1
915 | float | RD | _FFT_IL1[10] | A | Harmonic I L1
917 | float | RD | _FFT_IL1[11] | A | Harmonic I L1
919 | float | RD | _FFT_IL1[12] | A | Harmonic I L1
921 | float | RD | _FFT_IL1[13] | A | Harmonic I L1
923 | float | RD | _FFT_IL1[14] | A | Harmonic I L1
925 | float | RD | _FFT_IL1[15] | A | Harmonic I L1
927 | float | RD | _FFT_IL1[16] | A | Harmonic I L1
929 | float | RD | _FFT_IL1[17] | A | Harmonic I L1
931 | float | RD | _FFT_IL1[18] | A | Harmonic I L1
933 | float | RD | _FFT_IL1[19] | A | Harmonic I L1
935 | float | RD | _FFT_IL1[20] | A | Harmonic I L1
937 | float | RD | _FFT_IL1[21] | A | Harmonic I L1
939 | float | RD | _FFT_IL1[22] | A | Harmonic I L1
941 | float | RD | _FFT_IL1[23] | A | Harmonic I L1
943 | float | RD | _FFT_IL1[24] | A | Harmonic I L1
945 | float | RD | _FFT_IL1[25] | A | Harmonic I L1
947 | float | RD | _FFT_IL1[26] | A | Harmonic I L1
949 | float | RD | _FFT_IL1[27] | A | Harmonic I L1
951 | float | RD | _FFT_IL1[28] | A | Harmonic I L1
953 | float | RD | _FFT_IL1[29] | A | Harmonic I L1
955 | float | RD | _FFT_IL1[30] | A | Harmonic I L1
957 | float | RD | _FFT_IL1[31] | A | Harmonic I L1
959 | float | RD | _FFT_IL1[32] | A | Harmonic I L1
961 | float | RD | _FFT_IL1[33] | A | Harmonic I L1
963 | float | RD | _FFT_IL1[34] | A | Harmonic I L1
965 | float | RD | _FFT_IL1[35] | A | Harmonic I L1
967 | float | RD | _FFT_IL1[36] | A | Harmonic I L1
969 | float | RD | _FFT_IL1[37] | A | Harmonic I L1
971 | float | RD | _FFT_IL1[38] | A | Harmonic I L1
973 | float | RD | _FFT_IL1[39] | A | Harmonic I L1
975 | float | RD | _FFT_IL1[40] | A | Harmonic I L1
977 | float | RD | _FFT_IL1[41] | A | Harmonic I L1
979 | float | RD | _FFT_IL1[42] | A | Harmonic I L1
981 | float | RD | _FFT_IL1[43] | A | Harmonic I L1
983 | float | RD | _FFT_IL1[44] | A | Harmonic I L1
985 | float | RD | _FFT_IL1[45] | A | Harmonic I L1
987 | float | RD | _FFT_IL1[46] | A | Harmonic I L1
989 | float | RD | _FFT_IL1[47] | A | Harmonic I L1
991 | float | RD | _FFT_IL1[48] | A | Harmonic I L1
993 | float | RD | _FFT_IL1[49] | A | Harmonic I L1
995 | float | RD | _FFT_IL1[50] | A | Harmonic I L1
997 | float | RD | _FFT_IL1[51] | A | Harmonic I L1
999 | float | RD | _FFT_IL1[52] | A | Harmonic I L1
1001 | float | RD | _FFT_IL1[53] | A | Harmonic I L1
1003 | float | RD | _FFT_IL1[54] | A | Harmonic I L1
1005 | float | RD | _FFT_IL1[55] | A | Harmonic I L1
1007 | float | RD | _FFT_IL1[56] | A | Harmonic I L1
1009 | float | RD | _FFT_IL1[57] | A | Harmonic I L1
1011 | float | RD | _FFT_IL1[58] | A | Harmonic I L1
1013 | float | RD | _FFT_IL1[59] | A | Harmonic I L1
1015 | float | RD | _FFT_IL1[60] | A | Harmonic I L1
1017 | float | RD | _FFT_IL1[61] | A | Harmonic I L1
1019 | float | RD | _FFT_IL1[62] | A | Harmonic I L1
1021 | float | RD | _FFT_IL2[0] | A | Harmonic I L2
1023 | float | RD | _FFT_IL2[1] | A | Harmonic I L2
1025 | float | RD | _FFT_IL2[2] | A | Harmonic I L2
1027 | float | RD | _FFT_IL2[3] | A | Harmonic I L2
1029 | float | RD | _FFT_IL2[4] | A | Harmonic I L2
1031 | float | RD | _FFT_IL2[5] | A | Harmonic I L2
1033 | float | RD | _FFT_IL2[6] | A | Harmonic I L2
1035 | float | RD | _FFT_IL2[7] | A | Harmonic I L2
1037 | float | RD | _FFT_IL2[8] | A | Harmonic I L2
1039 | float | RD | _FFT_IL2[9] | A | Harmonic I L2
1041 | float | RD | _FFT_IL2[10] | A | Harmonic I L2
1043 | float | RD | _FFT_IL2[11] | A | Harmonic I L2
1045 | float | RD | _FFT_IL2[12] | A | Harmonic I L2
1047 | float | RD | _FFT_IL2[13] | A | Harmonic I L2
1049 | float | RD | _FFT_IL2[14] | A | Harmonic I L2
1051 | float | RD | _FFT_IL2[15] | A | Harmonic I L2
1053 | float | RD | _FFT_IL2[16] | A | Harmonic I L2
1055 | float | RD | _FFT_IL2[17] | A | Harmonic I L2
1057 | float | RD | _FFT_IL2[18] | A | Harmonic I L2
1059 | float | RD | _FFT_IL2[19] | A | Harmonic I L2
1061 | float | RD | _FFT_IL2[20] | A | Harmonic I L2
1063 | float | RD | _FFT_IL2[21] | A | Harmonic I L2
1065 | float | RD | _FFT_IL2[22] | A | Harmonic I L2
1067 | float | RD | _FFT_IL2[23] | A | Harmonic I L2
1069 | float | RD | _FFT_IL2[24] | A | Harmonic I L2
1071 | float | RD | _FFT_IL2[25] | A | Harmonic I L2
1073 | float | RD | _FFT_IL2[26] | A | Harmonic I L2
1075 | float | RD | _FFT_IL2[27] | A | Harmonic I L2
1077 | float | RD | _FFT_IL2[28] | A | Harmonic I L2
1079 | float | RD | _FFT_IL2[29] | A | Harmonic I L2
1081 | float | RD | _FFT_IL2[30] | A | Harmonic I L2
1083 | float | RD | _FFT_IL2[31] | A | Harmonic I L2
1085 | float | RD | _FFT_IL2[32] | A | Harmonic I L2
1087 | float | RD | _FFT_IL2[33] | A | Harmonic I L2
1089 | float | RD | _FFT_IL2[34] | A | Harmonic I L2
1091 | float | RD | _FFT_IL2[35] | A | Harmonic I L2
1093 | float | RD | _FFT_IL2[36] | A | Harmonic I L2
1095 | float | RD | _FFT_IL2[37] | A | Harmonic I L2
1097 | float | RD | _FFT_IL2[38] | A | Harmonic I L2
1099 | float | RD | _FFT_IL2[39] | A | Harmonic I L2
1101 | float | RD | _FFT_IL2[40] | A | Harmonic I L2
1103 | float | RD | _FFT_IL2[41] | A | Harmonic I L2
1105 | float | RD | _FFT_IL2[42] | A | Harmonic I L2
1107 | float | RD | _FFT_IL2[43] | A | Harmonic I L2
1109 | float | RD | _FFT_IL2[44] | A | Harmonic I L2
1111 | float | RD | _FFT_IL2[45] | A | Harmonic I L2
1113 | float | RD | _FFT_IL2[46] | A | Harmonic I L2
1115 | float | RD | _FFT_IL2[47] | A | Harmonic I L2
1117 | float | RD | _FFT_IL2[48] | A | Harmonic I L2
1119 | float | RD | _FFT_IL2[49] | A | Harmonic I L2
1121 | float | RD | _FFT_IL2[50] | A | Harmonic I L2
1123 | float | RD | _FFT_IL2[51] | A | Harmonic I L2
1125 | float | RD | _FFT_IL2[52] | A | Harmonic I L2
1127 | float | RD | _FFT_IL2[53] | A | Harmonic I L2
1129 | float | RD | _FFT_IL2[54] | A | Harmonic I L2
1131 | float | RD | _FFT_IL2[55] | A | Harmonic I L2
1133 | float | RD | _FFT_IL2[56] | A | Harmonic I L2
1135 | float | RD | _FFT_IL2[57] | A | Harmonic I L2
1137 | float | RD | _FFT_IL2[58] | A | Harmonic I L2
1139 | float | RD | _FFT_IL2[59] | A | Harmonic I L2
1141 | float | RD | _FFT_IL2[60] | A | Harmonic I L2
1143 | float | RD | _FFT_IL2[61] | A | Harmonic I L2
1145 | float | RD | _FFT_IL2[62] | A | Harmonic I L2
1147 | float | RD | _FFT_IL3[0] | A | Harmonic I L3
1149 | float | RD | _FFT_IL3[1] | A | Harmonic I L3
1151 | float | RD | _FFT_IL3[2] | A | Harmonic I L3
1153 | float | RD | _FFT_IL3[3] | A | Harmonic I L3
1155 | float | RD | _FFT_IL3[4] | A | Harmonic I L3
1157 | float | RD | _FFT_IL3[5] | A | Harmonic I L3
1159 | float | RD | _FFT_IL3[6] | A | Harmonic I L3
1161 | float | RD | _FFT_IL3[7] | A | Harmonic I L3
1163 | float | RD | _FFT_IL3[8] | A | Harmonic I L3
1165 | float | RD | _FFT_IL3[9] | A | Harmonic I L3
1167 | float | RD | _FFT_IL3[10] | A | Harmonic I L3
1169 | float | RD | _FFT_IL3[11] | A | Harmonic I L3
1171 | float | RD | _FFT_IL3[12] | A | Harmonic I L3
1173 | float | RD | _FFT_IL3[13] | A | Harmonic I L3
1175 | float | RD | _FFT_IL3[14] | A | Harmonic I L3
1177 | float | RD | _FFT_IL3[15] | A | Harmonic I L3
1179 | float | RD | _FFT_IL3[16] | A | Harmonic I L3
1181 | float | RD | _FFT_IL3[17] | A | Harmonic I L3
1183 | float | RD | _FFT_IL3[18] | A | Harmonic I L3
1185 | float | RD | _FFT_IL3[19] | A | Harmonic I L3
1187 | float | RD | _FFT_IL3[20] | A | Harmonic I L3
1189 | float | RD | _FFT_IL3[21] | A | Harmonic I L3
1191 | float | RD | _FFT_IL3[22] | A | Harmonic I L3
1193 | float | RD | _FFT_IL3[23] | A | Harmonic I L3
1195 | float | RD | _FFT_IL3[24] | A | Harmonic I L3
1197 | float | RD | _FFT_IL3[25] | A | Harmonic I L3
1199 | float | RD | _FFT_IL3[26] | A | Harmonic I L3
1201 | float | RD | _FFT_IL3[27] | A | Harmonic I L3
1203 | float | RD | _FFT_IL3[28] | A | Harmonic I L3
1205 | float | RD | _FFT_IL3[29] | A | Harmonic I L3
1207 | float | RD | _FFT_IL3[30] | A | Harmonic I L3
1209 | float | RD | _FFT_IL3[31] | A | Harmonic I L3
1211 | float | RD | _FFT_IL3[32] | A | Harmonic I L3
1213 | float | RD | _FFT_IL3[33] | A | Harmonic I L3
1215 | float | RD | _FFT_IL3[34] | A | Harmonic I L3
1217 | float | RD | _FFT_IL3[35] | A | Harmonic I L3
1219 | float | RD | _FFT_IL3[36] | A | Harmonic I L3
1221 | float | RD | _FFT_IL3[37] | A | Harmonic I L3
1223 | float | RD | _FFT_IL3[38] | A | Harmonic I L3
1225 | float | RD | _FFT_IL3[39] | A | Harmonic I L3
1227 | float | RD | _FFT_IL3[40] | A | Harmonic I L3
1229 | float | RD | _FFT_IL3[41] | A | Harmonic I L3
1231 | float | RD | _FFT_IL3[42] | A | Harmonic I L3
1233 | float | RD | _FFT_IL3[43] | A | Harmonic I L3
1235 | float | RD | _FFT_IL3[44] | A | Harmonic I L3
1237 | float | RD | _FFT_IL3[45] | A | Harmonic I L3
1239 | float | RD | _FFT_IL3[46] | A | Harmonic I L3
1241 | float | RD | _FFT_IL3[47] | A | Harmonic I L3
1243 | float | RD | _FFT_IL3[48] | A | Harmonic I L3
1245 | float | RD | _FFT_IL3[49] | A | Harmonic I L3
1247 | float | RD | _FFT_IL3[50] | A | Harmonic I L3
1249 | float | RD | _FFT_IL3[51] | A | Harmonic I L3
1251 | float | RD | _FFT_IL3[52] | A | Harmonic I L3
1253 | float | RD | _FFT_IL3[53] | A | Harmonic I L3
1255 | float | RD | _FFT_IL3[54] | A | Harmonic I L3
1257 | float | RD | _FFT_IL3[55] | A | Harmonic I L3
1259 | float | RD | _FFT_IL3[56] | A | Harmonic I L3
1261 | float | RD | _FFT_IL3[57] | A | Harmonic I L3
1263 | float | RD | _FFT_IL3[58] | A | Harmonic I L3
1265 | float | RD | _FFT_IL3[59] | A | Harmonic I L3
1267 | float | RD | _FFT_IL3[60] | A | Harmonic I L3
1269 | float | RD | _FFT_IL3[61] | A | Harmonic I L3
1271 | float | RD | _FFT_IL3[62] | A | Harmonic I L3
1273 | float | RD | _FFT_IL4[0] | A | Harmonic I L4
1275 | float | RD | _FFT_IL4[1] | A | Harmonic I L4
1277 | float | RD | _FFT_IL4[2] | A | Harmonic I L4
1279 | float | RD | _FFT_IL4[3] | A | Harmonic I L4
1281 | float | RD | _FFT_IL4[4] | A | Harmonic I L4
1283 | float | RD | _FFT_IL4[5] | A | Harmonic I L4
1285 | float | RD | _FFT_IL4[6] | A | Harmonic I L4
1287 | float | RD | _FFT_IL4[7] | A | Harmonic I L4
1289 | float | RD | _FFT_IL4[8] | A | Harmonic I L4
1291 | float | RD | _FFT_IL4[9] | A | Harmonic I L4
1293 | float | RD | _FFT_IL4[10] | A | Harmonic I L4
1295 | float | RD | _FFT_IL4[11] | A | Harmonic I L4
1297 | float | RD | _FFT_IL4[12] | A | Harmonic I L4
1299 | float | RD | _FFT_IL4[13] | A | Harmonic I L4
1301 | float | RD | _FFT_IL4[14] | A | Harmonic I L4
1303 | float | RD | _FFT_IL4[15] | A | Harmonic I L4
1305 | float | RD | _FFT_IL4[16] | A | Harmonic I L4
1307 | float | RD | _FFT_IL4[17] | A | Harmonic I L4
1309 | float | RD | _FFT_IL4[18] | A | Harmonic I L4
1311 | float | RD | _FFT_IL4[19] | A | Harmonic I L4
1313 | float | RD | _FFT_IL4[20] | A | Harmonic I L4
1315 | float | RD | _FFT_IL4[21] | A | Harmonic I L4
1317 | float | RD | _FFT_IL4[22] | A | Harmonic I L4
1319 | float | RD | _FFT_IL4[23] | A | Harmonic I L4
1321 | float | RD | _FFT_IL4[24] | A | Harmonic I L4
1323 | float | RD | _FFT_IL4[25] | A | Harmonic I L4
1325 | float | RD | _FFT_IL4[26] | A | Harmonic I L4
1327 | float | RD | _FFT_IL4[27] | A | Harmonic I L4
1329 | float | RD | _FFT_IL4[28] | A | Harmonic I L4
1331 | float | RD | _FFT_IL4[29] | A | Harmonic I L4
1333 | float | RD | _FFT_IL4[30] | A | Harmonic I L4
1335 | float | RD | _FFT_IL4[31] | A | Harmonic I L4
1337 | float | RD | _FFT_IL4[32] | A | Harmonic I L4
1339 | float | RD | _FFT_IL4[33] | A | Harmonic I L4
1341 | float | RD | _FFT_IL4[34] | A | Harmonic I L4
1343 | float | RD | _FFT_IL4[35] | A | Harmonic I L4
1345 | float | RD | _FFT_IL4[36] | A | Harmonic I L4
1347 | float | RD | _FFT_IL4[37] | A | Harmonic I L4
1349 | float | RD | _FFT_IL4[38] | A | Harmonic I L4
1351 | float | RD | _FFT_IL4[39] | A | Harmonic I L4
1353 | float | RD | _FFT_IL4[40] | A | Harmonic I L4
1355 | float | RD | _FFT_IL4[41] | A | Harmonic I L4
1357 | float | RD | _FFT_IL4[42] | A | Harmonic I L4
1359 | float | RD | _FFT_IL4[43] | A | Harmonic I L4
1361 | float | RD | _FFT_IL4[44] | A | Harmonic I L4
1363 | float | RD | _FFT_IL4[45] | A | Harmonic I L4
1365 | float | RD | _FFT_IL4[46] | A | Harmonic I L4
1367 | float | RD | _FFT_IL4[47] | A | Harmonic I L4
1369 | float | RD | _FFT_IL4[48] | A | Harmonic I L4
1371 | float | RD | _FFT_IL4[49] | A | Harmonic I L4
1373 | float | RD | _FFT_IL4[50] | A | Harmonic I L4
1375 | float | RD | _FFT_IL4[51] | A | Harmonic I L4
1377 | float | RD | _FFT_IL4[52] | A | Harmonic I L4
1379 | float | RD | _FFT_IL4[53] | A | Harmonic I L4
1381 | float | RD | _FFT_IL4[54] | A | Harmonic I L4
1383 | float | RD | _FFT_IL4[55] | A | Harmonic I L4
1385 | float | RD | _FFT_IL4[56] | A | Harmonic I L4
1387 | float | RD | _FFT_IL4[57] | A | Harmonic I L4
1389 | float | RD | _FFT_IL4[58] | A | Harmonic I L4
1391 | float | RD | _FFT_IL4[59] | A | Harmonic I L4
1393 | float | RD | _FFT_IL4[60] | A | Harmonic I L4
1395 | float | RD | _FFT_IL4[61] | A | Harmonic I L4
1397 | float | RD | _FFT_IL4[62] | A | Harmonic I L4
1399 | float | RD | _FFT_PL1[0] | W | Harmonic P L1
1401 | float | RD | _FFT_PL1[1] | W | Harmonic P L1
1403 | float | RD | _FFT_PL1[2] | W | Harmonic P L1
1405 | float | RD | _FFT_PL1[3] | W | Harmonic P L1
1407 | float | RD | _FFT_PL1[4] | W | Harmonic P L1
1409 | float | RD | _FFT_PL1[5] | W | Harmonic P L1
1411 | float | RD | _FFT_PL1[6] | W | Harmonic P L1
1413 | float | RD | _FFT_PL1[7] | W | Harmonic P L1
1415 | float | RD | _FFT_PL1[8] | W | Harmonic P L1
1417 | float | RD | _FFT_PL1[9] | W | Harmonic P L1
1419 | float | RD | _FFT_PL1[10] | W | Harmonic P L1
1421 | float | RD | _FFT_PL1[11] | W | Harmonic P L1
1423 | float | RD | _FFT_PL1[12] | W | Harmonic P L1
1425 | float | RD | _FFT_PL1[13] | W | Harmonic P L1
1427 | float | RD | _FFT_PL1[14] | W | Harmonic P L1
1429 | float | RD | _FFT_PL1[15] | W | Harmonic P L1
1431 | float | RD | _FFT_PL1[16] | W | Harmonic P L1
1433 | float | RD | _FFT_PL1[17] | W | Harmonic P L1
1435 | float | RD | _FFT_PL1[18] | W | Harmonic P L1
1437 | float | RD | _FFT_PL1[19] | W | Harmonic P L1
1439 | float | RD | _FFT_PL1[20] | W | Harmonic P L1
1441 | float | RD | _FFT_PL1[21] | W | Harmonic P L1
1443 | float | RD | _FFT_PL1[22] | W | Harmonic P L1
1445 | float | RD | _FFT_PL1[23] | W | Harmonic P L1
1447 | float | RD | _FFT_PL1[24] | W | Harmonic P L1
1449 | float | RD | _FFT_PL1[25] | W | Harmonic P L1
1451 | float | RD | _FFT_PL1[26] | W | Harmonic P L1
1453 | float | RD | _FFT_PL1[27] | W | Harmonic P L1
1455 | float | RD | _FFT_PL1[28] | W | Harmonic P L1
1457 | float | RD | _FFT_PL1[29] | W | Harmonic P L1
1459 | float | RD | _FFT_PL1[30] | W | Harmonic P L1
1461 | float | RD | _FFT_PL1[31] | W | Harmonic P L1
1463 | float | RD | _FFT_PL1[32] | W | Harmonic P L1
1465 | float | RD | _FFT_PL1[33] | W | Harmonic P L1
1467 | float | RD | _FFT_PL1[34] | W | Harmonic P L1
1469 | float | RD | _FFT_PL1[35] | W | Harmonic P L1
1471 | float | RD | _FFT_PL1[36] | W | Harmonic P L1
1473 | float | RD | _FFT_PL1[37] | W | Harmonic P L1
1475 | float | RD | _FFT_PL1[38] | W | Harmonic P L1
1477 | float | RD | _FFT_PL1[39] | W | Harmonic P L1
1479 | float | RD | _FFT_PL1[40] | W | Harmonic P L1
1481 | float | RD | _FFT_PL1[41] | W | Harmonic P L1
1483 | float | RD | _FFT_PL1[42] | W | Harmonic P L1
1485 | float | RD | _FFT_PL1[43] | W | Harmonic P L1
1487 | float | RD | _FFT_PL1[44] | W | Harmonic P L1
1489 | float | RD | _FFT_PL1[45] | W | Harmonic P L1
1491 | float | RD | _FFT_PL1[46] | W | Harmonic P L1
1493 | float | RD | _FFT_PL1[47] | W | Harmonic P L1
1495 | float | RD | _FFT_PL1[48] | W | Harmonic P L1
1497 | float | RD | _FFT_PL1[49] | W | Harmonic P L1
1499 | float | RD | _FFT_PL1[50] | W | Harmonic P L1
1501 | float | RD | _FFT_PL1[51] | W | Harmonic P L1
1503 | float | RD | _FFT_PL1[52] | W | Harmonic P L1
1505 | float | RD | _FFT_PL1[53] | W | Harmonic P L1
1507 | float | RD | _FFT_PL1[54] | W | Harmonic P L1
1509 | float | RD | _FFT_PL1[55] | W | Harmonic P L1
1511 | float | RD | _FFT_PL1[56] | W | Harmonic P L1
1513 | float | RD | _FFT_PL1[57] | W | Harmonic P L1
1515 | float | RD | _FFT_PL1[58] | W | Harmonic P L1
1517 | float | RD | _FFT_PL1[59] | W | Harmonic P L1
1519 | float | RD | _FFT_PL1[60] | W | Harmonic P L1
1521 | float | RD | _FFT_PL1[61] | W | Harmonic P L1
1523 | float | RD | _FFT_PL1[62] | W | Harmonic P L1
1525 | float | RD | _FFT_PL2[0] | W | Harmonic P L2
1527 | float | RD | _FFT_PL2[1] | W | Harmonic P L2
1529 | float | RD | _FFT_PL2[2] | W | Harmonic P L2
1531 | float | RD | _FFT_PL2[3] | W | Harmonic P L2
1533 | float | RD | _FFT_PL2[4] | W | Harmonic P L2
1535 | float | RD | _FFT_PL2[5] | W | Harmonic P L2
1537 | float | RD | _FFT_PL2[6] | W | Harmonic P L2
1539 | float | RD | _FFT_PL2[7] | W | Harmonic P L2
1541 | float | RD | _FFT_PL2[8] | W | Harmonic P L2
1543 | float | RD | _FFT_PL2[9] | W | Harmonic P L2
1545 | float | RD | _FFT_PL2[10] | W | Harmonic P L2
1547 | float | RD | _FFT_PL2[11] | W | Harmonic P L2
1549 | float | RD | _FFT_PL2[12] | W | Harmonic P L2
1551 | float | RD | _FFT_PL2[13] | W | Harmonic P L2
1553 | float | RD | _FFT_PL2[14] | W | Harmonic P L2
1555 | float | RD | _FFT_PL2[15] | W | Harmonic P L2
1557 | float | RD | _FFT_PL2[16] | W | Harmonic P L2
1559 | float | RD | _FFT_PL2[17] | W | Harmonic P L2
1561 | float | RD | _FFT_PL2[18] | W | Harmonic P L2
1563 | float | RD | _FFT_PL2[19] | W | Harmonic P L2
1565 | float | RD | _FFT_PL2[20] | W | Harmonic P L2
1567 | float | RD | _FFT_PL2[21] | W | Harmonic P L2
1569 | float | RD | _FFT_PL2[22] | W | Harmonic P L2
1571 | float | RD | _FFT_PL2[23] | W | Harmonic P L2
1573 | float | RD | _FFT_PL2[24] | W | Harmonic P L2
1575 | float | RD | _FFT_PL2[25] | W | Harmonic P L2
1577 | float | RD | _FFT_PL2[26] | W | Harmonic P L2
1579 | float | RD | _FFT_PL2[27] | W | Harmonic P L2
1581 | float | RD | _FFT_PL2[28] | W | Harmonic P L2
1583 | float | RD | _FFT_PL2[29] | W | Harmonic P L2
1585 | float | RD | _FFT_PL2[30] | W | Harmonic P L2
1587 | float | RD | _FFT_PL2[31] | W | Harmonic P L2
1589 | float | RD | _FFT_PL2[32] | W | Harmonic P L2
1591 | float | RD | _FFT_PL2[33] | W | Harmonic P L2
1593 | float | RD | _FFT_PL2[34] | W | Harmonic P L2
1595 | float | RD | _FFT_PL2[35] | W | Harmonic P L2
1597 | float | RD | _FFT_PL2[36] | W | Harmonic P L2
1599 | float | RD | _FFT_PL2[37] | W | Harmonic P L2
1601 | float | RD | _FFT_PL2[38] | W | Harmonic P L2
1603 | float | RD | _FFT_PL2[39] | W | Harmonic P L2
1605 | float | RD | _FFT_PL2[40] | W | Harmonic P L2
1607 | float | RD | _FFT_PL2[41] | W | Harmonic P L2
1609 | float | RD | _FFT_PL2[42] | W | Harmonic P L2
1611 | float | RD | _FFT_PL2[43] | W | Harmonic P L2
1613 | float | RD | _FFT_PL2[44] | W | Harmonic P L2
1615 | float | RD | _FFT_PL2[45] | W | Harmonic P L2
1617 | float | RD | _FFT_PL2[46] | W | Harmonic P L2
1619 | float | RD | _FFT_PL2[47] | W | Harmonic P L2
1621 | float | RD | _FFT_PL2[48] | W | Harmonic P L2
1623 | float | RD | _FFT_PL2[49] | W | Harmonic P L2
1625 | float | RD | _FFT_PL2[50] | W | Harmonic P L2
1627 | float | RD | _FFT_PL2[51] | W | Harmonic P L2
1629 | float | RD | _FFT_PL2[52] | W | Harmonic P L2
1631 | float | RD | _FFT_PL2[53] | W | Harmonic P L2
1633 | float | RD | _FFT_PL2[54] | W | Harmonic P L2
1635 | float | RD | _FFT_PL2[55] | W | Harmonic P L2
1637 | float | RD | _FFT_PL2[56] | W | Harmonic P L2
1639 | float | RD | _FFT_PL2[57] | W | Harmonic P L2
1641 | float | RD | _FFT_PL2[58] | W | Harmonic P L2
1643 | float | RD | _FFT_PL2[59] | W | Harmonic P L2
1645 | float | RD | _FFT_PL2[60] | W | Harmonic P L2
1647 | float | RD | _FFT_PL2[61] | W | Harmonic P L2
1649 | float | RD | _FFT_PL2[62] | W | Harmonic P L2
1651 | float | RD | _FFT_PL3[0] | W | Harmonic P L3
1653 | float | RD | _FFT_PL3[1] | W | Harmonic P L3
1655 | float | RD | _FFT_PL3[2] | W | Harmonic P L3
1657 | float | RD | _FFT_PL3[3] | W | Harmonic P L3
1659 | float | RD | _FFT_PL3[4] | W | Harmonic P L3
1661 | float | RD | _FFT_PL3[5] | W | Harmonic P L3
1663 | float | RD | _FFT_PL3[6] | W | Harmonic P L3
1665 | float | RD | _FFT_PL3[7] | W | Harmonic P L3
1667 | float | RD | _FFT_PL3[8] | W | Harmonic P L3
1669 | float | RD | _FFT_PL3[9] | W | Harmonic P L3
1671 | float | RD | _FFT_PL3[10] | W | Harmonic P L3
1673 | float | RD | _FFT_PL3[11] | W | Harmonic P L3
1675 | float | RD | _FFT_PL3[12] | W | Harmonic P L3
1677 | float | RD | _FFT_PL3[13] | W | Harmonic P L3
1679 | float | RD | _FFT_PL3[14] | W | Harmonic P L3
1681 | float | RD | _FFT_PL3[15] | W | Harmonic P L3
1683 | float | RD | _FFT_PL3[16] | W | Harmonic P L3
1685 | float | RD | _FFT_PL3[17] | W | Harmonic P L3
1687 | float | RD | _FFT_PL3[18] | W | Harmonic P L3
1689 | float | RD | _FFT_PL3[19] | W | Harmonic P L3
1691 | float | RD | _FFT_PL3[20] | W | Harmonic P L3
1693 | float | RD | _FFT_PL3[21] | W | Harmonic P L3
1695 | float | RD | _FFT_PL3[22] | W | Harmonic P L3
1697 | float | RD | _FFT_PL3[23] | W | Harmonic P L3
1699 | float | RD | _FFT_PL3[24] | W | Harmonic P L3
1701 | float | RD | _FFT_PL3[25] | W | Harmonic P L3
1703 | float | RD | _FFT_PL3[26] | W | Harmonic P L3
1705 | float | RD | _FFT_PL3[27] | W | Harmonic P L3
1707 | float | RD | _FFT_PL3[28] | W | Harmonic P L3
1709 | float | RD | _FFT_PL3[29] | W | Harmonic P L3
1711 | float | RD | _FFT_PL3[30] | W | Harmonic P L3
1713 | float | RD | _FFT_PL3[31] | W | Harmonic P L3
1715 | float | RD | _FFT_PL3[32] | W | Harmonic P L3
1717 | float | RD | _FFT_PL3[33] | W | Harmonic P L3
1719 | float | RD | _FFT_PL3[34] | W | Harmonic P L3
1721 | float | RD | _FFT_PL3[35] | W | Harmonic P L3
1723 | float | RD | _FFT_PL3[36] | W | Harmonic P L3
1725 | float | RD | _FFT_PL3[37] | W | Harmonic P L3
1727 | float | RD | _FFT_PL3[38] | W | Harmonic P L3
1729 | float | RD | _FFT_PL3[39] | W | Harmonic P L3
1731 | float | RD | _FFT_PL3[40] | W | Harmonic P L3
1733 | float | RD | _FFT_PL3[41] | W | Harmonic P L3
1735 | float | RD | _FFT_PL3[42] | W | Harmonic P L3
1737 | float | RD | _FFT_PL3[43] | W | Harmonic P L3
1739 | float | RD | _FFT_PL3[44] | W | Harmonic P L3
1741 | float | RD | _FFT_PL3[45] | W | Harmonic P L3
1743 | float | RD | _FFT_PL3[46] | W | Harmonic P L3
1745 | float | RD | _FFT_PL3[47] | W | Harmonic P L3
1747 | float | RD | _FFT_PL3[48] | W | Harmonic P L3
1749 | float | RD | _FFT_PL3[49] | W | Harmonic P L3
1751 | float | RD | _FFT_PL3[50] | W | Harmonic P L3
1753 | float | RD | _FFT_PL3[51] | W | Harmonic P L3
1755 | float | RD | _FFT_PL3[52] | W | Harmonic P L3
1757 | float | RD | _FFT_PL3[53] | W | Harmonic P L3
1759 | float | RD | _FFT_PL3[54] | W | Harmonic P L3
1761 | float | RD | _FFT_PL3[55] | W | Harmonic P L3
1763 | float | RD | _FFT_PL3[56] | W | Harmonic P L3
1765 | float | RD | _FFT_PL3[57] | W | Harmonic P L3
1767 | float | RD | _FFT_PL3[58] | W | Harmonic P L3
1769 | float | RD | _FFT_PL3[59] | W | Harmonic P L3
1771 | float | RD | _FFT_PL3[60] | W | Harmonic P L3
1773 | float | RD | _FFT_PL3[61] | W | Harmonic P L3
1775 | float | RD | _FFT_PL3[62] | W | Harmonic P L3
1777 | float | RD | _FFT_PL4[0] | W | Harmonic P L4
1779 | float | RD | _FFT_PL4[1] | W | Harmonic P L4
1781 | float | RD | _FFT_PL4[2] | W | Harmonic P L4
1783 | float | RD | _FFT_PL4[3] | W | Harmonic P L4
1785 | float | RD | _FFT_PL4[4] | W | Harmonic P L4
1787 | float | RD | _FFT_PL4[5] | W | Harmonic P L4
1789 | float | RD | _FFT_PL4[6] | W | Harmonic P L4
1791 | float | RD | _FFT_PL4[7] | W | Harmonic P L4
1793 | float | RD | _FFT_PL4[8] | W | Harmonic P L4
1795 | float | RD | _FFT_PL4[9] | W | Harmonic P L4
1797 | float | RD | _FFT_PL4[10] | W | Harmonic P L4
1799 | float | RD | _FFT_PL4[11] | W | Harmonic P L4
1801 | float | RD | _FFT_PL4[12] | W | Harmonic P L4
1803 | float | RD | _FFT_PL4[13] | W | Harmonic P L4
1805 | float | RD | _FFT_PL4[14] | W | Harmonic P L4
1807 | float | RD | _FFT_PL4[15] | W | Harmonic P L4
1809 | float | RD | _FFT_PL4[16] | W | Harmonic P L4
1811 | float | RD | _FFT_PL4[17] | W | Harmonic P L4
1813 | float | RD | _FFT_PL4[18] | W | Harmonic P L4
1815 | float | RD | _FFT_PL4[19] | W | Harmonic P L4
1817 | float | RD | _FFT_PL4[20] | W | Harmonic P L4
1819 | float | RD | _FFT_PL4[21] | W | Harmonic P L4
1821 | float | RD | _FFT_PL4[22] | W | Harmonic P L4
1823 | float | RD | _FFT_PL4[23] | W | Harmonic P L4
1825 | float | RD | _FFT_PL4[24] | W | Harmonic P L4
1827 | float | RD | _FFT_PL4[25] | W | Harmonic P L4
1829 | float | RD | _FFT_PL4[26] | W | Harmonic P L4
1831 | float | RD | _FFT_PL4[27] | W | Harmonic P L4
1833 | float | RD | _FFT_PL4[28] | W | Harmonic P L4
1835 | float | RD | _FFT_PL4[29] | W | Harmonic P L4
1837 | float | RD | _FFT_PL4[30] | W | Harmonic P L4
1839 | float | RD | _FFT_PL4[31] | W | Harmonic P L4
1841 | float | RD | _FFT_PL4[32] | W | Harmonic P L4
1843 | float | RD | _FFT_PL4[33] | W | Harmonic P L4
1845 | float | RD | _FFT_PL4[34] | W | Harmonic P L4
1847 | float | RD | _FFT_PL4[35] | W | Harmonic P L4
1849 | float | RD | _FFT_PL4[36] | W | Harmonic P L4
1851 | float | RD | _FFT_PL4[37] | W | Harmonic P L4
1853 | float | RD | _FFT_PL4[38] | W | Harmonic P L4
1855 | float | RD | _FFT_PL4[39] | W | Harmonic P L4
1857 | float | RD | _FFT_PL4[40] | W | Harmonic P L4
1859 | float | RD | _FFT_PL4[41] | W | Harmonic P L4
1861 | float | RD | _FFT_PL4[42] | W | Harmonic P L4
1863 | float | RD | _FFT_PL4[43] | W | Harmonic P L4
1865 | float | RD | _FFT_PL4[44] | W | Harmonic P L4
1867 | float | RD | _FFT_PL4[45] | W | Harmonic P L4
1869 | float | RD | _FFT_PL4[46] | W | Harmonic P L4
1871 | float | RD | _FFT_PL4[47] | W | Harmonic P L4
1873 | float | RD | _FFT_PL4[48] | W | Harmonic P L4
1875 | float | RD | _FFT_PL4[49] | W | Harmonic P L4
1877 | float | RD | _FFT_PL4[50] | W | Harmonic P L4
1879 | float | RD | _FFT_PL4[51] | W | Harmonic P L4
1881 | float | RD | _FFT_PL4[52] | W | Harmonic P L4
1883 | float | RD | _FFT_PL4[53] | W | Harmonic P L4
1885 | float | RD | _FFT_PL4[54] | W | Harmonic P L4
1887 | float | RD | _FFT_PL4[55] | W | Harmonic P L4
1889 | float | RD | _FFT_PL4[56] | W | Harmonic P L4
1891 | float | RD | _FFT_PL4[57] | W | Harmonic P L4
1893 | float | RD | _FFT_PL4[58] | W | Harmonic P L4
1895 | float | RD | _FFT_PL4[59] | W | Harmonic P L4
1897 | float | RD | _FFT_PL4[60] | W | Harmonic P L4
1899 | float | RD | _FFT_PL4[61] | W | Harmonic P L4
1901 | float | RD | _FFT_PL4[62] | W | Harmonic P L4
1903 | float | RD | _FFT_QL1[0] | var | Harmonic Q L1
1905 | float | RD | _FFT_QL1[1] | var | Harmonic Q L1
1907 | float | RD | _FFT_QL1[2] | var | Harmonic Q L1
1909 | float | RD | _FFT_QL1[3] | var | Harmonic Q L1
1911 | float | RD | _FFT_QL1[4] | var | Harmonic Q L1
1913 | float | RD | _FFT_QL1[5] | var | Harmonic Q L1
1915 | float | RD | _FFT_QL1[6] | var | Harmonic Q L1
1917 | float | RD | _FFT_QL1[7] | var | Harmonic Q L1
1919 | float | RD | _FFT_QL1[8] | var | Harmonic Q L1
1921 | float | RD | _FFT_QL1[9] | var | Harmonic Q L1
1923 | float | RD | _FFT_QL1[10] | var | Harmonic Q L1
1925 | float | RD | _FFT_QL1[11] | var | Harmonic Q L1
1927 | float | RD | _FFT_QL1[12] | var | Harmonic Q L1
1929 | float | RD | _FFT_QL1[13] | var | Harmonic Q L1
1931 | float | RD | _FFT_QL1[14] | var | Harmonic Q L1
1933 | float | RD | _FFT_QL1[15] | var | Harmonic Q L1
1935 | float | RD | _FFT_QL1[16] | var | Harmonic Q L1
1937 | float | RD | _FFT_QL1[17] | var | Harmonic Q L1
1939 | float | RD | _FFT_QL1[18] | var | Harmonic Q L1
1941 | float | RD | _FFT_QL1[19] | var | Harmonic Q L1
1943 | float | RD | _FFT_QL1[20] | var | Harmonic Q L1
1945 | float | RD | _FFT_QL1[21] | var | Harmonic Q L1
1947 | float | RD | _FFT_QL1[22] | var | Harmonic Q L1
1949 | float | RD | _FFT_QL1[23] | var | Harmonic Q L1
1951 | float | RD | _FFT_QL1[24] | var | Harmonic Q L1
1953 | float | RD | _FFT_QL1[25] | var | Harmonic Q L1
1955 | float | RD | _FFT_QL1[26] | var | Harmonic Q L1
1957 | float | RD | _FFT_QL1[27] | var | Harmonic Q L1
1959 | float | RD | _FFT_QL1[28] | var | Harmonic Q L1
1961 | float | RD | _FFT_QL1[29] | var | Harmonic Q L1
1963 | float | RD | _FFT_QL1[30] | var | Harmonic Q L1
1965 | float | RD | _FFT_QL1[31] | var | Harmonic Q L1
1967 | float | RD | _FFT_QL1[32] | var | Harmonic Q L1
1969 | float | RD | _FFT_QL1[33] | var | Harmonic Q L1
1971 | float | RD | _FFT_QL1[34] | var | Harmonic Q L1
1973 | float | RD | _FFT_QL1[35] | var | Harmonic Q L1
1975 | float | RD | _FFT_QL1[36] | var | Harmonic Q L1
1977 | float | RD | _FFT_QL1[37] | var | Harmonic Q L1
1979 | float | RD | _FFT_QL1[38] | var | Harmonic Q L1
1981 | float | RD | _FFT_QL1[39] | var | Harmonic Q L1
1983 | float | RD | _FFT_QL1[40] | var | Harmonic Q L1
1985 | float | RD | _FFT_QL1[41] | var | Harmonic Q L1
1987 | float | RD | _FFT_QL1[42] | var | Harmonic Q L1
1989 | float | RD | _FFT_QL1[43] | var | Harmonic Q L1
1991 | float | RD | _FFT_QL1[44] | var | Harmonic Q L1
1993 | float | RD | _FFT_QL1[45] | var | Harmonic Q L1
1995 | float | RD | _FFT_QL1[46] | var | Harmonic Q L1
1997 | float | RD | _FFT_QL1[47] | var | Harmonic Q L1
1999 | float | RD | _FFT_QL1[48] | var | Harmonic Q L1
2001 | float | RD | _FFT_QL1[49] | var | Harmonic Q L1
2003 | float | RD | _FFT_QL1[50] | var | Harmonic Q L1
2005 | float | RD | _FFT_QL1[51] | var | Harmonic Q L1
2007 | float | RD | _FFT_QL1[52] | var | Harmonic Q L1
2009 | float | RD | _FFT_QL1[53] | var | Harmonic Q L1
2011 | float | RD | _FFT_QL1[54] | var | Harmonic Q L1
2013 | float | RD | _FFT_QL1[55] | var | Harmonic Q L1
2015 | float | RD | _FFT_QL1[56] | var | Harmonic Q L1
2017 | float | RD | _FFT_QL1[57] | var | Harmonic Q L1
2019 | float | RD | _FFT_QL1[58] | var | Harmonic Q L1
2021 | float | RD | _FFT_QL1[59] | var | Harmonic Q L1
2023 | float | RD | _FFT_QL1[60] | var | Harmonic Q L1
2025 | float | RD | _FFT_QL1[61] | var | Harmonic Q L1
2027 | float | RD | _FFT_QL1[62] | var | Harmonic Q L1
2029 | float | RD | _FFT_QL2[0] | var | Harmonic Q L2
2031 | float | RD | _FFT_QL2[1] | var | Harmonic Q L2
2033 | float | RD | _FFT_QL2[2] | var | Harmonic Q L2
2035 | float | RD | _FFT_QL2[3] | var | Harmonic Q L2
2037 | float | RD | _FFT_QL2[4] | var | Harmonic Q L2
2039 | float | RD | _FFT_QL2[5] | var | Harmonic Q L2
2041 | float | RD | _FFT_QL2[6] | var | Harmonic Q L2
2043 | float | RD | _FFT_QL2[7] | var | Harmonic Q L2
2045 | float | RD | _FFT_QL2[8] | var | Harmonic Q L2
2047 | float | RD | _FFT_QL2[9] | var | Harmonic Q L2
2049 | float | RD | _FFT_QL2[10] | var | Harmonic Q L2
2051 | float | RD | _FFT_QL2[11] | var | Harmonic Q L2
2053 | float | RD | _FFT_QL2[12] | var | Harmonic Q L2
2055 | float | RD | _FFT_QL2[13] | var | Harmonic Q L2
2057 | float | RD | _FFT_QL2[14] | var | Harmonic Q L2
2059 | float | RD | _FFT_QL2[15] | var | Harmonic Q L2
2061 | float | RD | _FFT_QL2[16] | var | Harmonic Q L2
2063 | float | RD | _FFT_QL2[17] | var | Harmonic Q L2
2065 | float | RD | _FFT_QL2[18] | var | Harmonic Q L2
2067 | float | RD | _FFT_QL2[19] | var | Harmonic Q L2
2069 | float | RD | _FFT_QL2[20] | var | Harmonic Q L2
2071 | float | RD | _FFT_QL2[21] | var | Harmonic Q L2
2073 | float | RD | _FFT_QL2[22] | var | Harmonic Q L2
2075 | float | RD | _FFT_QL2[23] | var | Harmonic Q L2
2077 | float | RD | _FFT_QL2[24] | var | Harmonic Q L2
2079 | float | RD | _FFT_QL2[25] | var | Harmonic Q L2
2081 | float | RD | _FFT_QL2[26] | var | Harmonic Q L2
2083 | float | RD | _FFT_QL2[27] | var | Harmonic Q L2
2085 | float | RD | _FFT_QL2[28] | var | Harmonic Q L2
2087 | float | RD | _FFT_QL2[29] | var | Harmonic Q L2
2089 | float | RD | _FFT_QL2[30] | var | Harmonic Q L2
2091 | float | RD | _FFT_QL2[31] | var | Harmonic Q L2
2093 | float | RD | _FFT_QL2[32] | var | Harmonic Q L2
2095 | float | RD | _FFT_QL2[33] | var | Harmonic Q L2
2097 | float | RD | _FFT_QL2[34] | var | Harmonic Q L2
2099 | float | RD | _FFT_QL2[35] | var | Harmonic Q L2
2101 | float | RD | _FFT_QL2[36] | var | Harmonic Q L2
2103 | float | RD | _FFT_QL2[37] | var | Harmonic Q L2
2105 | float | RD | _FFT_QL2[38] | var | Harmonic Q L2
2107 | float | RD | _FFT_QL2[39] | var | Harmonic Q L2
2109 | float | RD | _FFT_QL2[40] | var | Harmonic Q L2
2111 | float | RD | _FFT_QL2[41] | var | Harmonic Q L2
2113 | float | RD | _FFT_QL2[42] | var | Harmonic Q L2
2115 | float | RD | _FFT_QL2[43] | var | Harmonic Q L2
2117 | float | RD | _FFT_QL2[44] | var | Harmonic Q L2
2119 | float | RD | _FFT_QL2[45] | var | Harmonic Q L2
2121 | float | RD | _FFT_QL2[46] | var | Harmonic Q L2
2123 | float | RD | _FFT_QL2[47] | var | Harmonic Q L2
2125 | float | RD | _FFT_QL2[48] | var | Harmonic Q L2
2127 | float | RD | _FFT_QL2[49] | var | Harmonic Q L2
2129 | float | RD | _FFT_QL2[50] | var | Harmonic Q L2
2131 | float | RD | _FFT_QL2[51] | var | Harmonic Q L2
2133 | float | RD | _FFT_QL2[52] | var | Harmonic Q L2
2135 | float | RD | _FFT_QL2[53] | var | Harmonic Q L2
2137 | float | RD | _FFT_QL2[54] | var | Harmonic Q L2
2139 | float | RD | _FFT_QL2[55] | var | Harmonic Q L2
2141 | float | RD | _FFT_QL2[56] | var | Harmonic Q L2
2143 | float | RD | _FFT_QL2[57] | var | Harmonic Q L2
2145 | float | RD | _FFT_QL2[58] | var | Harmonic Q L2
2147 | float | RD | _FFT_QL2[59] | var | Harmonic Q L2
2149 | float | RD | _FFT_QL2[60] | var | Harmonic Q L2
2151 | float | RD | _FFT_QL2[61] | var | Harmonic Q L2
2153 | float | RD | _FFT_QL2[62] | var | Harmonic Q L2
2155 | float | RD | _FFT_QL3[0] | var | Harmonic Q L3
2157 | float | RD | _FFT_QL3[1] | var | Harmonic Q L3
2159 | float | RD | _FFT_QL3[2] | var | Harmonic Q L3
2161 | float | RD | _FFT_QL3[3] | var | Harmonic Q L3
2163 | float | RD | _FFT_QL3[4] | var | Harmonic Q L3
2165 | float | RD | _FFT_QL3[5] | var | Harmonic Q L3
2167 | float | RD | _FFT_QL3[6] | var | Harmonic Q L3
2169 | float | RD | _FFT_QL3[7] | var | Harmonic Q L3
2171 | float | RD | _FFT_QL3[8] | var | Harmonic Q L3
2173 | float | RD | _FFT_QL3[9] | var | Harmonic Q L3
2175 | float | RD | _FFT_QL3[10] | var | Harmonic Q L3
2177 | float | RD | _FFT_QL3[11] | var | Harmonic Q L3
2179 | float | RD | _FFT_QL3[12] | var | Harmonic Q L3
2181 | float | RD | _FFT_QL3[13] | var | Harmonic Q L3
2183 | float | RD | _FFT_QL3[14] | var | Harmonic Q L3
2185 | float | RD | _FFT_QL3[15] | var | Harmonic Q L3
2187 | float | RD | _FFT_QL3[16] | var | Harmonic Q L3
2189 | float | RD | _FFT_QL3[17] | var | Harmonic Q L3
2191 | float | RD | _FFT_QL3[18] | var | Harmonic Q L3
2193 | float | RD | _FFT_QL3[19] | var | Harmonic Q L3
2195 | float | RD | _FFT_QL3[20] | var | Harmonic Q L3
2197 | float | RD | _FFT_QL3[21] | var | Harmonic Q L3
2199 | float | RD | _FFT_QL3[22] | var | Harmonic Q L3
2201 | float | RD | _FFT_QL3[23] | var | Harmonic Q L3
2203 | float | RD | _FFT_QL3[24] | var | Harmonic Q L3
2205 | float | RD | _FFT_QL3[25] | var | Harmonic Q L3
2207 | float | RD | _FFT_QL3[26] | var | Harmonic Q L3
2209 | float | RD | _FFT_QL3[27] | var | Harmonic Q L3
2211 | float | RD | _FFT_QL3[28] | var | Harmonic Q L3
2213 | float | RD | _FFT_QL3[29] | var | Harmonic Q L3
2215 | float | RD | _FFT_QL3[30] | var | Harmonic Q L3
2217 | float | RD | _FFT_QL3[31] | var | Harmonic Q L3
2219 | float | RD | _FFT_QL3[32] | var | Harmonic Q L3
2221 | float | RD | _FFT_QL3[33] | var | Harmonic Q L3
2223 | float | RD | _FFT_QL3[34] | var | Harmonic Q L3
2225 | float | RD | _FFT_QL3[35] | var | Harmonic Q L3
2227 | float | RD | _FFT_QL3[36] | var | Harmonic Q L3
2229 | float | RD | _FFT_QL3[37] | var | Harmonic Q L3
2231 | float | RD | _FFT_QL3[38] | var | Harmonic Q L3
2233 | float | RD | _FFT_QL3[39] | var | Harmonic Q L3
2235 | float | RD | _FFT_QL3[40] | var | Harmonic Q L3
2237 | float | RD | _FFT_QL3[41] | var | Harmonic Q L3
2239 | float | RD | _FFT_QL3[42] | var | Harmonic Q L3
2241 | float | RD | _FFT_QL3[43] | var | Harmonic Q L3
2243 | float | RD | _FFT_QL3[44] | var | Harmonic Q L3
2245 | float | RD | _FFT_QL3[45] | var | Harmonic Q L3
2247 | float | RD | _FFT_QL3[46] | var | Harmonic Q L3
2249 | float | RD | _FFT_QL3[47] | var | Harmonic Q L3
2251 | float | RD | _FFT_QL3[48] | var | Harmonic Q L3
2253 | float | RD | _FFT_QL3[49] | var | Harmonic Q L3
2255 | float | RD | _FFT_QL3[50] | var | Harmonic Q L3
2257 | float | RD | _FFT_QL3[51] | var | Harmonic Q L3
2259 | float | RD | _FFT_QL3[52] | var | Harmonic Q L3
2261 | float | RD | _FFT_QL3[53] | var | Harmonic Q L3
2263 | float | RD | _FFT_QL3[54] | var | Harmonic Q L3
2265 | float | RD | _FFT_QL3[55] | var | Harmonic Q L3
2267 | float | RD | _FFT_QL3[56] | var | Harmonic Q L3
2269 | float | RD | _FFT_QL3[57] | var | Harmonic Q L3
2271 | float | RD | _FFT_QL3[58] | var | Harmonic Q L3
2273 | float | RD | _FFT_QL3[59] | var | Harmonic Q L3
2275 | float | RD | _FFT_QL3[60] | var | Harmonic Q L3
2277 | float | RD | _FFT_QL3[61] | var | Harmonic Q L3
2279 | float | RD | _FFT_QL3[62] | var | Harmonic Q L3
2281 | float | RD | _FFT_QL4[0] | var | Harmonic Q L4
2283 | float | RD | _FFT_QL4[1] | var | Harmonic Q L4
2285 | float | RD | _FFT_QL4[2] | var | Harmonic Q L4
2287 | float | RD | _FFT_QL4[3] | var | Harmonic Q L4
2289 | float | RD | _FFT_QL4[4] | var | Harmonic Q L4
2291 | float | RD | _FFT_QL4[5] | var | Harmonic Q L4
2293 | float | RD | _FFT_QL4[6] | var | Harmonic Q L4
2295 | float | RD | _FFT_QL4[7] | var | Harmonic Q L4
2297 | float | RD | _FFT_QL4[8] | var | Harmonic Q L4
2299 | float | RD | _FFT_QL4[9] | var | Harmonic Q L4
2301 | float | RD | _FFT_QL4[10] | var | Harmonic Q L4
2303 | float | RD | _FFT_QL4[11] | var | Harmonic Q L4
2305 | float | RD | _FFT_QL4[12] | var | Harmonic Q L4
2307 | float | RD | _FFT_QL4[13] | var | Harmonic Q L4
2309 | float | RD | _FFT_QL4[14] | var | Harmonic Q L4
2311 | float | RD | _FFT_QL4[15] | var | Harmonic Q L4
2313 | float | RD | _FFT_QL4[16] | var | Harmonic Q L4
2315 | float | RD | _FFT_QL4[17] | var | Harmonic Q L4
2317 | float | RD | _FFT_QL4[18] | var | Harmonic Q L4
2319 | float | RD | _FFT_QL4[19] | var | Harmonic Q L4
2321 | float | RD | _FFT_QL4[20] | var | Harmonic Q L4
2323 | float | RD | _FFT_QL4[21] | var | Harmonic Q L4
2325 | float | RD | _FFT_QL4[22] | var | Harmonic Q L4
2327 | float | RD | _FFT_QL4[23] | var | Harmonic Q L4
2329 | float | RD | _FFT_QL4[24] | var | Harmonic Q L4
2331 | float | RD | _FFT_QL4[25] | var | Harmonic Q L4
2333 | float | RD | _FFT_QL4[26] | var | Harmonic Q L4
2335 | float | RD | _FFT_QL4[27] | var | Harmonic Q L4
2337 | float | RD | _FFT_QL4[28] | var | Harmonic Q L4
2339 | float | RD | _FFT_QL4[29] | var | Harmonic Q L4
2341 | float | RD | _FFT_QL4[30] | var | Harmonic Q L4
2343 | float | RD | _FFT_QL4[31] | var | Harmonic Q L4
2345 | float | RD | _FFT_QL4[32] | var | Harmonic Q L4
2347 | float | RD | _FFT_QL4[33] | var | Harmonic Q L4
2349 | float | RD | _FFT_QL4[34] | var | Harmonic Q L4
2351 | float | RD | _FFT_QL4[35] | var | Harmonic Q L4
2353 | float | RD | _FFT_QL4[36] | var | Harmonic Q L4
2355 | float | RD | _FFT_QL4[37] | var | Harmonic Q L4
2357 | float | RD | _FFT_QL4[38] | var | Harmonic Q L4
2359 | float | RD | _FFT_QL4[39] | var | Harmonic Q L4
2361 | float | RD | _FFT_QL4[40] | var | Harmonic Q L4
2363 | float | RD | _FFT_QL4[41] | var | Harmonic Q L4
2365 | float | RD | _FFT_QL4[42] | var | Harmonic Q L4
2367 | float | RD | _FFT_QL4[43] | var | Harmonic Q L4
2369 | float | RD | _FFT_QL4[44] | var | Harmonic Q L4
2371 | float | RD | _FFT_QL4[45] | var | Harmonic Q L4
2373 | float | RD | _FFT_QL4[46] | var | Harmonic Q L4
2375 | float | RD | _FFT_QL4[47] | var | Harmonic Q L4
2377 | float | RD | _FFT_QL4[48] | var | Harmonic Q L4
2379 | float | RD | _FFT_QL4[49] | var | Harmonic Q L4
2381 | float | RD | _FFT_QL4[50] | var | Harmonic Q L4
2383 | float | RD | _FFT_QL4[51] | var | Harmonic Q L4
2385 | float | RD | _FFT_QL4[52] | var | Harmonic Q L4
2387 | float | RD | _FFT_QL4[53] | var | Harmonic Q L4
2389 | float | RD | _FFT_QL4[54] | var | Harmonic Q L4
2391 | float | RD | _FFT_QL4[55] | var | Harmonic Q L4
2393 | float | RD | _FFT_QL4[56] | var | Harmonic Q L4
2395 | float | RD | _FFT_QL4[57] | var | Harmonic Q L4
2397 | float | RD | _FFT_QL4[58] | var | Harmonic Q L4
2399 | float | RD | _FFT_QL4[59] | var | Harmonic Q L4
2401 | float | RD | _FFT_QL4[60] | var | Harmonic Q L4
2403 | float | RD | _FFT_QL4[61] | var | Harmonic Q L4
2405 | float | RD | _FFT_QL4[62] | var | Harmonic Q L4
2407 | float | RD | _FFT_ULLZ1[0] | V | Interharmonic U L1..L2
2409 | float | RD | _FFT_ULLZ1[1] | V | Interharmonic U L1..L2
2411 | float | RD | _FFT_ULLZ1[2] | V | Interharmonic U L1..L2
2413 | float | RD | _FFT_ULLZ1[3] | V | Interharmonic U L1..L2
2415 | float | RD | _FFT_ULLZ1[4] | V | Interharmonic U L1..L2
2417 | float | RD | _FFT_ULLZ1[5] | V | Interharmonic U L1..L2
2419 | float | RD | _FFT_ULLZ1[6] | V | Interharmonic U L1..L2
2421 | float | RD | _FFT_ULLZ1[7] | V | Interharmonic U L1..L2
2423 | float | RD | _FFT_ULLZ1[8] | V | Interharmonic U L1..L2
2425 | float | RD | _FFT_ULLZ1[9] | V | Interharmonic U L1..L2
2427 | float | RD | _FFT_ULLZ1[10] | V | Interharmonic U L1..L2
2429 | float | RD | _FFT_ULLZ1[11] | V | Interharmonic U L1..L2
2431 | float | RD | _FFT_ULLZ1[12] | V | Interharmonic U L1..L2
2433 | float | RD | _FFT_ULLZ1[13] | V | Interharmonic U L1..L2
2435 | float | RD | _FFT_ULLZ1[14] | V | Interharmonic U L1..L2
2437 | float | RD | _FFT_ULLZ1[15] | V | Interharmonic U L1..L2
2439 | float | RD | _FFT_ULLZ1[16] | V | Interharmonic U L1..L2
2441 | float | RD | _FFT_ULLZ1[17] | V | Interharmonic U L1..L2
2443 | float | RD | _FFT_ULLZ1[18] | V | Interharmonic U L1..L2
2445 | float | RD | _FFT_ULLZ1[19] | V | Interharmonic U L1..L2
2447 | float | RD | _FFT_ULLZ1[20] | V | Interharmonic U L1..L2
2449 | float | RD | _FFT_ULLZ1[21] | V | Interharmonic U L1..L2
2451 | float | RD | _FFT_ULLZ1[22] | V | Interharmonic U L1..L2
2453 | float | RD | _FFT_ULLZ1[23] | V | Interharmonic U L1..L2
2455 | float | RD | _FFT_ULLZ1[24] | V | Interharmonic U L1..L2
2457 | float | RD | _FFT_ULLZ1[25] | V | Interharmonic U L1..L2
2459 | float | RD | _FFT_ULLZ1[26] | V | Interharmonic U L1..L2
2461 | float | RD | _FFT_ULLZ1[27] | V | Interharmonic U L1..L2
2463 | float | RD | _FFT_ULLZ1[28] | V | Interharmonic U L1..L2
2465 | float | RD | _FFT_ULLZ1[29] | V | Interharmonic U L1..L2
2467 | float | RD | _FFT_ULLZ1[30] | V | Interharmonic U L1..L2
2469 | float | RD | _FFT_ULLZ1[31] | V | Interharmonic U L1..L2
2471 | float | RD | _FFT_ULLZ1[32] | V | Interharmonic U L1..L2
2473 | float | RD | _FFT_ULLZ1[33] | V | Interharmonic U L1..L2
2475 | float | RD | _FFT_ULLZ1[34] | V | Interharmonic U L1..L2
2477 | float | RD | _FFT_ULLZ1[35] | V | Interharmonic U L1..L2
2479 | float | RD | _FFT_ULLZ1[36] | V | Interharmonic U L1..L2
2481 | float | RD | _FFT_ULLZ1[37] | V | Interharmonic U L1..L2
2483 | float | RD | _FFT_ULLZ1[38] | V | Interharmonic U L1..L2
2485 | float | RD | _FFT_ULLZ1[39] | V | Interharmonic U L1..L2
2487 | float | RD | _FFT_ULLZ1[40] | V | Interharmonic U L1..L2
2489 | float | RD | _FFT_ULLZ1[41] | V | Interharmonic U L1..L2
2491 | float | RD | _FFT_ULLZ1[42] | V | Interharmonic U L1..L2
2493 | float | RD | _FFT_ULLZ1[43] | V | Interharmonic U L1..L2
2495 | float | RD | _FFT_ULLZ1[44] | V | Interharmonic U L1..L2
2497 | float | RD | _FFT_ULLZ1[45] | V | Interharmonic U L1..L2
2499 | float | RD | _FFT_ULLZ1[46] | V | Interharmonic U L1..L2
2501 | float | RD | _FFT_ULLZ1[47] | V | Interharmonic U L1..L2
2503 | float | RD | _FFT_ULLZ1[48] | V | Interharmonic U L1..L2
2505 | float | RD | _FFT_ULLZ1[49] | V | Interharmonic U L1..L2
2507 | float | RD | _FFT_ULLZ1[50] | V | Interharmonic U L1..L2
2509 | float | RD | _FFT_ULLZ1[51] | V | Interharmonic U L1..L2
2511 | float | RD | _FFT_ULLZ1[52] | V | Interharmonic U L1..L2
2513 | float | RD | _FFT_ULLZ1[53] | V | Interharmonic U L1..L2
2515 | float | RD | _FFT_ULLZ1[54] | V | Interharmonic U L1..L2
2517 | float | RD | _FFT_ULLZ1[55] | V | Interharmonic U L1..L2
2519 | float | RD | _FFT_ULLZ1[56] | V | Interharmonic U L1..L2
2521 | float | RD | _FFT_ULLZ1[57] | V | Interharmonic U L1..L2
2523 | float | RD | _FFT_ULLZ1[58] | V | Interharmonic U L1..L2
2525 | float | RD | _FFT_ULLZ1[59] | V | Interharmonic U L1..L2
2527 | float | RD | _FFT_ULLZ1[60] | V | Interharmonic U L1..L2
2529 | float | RD | _FFT_ULLZ1[61] | V | Interharmonic U L1..L2
2531 | float | RD | _FFT_ULLZ1[62] | V | Interharmonic U L1..L2
2533 | float | RD | _FFT_ULLZ2[0] | V | Interharmonic U L2..L3
2535 | float | RD | _FFT_ULLZ2[1] | V | Interharmonic U L2..L3
2537 | float | RD | _FFT_ULLZ2[2] | V | Interharmonic U L2..L3
2539 | float | RD | _FFT_ULLZ2[3] | V | Interharmonic U L2..L3
2541 | float | RD | _FFT_ULLZ2[4] | V | Interharmonic U L2..L3
2543 | float | RD | _FFT_ULLZ2[5] | V | Interharmonic U L2..L3
2545 | float | RD | _FFT_ULLZ2[6] | V | Interharmonic U L2..L3
2547 | float | RD | _FFT_ULLZ2[7] | V | Interharmonic U L2..L3
2549 | float | RD | _FFT_ULLZ2[8] | V | Interharmonic U L2..L3
2551 | float | RD | _FFT_ULLZ2[9] | V | Interharmonic U L2..L3
2553 | float | RD | _FFT_ULLZ2[10] | V | Interharmonic U L2..L3
2555 | float | RD | _FFT_ULLZ2[11] | V | Interharmonic U L2..L3
2557 | float | RD | _FFT_ULLZ2[12] | V | Interharmonic U L2..L3
2559 | float | RD | _FFT_ULLZ2[13] | V | Interharmonic U L2..L3
2561 | float | RD | _FFT_ULLZ2[14] | V | Interharmonic U L2..L3
2563 | float | RD | _FFT_ULLZ2[15] | V | Interharmonic U L2..L3
2565 | float | RD | _FFT_ULLZ2[16] | V | Interharmonic U L2..L3
2567 | float | RD | _FFT_ULLZ2[17] | V | Interharmonic U L2..L3
2569 | float | RD | _FFT_ULLZ2[18] | V | Interharmonic U L2..L3
2571 | float | RD | _FFT_ULLZ2[19] | V | Interharmonic U L2..L3
2573 | float | RD | _FFT_ULLZ2[20] | V | Interharmonic U L2..L3
2575 | float | RD | _FFT_ULLZ2[21] | V | Interharmonic U L2..L3
2577 | float | RD | _FFT_ULLZ2[22] | V | Interharmonic U L2..L3
2579 | float | RD | _FFT_ULLZ2[23] | V | Interharmonic U L2..L3
2581 | float | RD | _FFT_ULLZ2[24] | V | Interharmonic U L2..L3
2583 | float | RD | _FFT_ULLZ2[25] | V | Interharmonic U L2..L3
2585 | float | RD | _FFT_ULLZ2[26] | V | Interharmonic U L2..L3
2587 | float | RD | _FFT_ULLZ2[27] | V | Interharmonic U L2..L3
2589 | float | RD | _FFT_ULLZ2[28] | V | Interharmonic U L2..L3
2591 | float | RD | _FFT_ULLZ2[29] | V | Interharmonic U L2..L3
2593 | float | RD | _FFT_ULLZ2[30] | V | Interharmonic U L2..L3
2595 | float | RD | _FFT_ULLZ2[31] | V | Interharmonic U L2..L3
2597 | float | RD | _FFT_ULLZ2[32] | V | Interharmonic U L2..L3
2599 | float | RD | _FFT_ULLZ2[33] | V | Interharmonic U L2..L3
2601 | float | RD | _FFT_ULLZ2[34] | V | Interharmonic U L2..L3
2603 | float | RD | _FFT_ULLZ2[35] | V | Interharmonic U L2..L3
2605 | float | RD | _FFT_ULLZ2[36] | V | Interharmonic U L2..L3
2607 | float | RD | _FFT_ULLZ2[37] | V | Interharmonic U L2..L3
2609 | float | RD | _FFT_ULLZ2[38] | V | Interharmonic U L2..L3
2611 | float | RD | _FFT_ULLZ2[39] | V | Interharmonic U L2..L3
2613 | float | RD | _FFT_ULLZ2[40] | V | Interharmonic U L2..L3
2615 | float | RD | _FFT_ULLZ2[41] | V | Interharmonic U L2..L3
2617 | float | RD | _FFT_ULLZ2[42] | V | Interharmonic U L2..L3
2619 | float | RD | _FFT_ULLZ2[43] | V | Interharmonic U L2..L3
2621 | float | RD | _FFT_ULLZ2[44] | V | Interharmonic U L2..L3
2623 | float | RD | _FFT_ULLZ2[45] | V | Interharmonic U L2..L3
2625 | float | RD | _FFT_ULLZ2[46] | V | Interharmonic U L2..L3
2627 | float | RD | _FFT_ULLZ2[47] | V | Interharmonic U L2..L3
2629 | float | RD | _FFT_ULLZ2[48] | V | Interharmonic U L2..L3
2631 | float | RD | _FFT_ULLZ2[49] | V | Interharmonic U L2..L3
2633 | float | RD | _FFT_ULLZ2[50] | V | Interharmonic U L2..L3
2635 | float | RD | _FFT_ULLZ2[51] | V | Interharmonic U L2..L3
2637 | float | RD | _FFT_ULLZ2[52] | V | Interharmonic U L2..L3
2639 | float | RD | _FFT_ULLZ2[53] | V | Interharmonic U L2..L3
2641 | float | RD | _FFT_ULLZ2[54] | V | Interharmonic U L2..L3
2643 | float | RD | _FFT_ULLZ2[55] | V | Interharmonic U L2..L3
2645 | float | RD | _FFT_ULLZ2[56] | V | Interharmonic U L2..L3
2647 | float | RD | _FFT_ULLZ2[57] | V | Interharmonic U L2..L3
2649 | float | RD | _FFT_ULLZ2[58] | V | Interharmonic U L2..L3
2651 | float | RD | _FFT_ULLZ2[59] | V | Interharmonic U L2..L3
2653 | float | RD | _FFT_ULLZ2[60] | V | Interharmonic U L2..L3
2655 | float | RD | _FFT_ULLZ2[61] | V | Interharmonic U L2..L3
2657 | float | RD | _FFT_ULLZ2[62] | V | Interharmonic U L2..L3
2659 | float | RD | _FFT_ULLZ3[0] | V | Interharmonic U L3..L1
2661 | float | RD | _FFT_ULLZ3[1] | V | Interharmonic U L3..L1
2663 | float | RD | _FFT_ULLZ3[2] | V | Interharmonic U L3..L1
2665 | float | RD | _FFT_ULLZ3[3] | V | Interharmonic U L3..L1
2667 | float | RD | _FFT_ULLZ3[4] | V | Interharmonic U L3..L1
2669 | float | RD | _FFT_ULLZ3[5] | V | Interharmonic U L3..L1
2671 | float | RD | _FFT_ULLZ3[6] | V | Interharmonic U L3..L1
2673 | float | RD | _FFT_ULLZ3[7] | V | Interharmonic U L3..L1
2675 | float | RD | _FFT_ULLZ3[8] | V | Interharmonic U L3..L1
2677 | float | RD | _FFT_ULLZ3[9] | V | Interharmonic U L3..L1
2679 | float | RD | _FFT_ULLZ3[10] | V | Interharmonic U L3..L1
2681 | float | RD | _FFT_ULLZ3[11] | V | Interharmonic U L3..L1
2683 | float | RD | _FFT_ULLZ3[12] | V | Interharmonic U L3..L1
2685 | float | RD | _FFT_ULLZ3[13] | V | Interharmonic U L3..L1
2687 | float | RD | _FFT_ULLZ3[14] | V | Interharmonic U L3..L1
2689 | float | RD | _FFT_ULLZ3[15] | V | Interharmonic U L3..L1
2691 | float | RD | _FFT_ULLZ3[16] | V | Interharmonic U L3..L1
2693 | float | RD | _FFT_ULLZ3[17] | V | Interharmonic U L3..L1
2695 | float | RD | _FFT_ULLZ3[18] | V | Interharmonic U L3..L1
2697 | float | RD | _FFT_ULLZ3[19] | V | Interharmonic U L3..L1
2699 | float | RD | _FFT_ULLZ3[20] | V | Interharmonic U L3..L1
2701 | float | RD | _FFT_ULLZ3[21] | V | Interharmonic U L3..L1
2703 | float | RD | _FFT_ULLZ3[22] | V | Interharmonic U L3..L1
2705 | float | RD | _FFT_ULLZ3[23] | V | Interharmonic U L3..L1
2707 | float | RD | _FFT_ULLZ3[24] | V | Interharmonic U L3..L1
2709 | float | RD | _FFT_ULLZ3[25] | V | Interharmonic U L3..L1
2711 | float | RD | _FFT_ULLZ3[26] | V | Interharmonic U L3..L1
2713 | float | RD | _FFT_ULLZ3[27] | V | Interharmonic U L3..L1
2715 | float | RD | _FFT_ULLZ3[28] | V | Interharmonic U L3..L1
2717 | float | RD | _FFT_ULLZ3[29] | V | Interharmonic U L3..L1
2719 | float | RD | _FFT_ULLZ3[30] | V | Interharmonic U L3..L1
2721 | float | RD | _FFT_ULLZ3[31] | V | Interharmonic U L3..L1
2723 | float | RD | _FFT_ULLZ3[32] | V | Interharmonic U L3..L1
2725 | float | RD | _FFT_ULLZ3[33] | V | Interharmonic U L3..L1
2727 | float | RD | _FFT_ULLZ3[34] | V | Interharmonic U L3..L1
2729 | float | RD | _FFT_ULLZ3[35] | V | Interharmonic U L3..L1
2731 | float | RD | _FFT_ULLZ3[36] | V | Interharmonic U L3..L1
2733 | float | RD | _FFT_ULLZ3[37] | V | Interharmonic U L3..L1
2735 | float | RD | _FFT_ULLZ3[38] | V | Interharmonic U L3..L1
2737 | float | RD | _FFT_ULLZ3[39] | V | Interharmonic U L3..L1
2739 | float | RD | _FFT_ULLZ3[40] | V | Interharmonic U L3..L1
2741 | float | RD | _FFT_ULLZ3[41] | V | Interharmonic U L3..L1
2743 | float | RD | _FFT_ULLZ3[42] | V | Interharmonic U L3..L1
2745 | float | RD | _FFT_ULLZ3[43] | V | Interharmonic U L3..L1
2747 | float | RD | _FFT_ULLZ3[44] | V | Interharmonic U L3..L1
2749 | float | RD | _FFT_ULLZ3[45] | V | Interharmonic U L3..L1
2751 | float | RD | _FFT_ULLZ3[46] | V | Interharmonic U L3..L1
2753 | float | RD | _FFT_ULLZ3[47] | V | Interharmonic U L3..L1
2755 | float | RD | _FFT_ULLZ3[48] | V | Interharmonic U L3..L1
2757 | float | RD | _FFT_ULLZ3[49] | V | Interharmonic U L3..L1
2759 | float | RD | _FFT_ULLZ3[50] | V | Interharmonic U L3..L1
2761 | float | RD | _FFT_ULLZ3[51] | V | Interharmonic U L3..L1
2763 | float | RD | _FFT_ULLZ3[52] | V | Interharmonic U L3..L1
2765 | float | RD | _FFT_ULLZ3[53] | V | Interharmonic U L3..L1
2767 | float | RD | _FFT_ULLZ3[54] | V | Interharmonic U L3..L1
2769 | float | RD | _FFT_ULLZ3[55] | V | Interharmonic U L3..L1
2771 | float | RD | _FFT_ULLZ3[56] | V | Interharmonic U L3..L1
2773 | float | RD | _FFT_ULLZ3[57] | V | Interharmonic U L3..L1
2775 | float | RD | _FFT_ULLZ3[58] | V | Interharmonic U L3..L1
2777 | float | RD | _FFT_ULLZ3[59] | V | Interharmonic U L3..L1
2779 | float | RD | _FFT_ULLZ3[60] | V | Interharmonic U L3..L1
2781 | float | RD | _FFT_ULLZ3[61] | V | Interharmonic U L3..L1
2783 | float | RD | _FFT_ULLZ3[62] | V | Interharmonic U L3..L1
2785 | float | RD | _FFT_ULZ1[0] | V | Interharmonic U L1
2787 | float | RD | _FFT_ULZ1[1] | V | Interharmonic U L1
2789 | float | RD | _FFT_ULZ1[2] | V | Interharmonic U L1
2791 | float | RD | _FFT_ULZ1[3] | V | Interharmonic U L1
2793 | float | RD | _FFT_ULZ1[4] | V | Interharmonic U L1
2795 | float | RD | _FFT_ULZ1[5] | V | Interharmonic U L1
2797 | float | RD | _FFT_ULZ1[6] | V | Interharmonic U L1
2799 | float | RD | _FFT_ULZ1[7] | V | Interharmonic U L1
2801 | float | RD | _FFT_ULZ1[8] | V | Interharmonic U L1
2803 | float | RD | _FFT_ULZ1[9] | V | Interharmonic U L1
2805 | float | RD | _FFT_ULZ1[10] | V | Interharmonic U L1
2807 | float | RD | _FFT_ULZ1[11] | V | Interharmonic U L1
2809 | float | RD | _FFT_ULZ1[12] | V | Interharmonic U L1
2811 | float | RD | _FFT_ULZ1[13] | V | Interharmonic U L1
2813 | float | RD | _FFT_ULZ1[14] | V | Interharmonic U L1
2815 | float | RD | _FFT_ULZ1[15] | V | Interharmonic U L1
2817 | float | RD | _FFT_ULZ1[16] | V | Interharmonic U L1
2819 | float | RD | _FFT_ULZ1[17] | V | Interharmonic U L1
2821 | float | RD | _FFT_ULZ1[18] | V | Interharmonic U L1
2823 | float | RD | _FFT_ULZ1[19] | V | Interharmonic U L1
2825 | float | RD | _FFT_ULZ1[20] | V | Interharmonic U L1
2827 | float | RD | _FFT_ULZ1[21] | V | Interharmonic U L1
2829 | float | RD | _FFT_ULZ1[22] | V | Interharmonic U L1
2831 | float | RD | _FFT_ULZ1[23] | V | Interharmonic U L1
2833 | float | RD | _FFT_ULZ1[24] | V | Interharmonic U L1
2835 | float | RD | _FFT_ULZ1[25] | V | Interharmonic U L1
2837 | float | RD | _FFT_ULZ1[26] | V | Interharmonic U L1
2839 | float | RD | _FFT_ULZ1[27] | V | Interharmonic U L1
2841 | float | RD | _FFT_ULZ1[28] | V | Interharmonic U L1
2843 | float | RD | _FFT_ULZ1[29] | V | Interharmonic U L1
2845 | float | RD | _FFT_ULZ1[30] | V | Interharmonic U L1
2847 | float | RD | _FFT_ULZ1[31] | V | Interharmonic U L1
2849 | float | RD | _FFT_ULZ1[32] | V | Interharmonic U L1
2851 | float | RD | _FFT_ULZ1[33] | V | Interharmonic U L1
2853 | float | RD | _FFT_ULZ1[34] | V | Interharmonic U L1
2855 | float | RD | _FFT_ULZ1[35] | V | Interharmonic U L1
2857 | float | RD | _FFT_ULZ1[36] | V | Interharmonic U L1
2859 | float | RD | _FFT_ULZ1[37] | V | Interharmonic U L1
2861 | float | RD | _FFT_ULZ1[38] | V | Interharmonic U L1
2863 | float | RD | _FFT_ULZ1[39] | V | Interharmonic U L1
2865 | float | RD | _FFT_ULZ1[40] | V | Interharmonic U L1
2867 | float | RD | _FFT_ULZ1[41] | V | Interharmonic U L1
2869 | float | RD | _FFT_ULZ1[42] | V | Interharmonic U L1
2871 | float | RD | _FFT_ULZ1[43] | V | Interharmonic U L1
2873 | float | RD | _FFT_ULZ1[44] | V | Interharmonic U L1
2875 | float | RD | _FFT_ULZ1[45] | V | Interharmonic U L1
2877 | float | RD | _FFT_ULZ1[46] | V | Interharmonic U L1
2879 | float | RD | _FFT_ULZ1[47] | V | Interharmonic U L1
2881 | float | RD | _FFT_ULZ1[48] | V | Interharmonic U L1
2883 | float | RD | _FFT_ULZ1[49] | V | Interharmonic U L1
2885 | float | RD | _FFT_ULZ1[50] | V | Interharmonic U L1
2887 | float | RD | _FFT_ULZ1[51] | V | Interharmonic U L1
2889 | float | RD | _FFT_ULZ1[52] | V | Interharmonic U L1
2891 | float | RD | _FFT_ULZ1[53] | V | Interharmonic U L1
2893 | float | RD | _FFT_ULZ1[54] | V | Interharmonic U L1
2895 | float | RD | _FFT_ULZ1[55] | V | Interharmonic U L1
2897 | float | RD | _FFT_ULZ1[56] | V | Interharmonic U L1
2899 | float | RD | _FFT_ULZ1[57] | V | Interharmonic U L1
2901 | float | RD | _FFT_ULZ1[58] | V | Interharmonic U L1
2903 | float | RD | _FFT_ULZ1[59] | V | Interharmonic U L1
2905 | float | RD | _FFT_ULZ1[60] | V | Interharmonic U L1
2907 | float | RD | _FFT_ULZ1[61] | V | Interharmonic U L1
2909 | float | RD | _FFT_ULZ1[62] | V | Interharmonic U L1
2911 | float | RD | _FFT_ULZ2[0] | V | Interharmonic U L2
2913 | float | RD | _FFT_ULZ2[1] | V | Interharmonic U L2
2915 | float | RD | _FFT_ULZ2[2] | V | Interharmonic U L2
2917 | float | RD | _FFT_ULZ2[3] | V | Interharmonic U L2
2919 | float | RD | _FFT_ULZ2[4] | V | Interharmonic U L2
2921 | float | RD | _FFT_ULZ2[5] | V | Interharmonic U L2
2923 | float | RD | _FFT_ULZ2[6] | V | Interharmonic U L2
2925 | float | RD | _FFT_ULZ2[7] | V | Interharmonic U L2
2927 | float | RD | _FFT_ULZ2[8] | V | Interharmonic U L2
2929 | float | RD | _FFT_ULZ2[9] | V | Interharmonic U L2
2931 | float | RD | _FFT_ULZ2[10] | V | Interharmonic U L2
2933 | float | RD | _FFT_ULZ2[11] | V | Interharmonic U L2
2935 | float | RD | _FFT_ULZ2[12] | V | Interharmonic U L2
2937 | float | RD | _FFT_ULZ2[13] | V | Interharmonic U L2
2939 | float | RD | _FFT_ULZ2[14] | V | Interharmonic U L2
2941 | float | RD | _FFT_ULZ2[15] | V | Interharmonic U L2
2943 | float | RD | _FFT_ULZ2[16] | V | Interharmonic U L2
2945 | float | RD | _FFT_ULZ2[17] | V | Interharmonic U L2
2947 | float | RD | _FFT_ULZ2[18] | V | Interharmonic U L2
2949 | float | RD | _FFT_ULZ2[19] | V | Interharmonic U L2
2951 | float | RD | _FFT_ULZ2[20] | V | Interharmonic U L2
2953 | float | RD | _FFT_ULZ2[21] | V | Interharmonic U L2
2955 | float | RD | _FFT_ULZ2[22] | V | Interharmonic U L2
2957 | float | RD | _FFT_ULZ2[23] | V | Interharmonic U L2
2959 | float | RD | _FFT_ULZ2[24] | V | Interharmonic U L2
2961 | float | RD | _FFT_ULZ2[25] | V | Interharmonic U L2
2963 | float | RD | _FFT_ULZ2[26] | V | Interharmonic U L2
2965 | float | RD | _FFT_ULZ2[27] | V | Interharmonic U L2
2967 | float | RD | _FFT_ULZ2[28] | V | Interharmonic U L2
2969 | float | RD | _FFT_ULZ2[29] | V | Interharmonic U L2
2971 | float | RD | _FFT_ULZ2[30] | V | Interharmonic U L2
2973 | float | RD | _FFT_ULZ2[31] | V | Interharmonic U L2
2975 | float | RD | _FFT_ULZ2[32] | V | Interharmonic U L2
2977 | float | RD | _FFT_ULZ2[33] | V | Interharmonic U L2
2979 | float | RD | _FFT_ULZ2[34] | V | Interharmonic U L2
2981 | float | RD | _FFT_ULZ2[35] | V | Interharmonic U L2
2983 | float | RD | _FFT_ULZ2[36] | V | Interharmonic U L2
2985 | float | RD | _FFT_ULZ2[37] | V | Interharmonic U L2
2987 | float | RD | _FFT_ULZ2[38] | V | Interharmonic U L2
2989 | float | RD | _FFT_ULZ2[39] | V | Interharmonic U L2
2991 | float | RD | _FFT_ULZ2[40] | V | Interharmonic U L2
2993 | float | RD | _FFT_ULZ2[41] | V | Interharmonic U L2
2995 | float | RD | _FFT_ULZ2[42] | V | Interharmonic U L2
2997 | float | RD | _FFT_ULZ2[43] | V | Interharmonic U L2
2999 | float | RD | _FFT_ULZ2[44] | V | Interharmonic U L2
3001 | float | RD | _FFT_ULZ2[45] | V | Interharmonic U L2
3003 | float | RD | _FFT_ULZ2[46] | V | Interharmonic U L2
3005 | float | RD | _FFT_ULZ2[47] | V | Interharmonic U L2
3007 | float | RD | _FFT_ULZ2[48] | V | Interharmonic U L2
3009 | float | RD | _FFT_ULZ2[49] | V | Interharmonic U L2
3011 | float | RD | _FFT_ULZ2[50] | V | Interharmonic U L2
3013 | float | RD | _FFT_ULZ2[51] | V | Interharmonic U L2
3015 | float | RD | _FFT_ULZ2[52] | V | Interharmonic U L2
3017 | float | RD | _FFT_ULZ2[53] | V | Interharmonic U L2
3019 | float | RD | _FFT_ULZ2[54] | V | Interharmonic U L2
3021 | float | RD | _FFT_ULZ2[55] | V | Interharmonic U L2
3023 | float | RD | _FFT_ULZ2[56] | V | Interharmonic U L2
3025 | float | RD | _FFT_ULZ2[57] | V | Interharmonic U L2
3027 | float | RD | _FFT_ULZ2[58] | V | Interharmonic U L2
3029 | float | RD | _FFT_ULZ2[59] | V | Interharmonic U L2
3031 | float | RD | _FFT_ULZ2[60] | V | Interharmonic U L2
3033 | float | RD | _FFT_ULZ2[61] | V | Interharmonic U L2
3035 | float | RD | _FFT_ULZ2[62] | V | Interharmonic U L2
3037 | float | RD | _FFT_ULZ3[0] | V | Interharmonic U L3
3039 | float | RD | _FFT_ULZ3[1] | V | Interharmonic U L3
3041 | float | RD | _FFT_ULZ3[2] | V | Interharmonic U L3
3043 | float | RD | _FFT_ULZ3[3] | V | Interharmonic U L3
3045 | float | RD | _FFT_ULZ3[4] | V | Interharmonic U L3
3047 | float | RD | _FFT_ULZ3[5] | V | Interharmonic U L3
3049 | float | RD | _FFT_ULZ3[6] | V | Interharmonic U L3
3051 | float | RD | _FFT_ULZ3[7] | V | Interharmonic U L3
3053 | float | RD | _FFT_ULZ3[8] | V | Interharmonic U L3
3055 | float | RD | _FFT_ULZ3[9] | V | Interharmonic U L3
3057 | float | RD | _FFT_ULZ3[10] | V | Interharmonic U L3
3059 | float | RD | _FFT_ULZ3[11] | V | Interharmonic U L3
3061 | float | RD | _FFT_ULZ3[12] | V | Interharmonic U L3
3063 | float | RD | _FFT_ULZ3[13] | V | Interharmonic U L3
3065 | float | RD | _FFT_ULZ3[14] | V | Interharmonic U L3
3067 | float | RD | _FFT_ULZ3[15] | V | Interharmonic U L3
3069 | float | RD | _FFT_ULZ3[16] | V | Interharmonic U L3
3071 | float | RD | _FFT_ULZ3[17] | V | Interharmonic U L3
3073 | float | RD | _FFT_ULZ3[18] | V | Interharmonic U L3
3075 | float | RD | _FFT_ULZ3[19] | V | Interharmonic U L3
3077 | float | RD | _FFT_ULZ3[20] | V | Interharmonic U L3
3079 | float | RD | _FFT_ULZ3[21] | V | Interharmonic U L3
3081 | float | RD | _FFT_ULZ3[22] | V | Interharmonic U L3
3083 | float | RD | _FFT_ULZ3[23] | V | Interharmonic U L3
3085 | float | RD | _FFT_ULZ3[24] | V | Interharmonic U L3
3087 | float | RD | _FFT_ULZ3[25] | V | Interharmonic U L3
3089 | float | RD | _FFT_ULZ3[26] | V | Interharmonic U L3
3091 | float | RD | _FFT_ULZ3[27] | V | Interharmonic U L3
3093 | float | RD | _FFT_ULZ3[28] | V | Interharmonic U L3
3095 | float | RD | _FFT_ULZ3[29] | V | Interharmonic U L3
3097 | float | RD | _FFT_ULZ3[30] | V | Interharmonic U L3
3099 | float | RD | _FFT_ULZ3[31] | V | Interharmonic U L3
3101 | float | RD | _FFT_ULZ3[32] | V | Interharmonic U L3
3103 | float | RD | _FFT_ULZ3[33] | V | Interharmonic U L3
3105 | float | RD | _FFT_ULZ3[34] | V | Interharmonic U L3
3107 | float | RD | _FFT_ULZ3[35] | V | Interharmonic U L3
3109 | float | RD | _FFT_ULZ3[36] | V | Interharmonic U L3
3111 | float | RD | _FFT_ULZ3[37] | V | Interharmonic U L3
3113 | float | RD | _FFT_ULZ3[38] | V | Interharmonic U L3
3115 | float | RD | _FFT_ULZ3[39] | V | Interharmonic U L3
3117 | float | RD | _FFT_ULZ3[40] | V | Interharmonic U L3
3119 | float | RD | _FFT_ULZ3[41] | V | Interharmonic U L3
3121 | float | RD | _FFT_ULZ3[42] | V | Interharmonic U L3
3123 | float | RD | _FFT_ULZ3[43] | V | Interharmonic U L3
3125 | float | RD | _FFT_ULZ3[44] | V | Interharmonic U L3
3127 | float | RD | _FFT_ULZ3[45] | V | Interharmonic U L3
3129 | float | RD | _FFT_ULZ3[46] | V | Interharmonic U L3
3131 | float | RD | _FFT_ULZ3[47] | V | Interharmonic U L3
3133 | float | RD | _FFT_ULZ3[48] | V | Interharmonic U L3
3135 | float | RD | _FFT_ULZ3[49] | V | Interharmonic U L3
3137 | float | RD | _FFT_ULZ3[50] | V | Interharmonic U L3
3139 | float | RD | _FFT_ULZ3[51] | V | Interharmonic U L3
3141 | float | RD | _FFT_ULZ3[52] | V | Interharmonic U L3
3143 | float | RD | _FFT_ULZ3[53] | V | Interharmonic U L3
3145 | float | RD | _FFT_ULZ3[54] | V | Interharmonic U L3
3147 | float | RD | _FFT_ULZ3[55] | V | Interharmonic U L3
3149 | float | RD | _FFT_ULZ3[56] | V | Interharmonic U L3
3151 | float | RD | _FFT_ULZ3[57] | V | Interharmonic U L3
3153 | float | RD | _FFT_ULZ3[58] | V | Interharmonic U L3
3155 | float | RD | _FFT_ULZ3[59] | V | Interharmonic U L3
3157 | float | RD | _FFT_ULZ3[60] | V | Interharmonic U L3
3159 | float | RD | _FFT_ULZ3[61] | V | Interharmonic U L3
3161 | float | RD | _FFT_ULZ3[62] | V | Interharmonic U L3
3163 | float | RD | _FFT_ULZ4[0] | V | Interharmonic U L4
3165 | float | RD | _FFT_ULZ4[1] | V | Interharmonic U L4
3167 | float | RD | _FFT_ULZ4[2] | V | Interharmonic U L4
3169 | float | RD | _FFT_ULZ4[3] | V | Interharmonic U L4
3171 | float | RD | _FFT_ULZ4[4] | V | Interharmonic U L4
3173 | float | RD | _FFT_ULZ4[5] | V | Interharmonic U L4
3175 | float | RD | _FFT_ULZ4[6] | V | Interharmonic U L4
3177 | float | RD | _FFT_ULZ4[7] | V | Interharmonic U L4
3179 | float | RD | _FFT_ULZ4[8] | V | Interharmonic U L4
3181 | float | RD | _FFT_ULZ4[9] | V | Interharmonic U L4
3183 | float | RD | _FFT_ULZ4[10] | V | Interharmonic U L4
3185 | float | RD | _FFT_ULZ4[11] | V | Interharmonic U L4
3187 | float | RD | _FFT_ULZ4[12] | V | Interharmonic U L4
3189 | float | RD | _FFT_ULZ4[13] | V | Interharmonic U L4
3191 | float | RD | _FFT_ULZ4[14] | V | Interharmonic U L4
3193 | float | RD | _FFT_ULZ4[15] | V | Interharmonic U L4
3195 | float | RD | _FFT_ULZ4[16] | V | Interharmonic U L4
3197 | float | RD | _FFT_ULZ4[17] | V | Interharmonic U L4
3199 | float | RD | _FFT_ULZ4[18] | V | Interharmonic U L4
3201 | float | RD | _FFT_ULZ4[19] | V | Interharmonic U L4
3203 | float | RD | _FFT_ULZ4[20] | V | Interharmonic U L4
3205 | float | RD | _FFT_ULZ4[21] | V | Interharmonic U L4
3207 | float | RD | _FFT_ULZ4[22] | V | Interharmonic U L4
3209 | float | RD | _FFT_ULZ4[23] | V | Interharmonic U L4
3211 | float | RD | _FFT_ULZ4[24] | V | Interharmonic U L4
3213 | float | RD | _FFT_ULZ4[25] | V | Interharmonic U L4
3215 | float | RD | _FFT_ULZ4[26] | V | Interharmonic U L4
3217 | float | RD | _FFT_ULZ4[27] | V | Interharmonic U L4
3219 | float | RD | _FFT_ULZ4[28] | V | Interharmonic U L4
3221 | float | RD | _FFT_ULZ4[29] | V | Interharmonic U L4
3223 | float | RD | _FFT_ULZ4[30] | V | Interharmonic U L4
3225 | float | RD | _FFT_ULZ4[31] | V | Interharmonic U L4
3227 | float | RD | _FFT_ULZ4[32] | V | Interharmonic U L4
3229 | float | RD | _FFT_ULZ4[33] | V | Interharmonic U L4
3231 | float | RD | _FFT_ULZ4[34] | V | Interharmonic U L4
3233 | float | RD | _FFT_ULZ4[35] | V | Interharmonic U L4
3235 | float | RD | _FFT_ULZ4[36] | V | Interharmonic U L4
3237 | float | RD | _FFT_ULZ4[37] | V | Interharmonic U L4
3239 | float | RD | _FFT_ULZ4[38] | V | Interharmonic U L4
3241 | float | RD | _FFT_ULZ4[39] | V | Interharmonic U L4
3243 | float | RD | _FFT_ULZ4[40] | V | Interharmonic U L4
3245 | float | RD | _FFT_ULZ4[41] | V | Interharmonic U L4
3247 | float | RD | _FFT_ULZ4[42] | V | Interharmonic U L4
3249 | float | RD | _FFT_ULZ4[43] | V | Interharmonic U L4
3251 | float | RD | _FFT_ULZ4[44] | V | Interharmonic U L4
3253 | float | RD | _FFT_ULZ4[45] | V | Interharmonic U L4
3255 | float | RD | _FFT_ULZ4[46] | V | Interharmonic U L4
3257 | float | RD | _FFT_ULZ4[47] | V | Interharmonic U L4
3259 | float | RD | _FFT_ULZ4[48] | V | Interharmonic U L4
3261 | float | RD | _FFT_ULZ4[49] | V | Interharmonic U L4
3263 | float | RD | _FFT_ULZ4[50] | V | Interharmonic U L4
3265 | float | RD | _FFT_ULZ4[51] | V | Interharmonic U L4
3267 | float | RD | _FFT_ULZ4[52] | V | Interharmonic U L4
3269 | float | RD | _FFT_ULZ4[53] | V | Interharmonic U L4
3271 | float | RD | _FFT_ULZ4[54] | V | Interharmonic U L4
3273 | float | RD | _FFT_ULZ4[55] | V | Interharmonic U L4
3275 | float | RD | _FFT_ULZ4[56] | V | Interharmonic U L4
3277 | float | RD | _FFT_ULZ4[57] | V | Interharmonic U L4
3279 | float | RD | _FFT_ULZ4[58] | V | Interharmonic U L4
3281 | float | RD | _FFT_ULZ4[59] | V | Interharmonic U L4
3283 | float | RD | _FFT_ULZ4[60] | V | Interharmonic U L4
3285 | float | RD | _FFT_ULZ4[61] | V | Interharmonic U L4
3287 | float | RD | _FFT_ULZ4[62] | V | Interharmonic U L4
3289 | float | RD | _FFT_ILZ1[0] | A | Interharmonic I L1
3291 | float | RD | _FFT_ILZ1[1] | A | Interharmonic I L1
3293 | float | RD | _FFT_ILZ1[2] | A | Interharmonic I L1
3295 | float | RD | _FFT_ILZ1[3] | A | Interharmonic I L1
3297 | float | RD | _FFT_ILZ1[4] | A | Interharmonic I L1
3299 | float | RD | _FFT_ILZ1[5] | A | Interharmonic I L1
3301 | float | RD | _FFT_ILZ1[6] | A | Interharmonic I L1
3303 | float | RD | _FFT_ILZ1[7] | A | Interharmonic I L1
3305 | float | RD | _FFT_ILZ1[8] | A | Interharmonic I L1
3307 | float | RD | _FFT_ILZ1[9] | A | Interharmonic I L1
3309 | float | RD | _FFT_ILZ1[10] | A | Interharmonic I L1
3311 | float | RD | _FFT_ILZ1[11] | A | Interharmonic I L1
3313 | float | RD | _FFT_ILZ1[12] | A | Interharmonic I L1
3315 | float | RD | _FFT_ILZ1[13] | A | Interharmonic I L1
3317 | float | RD | _FFT_ILZ1[14] | A | Interharmonic I L1
3319 | float | RD | _FFT_ILZ1[15] | A | Interharmonic I L1
3321 | float | RD | _FFT_ILZ1[16] | A | Interharmonic I L1
3323 | float | RD | _FFT_ILZ1[17] | A | Interharmonic I L1
3325 | float | RD | _FFT_ILZ1[18] | A | Interharmonic I L1
3327 | float | RD | _FFT_ILZ1[19] | A | Interharmonic I L1
3329 | float | RD | _FFT_ILZ1[20] | A | Interharmonic I L1
3331 | float | RD | _FFT_ILZ1[21] | A | Interharmonic I L1
3333 | float | RD | _FFT_ILZ1[22] | A | Interharmonic I L1
3335 | float | RD | _FFT_ILZ1[23] | A | Interharmonic I L1
3337 | float | RD | _FFT_ILZ1[24] | A | Interharmonic I L1
3339 | float | RD | _FFT_ILZ1[25] | A | Interharmonic I L1
3341 | float | RD | _FFT_ILZ1[26] | A | Interharmonic I L1
3343 | float | RD | _FFT_ILZ1[27] | A | Interharmonic I L1
3345 | float | RD | _FFT_ILZ1[28] | A | Interharmonic I L1
3347 | float | RD | _FFT_ILZ1[29] | A | Interharmonic I L1
3349 | float | RD | _FFT_ILZ1[30] | A | Interharmonic I L1
3351 | float | RD | _FFT_ILZ1[31] | A | Interharmonic I L1
3353 | float | RD | _FFT_ILZ1[32] | A | Interharmonic I L1
3355 | float | RD | _FFT_ILZ1[33] | A | Interharmonic I L1
3357 | float | RD | _FFT_ILZ1[34] | A | Interharmonic I L1
3359 | float | RD | _FFT_ILZ1[35] | A | Interharmonic I L1
3361 | float | RD | _FFT_ILZ1[36] | A | Interharmonic I L1
3363 | float | RD | _FFT_ILZ1[37] | A | Interharmonic I L1
3365 | float | RD | _FFT_ILZ1[38] | A | Interharmonic I L1
3367 | float | RD | _FFT_ILZ1[39] | A | Interharmonic I L1
3369 | float | RD | _FFT_ILZ1[40] | A | Interharmonic I L1
3371 | float | RD | _FFT_ILZ1[41] | A | Interharmonic I L1
3373 | float | RD | _FFT_ILZ1[42] | A | Interharmonic I L1
3375 | float | RD | _FFT_ILZ1[43] | A | Interharmonic I L1
3377 | float | RD | _FFT_ILZ1[44] | A | Interharmonic I L1
3379 | float | RD | _FFT_ILZ1[45] | A | Interharmonic I L1
3381 | float | RD | _FFT_ILZ1[46] | A | Interharmonic I L1
3383 | float | RD | _FFT_ILZ1[47] | A | Interharmonic I L1
3385 | float | RD | _FFT_ILZ1[48] | A | Interharmonic I L1
3387 | float | RD | _FFT_ILZ1[49] | A | Interharmonic I L1
3389 | float | RD | _FFT_ILZ1[50] | A | Interharmonic I L1
3391 | float | RD | _FFT_ILZ1[51] | A | Interharmonic I L1
3393 | float | RD | _FFT_ILZ1[52] | A | Interharmonic I L1
3395 | float | RD | _FFT_ILZ1[53] | A | Interharmonic I L1
3397 | float | RD | _FFT_ILZ1[54] | A | Interharmonic I L1
3399 | float | RD | _FFT_ILZ1[55] | A | Interharmonic I L1
3401 | float | RD | _FFT_ILZ1[56] | A | Interharmonic I L1
3403 | float | RD | _FFT_ILZ1[57] | A | Interharmonic I L1
3405 | float | RD | _FFT_ILZ1[58] | A | Interharmonic I L1
3407 | float | RD | _FFT_ILZ1[59] | A | Interharmonic I L1
3409 | float | RD | _FFT_ILZ1[60] | A | Interharmonic I L1
3411 | float | RD | _FFT_ILZ1[61] | A | Interharmonic I L1
3413 | float | RD | _FFT_ILZ1[62] | A | Interharmonic I L1
3415 | float | RD | _FFT_ILZ2[0] | A | Interharmonic I L2
3417 | float | RD | _FFT_ILZ2[1] | A | Interharmonic I L2
3419 | float | RD | _FFT_ILZ2[2] | A | Interharmonic I L2
3421 | float | RD | _FFT_ILZ2[3] | A | Interharmonic I L2
3423 | float | RD | _FFT_ILZ2[4] | A | Interharmonic I L2
3425 | float | RD | _FFT_ILZ2[5] | A | Interharmonic I L2
3427 | float | RD | _FFT_ILZ2[6] | A | Interharmonic I L2
3429 | float | RD | _FFT_ILZ2[7] | A | Interharmonic I L2
3431 | float | RD | _FFT_ILZ2[8] | A | Interharmonic I L2
3433 | float | RD | _FFT_ILZ2[9] | A | Interharmonic I L2
3435 | float | RD | _FFT_ILZ2[10] | A | Interharmonic I L2
3437 | float | RD | _FFT_ILZ2[11] | A | Interharmonic I L2
3439 | float | RD | _FFT_ILZ2[12] | A | Interharmonic I L2
3441 | float | RD | _FFT_ILZ2[13] | A | Interharmonic I L2
3443 | float | RD | _FFT_ILZ2[14] | A | Interharmonic I L2
3445 | float | RD | _FFT_ILZ2[15] | A | Interharmonic I L2
3447 | float | RD | _FFT_ILZ2[16] | A | Interharmonic I L2
3449 | float | RD | _FFT_ILZ2[17] | A | Interharmonic I L2
3451 | float | RD | _FFT_ILZ2[18] | A | Interharmonic I L2
3453 | float | RD | _FFT_ILZ2[19] | A | Interharmonic I L2
3455 | float | RD | _FFT_ILZ2[20] | A | Interharmonic I L2
3457 | float | RD | _FFT_ILZ2[21] | A | Interharmonic I L2
3459 | float | RD | _FFT_ILZ2[22] | A | Interharmonic I L2
3461 | float | RD | _FFT_ILZ2[23] | A | Interharmonic I L2
3463 | float | RD | _FFT_ILZ2[24] | A | Interharmonic I L2
3465 | float | RD | _FFT_ILZ2[25] | A | Interharmonic I L2
3467 | float | RD | _FFT_ILZ2[26] | A | Interharmonic I L2
3469 | float | RD | _FFT_ILZ2[27] | A | Interharmonic I L2
3471 | float | RD | _FFT_ILZ2[28] | A | Interharmonic I L2
3473 | float | RD | _FFT_ILZ2[29] | A | Interharmonic I L2
3475 | float | RD | _FFT_ILZ2[30] | A | Interharmonic I L2
3477 | float | RD | _FFT_ILZ2[31] | A | Interharmonic I L2
3479 | float | RD | _FFT_ILZ2[32] | A | Interharmonic I L2
3481 | float | RD | _FFT_ILZ2[33] | A | Interharmonic I L2
3483 | float | RD | _FFT_ILZ2[34] | A | Interharmonic I L2
3485 | float | RD | _FFT_ILZ2[35] | A | Interharmonic I L2
3487 | float | RD | _FFT_ILZ2[36] | A | Interharmonic I L2
3489 | float | RD | _FFT_ILZ2[37] | A | Interharmonic I L2
3491 | float | RD | _FFT_ILZ2[38] | A | Interharmonic I L2
3493 | float | RD | _FFT_ILZ2[39] | A | Interharmonic I L2
3495 | float | RD | _FFT_ILZ2[40] | A | Interharmonic I L2
3497 | float | RD | _FFT_ILZ2[41] | A | Interharmonic I L2
3499 | float | RD | _FFT_ILZ2[42] | A | Interharmonic I L2
3501 | float | RD | _FFT_ILZ2[43] | A | Interharmonic I L2
3503 | float | RD | _FFT_ILZ2[44] | A | Interharmonic I L2
3505 | float | RD | _FFT_ILZ2[45] | A | Interharmonic I L2
3507 | float | RD | _FFT_ILZ2[46] | A | Interharmonic I L2
3509 | float | RD | _FFT_ILZ2[47] | A | Interharmonic I L2
3511 | float | RD | _FFT_ILZ2[48] | A | Interharmonic I L2
3513 | float | RD | _FFT_ILZ2[49] | A | Interharmonic I L2
3515 | float | RD | _FFT_ILZ2[50] | A | Interharmonic I L2
3517 | float | RD | _FFT_ILZ2[51] | A | Interharmonic I L2
3519 | float | RD | _FFT_ILZ2[52] | A | Interharmonic I L2
3521 | float | RD | _FFT_ILZ2[53] | A | Interharmonic I L2
3523 | float | RD | _FFT_ILZ2[54] | A | Interharmonic I L2
3525 | float | RD | _FFT_ILZ2[55] | A | Interharmonic I L2
3527 | float | RD | _FFT_ILZ2[56] | A | Interharmonic I L2
3529 | float | RD | _FFT_ILZ2[57] | A | Interharmonic I L2
3531 | float | RD | _FFT_ILZ2[58] | A | Interharmonic I L2
3533 | float | RD | _FFT_ILZ2[59] | A | Interharmonic I L2
3535 | float | RD | _FFT_ILZ2[60] | A | Interharmonic I L2
3537 | float | RD | _FFT_ILZ2[61] | A | Interharmonic I L2
3539 | float | RD | _FFT_ILZ2[62] | A | Interharmonic I L2
3541 | float | RD | _FFT_ILZ3[0] | A | Interharmonic I L3
3543 | float | RD | _FFT_ILZ3[1] | A | Interharmonic I L3
3545 | float | RD | _FFT_ILZ3[2] | A | Interharmonic I L3
3547 | float | RD | _FFT_ILZ3[3] | A | Interharmonic I L3
3549 | float | RD | _FFT_ILZ3[4] | A | Interharmonic I L3
3551 | float | RD | _FFT_ILZ3[5] | A | Interharmonic I L3
3553 | float | RD | _FFT_ILZ3[6] | A | Interharmonic I L3
3555 | float | RD | _FFT_ILZ3[7] | A | Interharmonic I L3
3557 | float | RD | _FFT_ILZ3[8] | A | Interharmonic I L3
3559 | float | RD | _FFT_ILZ3[9] | A | Interharmonic I L3
3561 | float | RD | _FFT_ILZ3[10] | A | Interharmonic I L3
3563 | float | RD | _FFT_ILZ3[11] | A | Interharmonic I L3
3565 | float | RD | _FFT_ILZ3[12] | A | Interharmonic I L3
3567 | float | RD | _FFT_ILZ3[13] | A | Interharmonic I L3
3569 | float | RD | _FFT_ILZ3[14] | A | Interharmonic I L3
3571 | float | RD | _FFT_ILZ3[15] | A | Interharmonic I L3
3573 | float | RD | _FFT_ILZ3[16] | A | Interharmonic I L3
3575 | float | RD | _FFT_ILZ3[17] | A | Interharmonic I L3
3577 | float | RD | _FFT_ILZ3[18] | A | Interharmonic I L3
3579 | float | RD | _FFT_ILZ3[19] | A | Interharmonic I L3
3581 | float | RD | _FFT_ILZ3[20] | A | Interharmonic I L3
3583 | float | RD | _FFT_ILZ3[21] | A | Interharmonic I L3
3585 | float | RD | _FFT_ILZ3[22] | A | Interharmonic I L3
3587 | float | RD | _FFT_ILZ3[23] | A | Interharmonic I L3
3589 | float | RD | _FFT_ILZ3[24] | A | Interharmonic I L3
3591 | float | RD | _FFT_ILZ3[25] | A | Interharmonic I L3
3593 | float | RD | _FFT_ILZ3[26] | A | Interharmonic I L3
3595 | float | RD | _FFT_ILZ3[27] | A | Interharmonic I L3
3597 | float | RD | _FFT_ILZ3[28] | A | Interharmonic I L3
3599 | float | RD | _FFT_ILZ3[29] | A | Interharmonic I L3
3601 | float | RD | _FFT_ILZ3[30] | A | Interharmonic I L3
3603 | float | RD | _FFT_ILZ3[31] | A | Interharmonic I L3
3605 | float | RD | _FFT_ILZ3[32] | A | Interharmonic I L3
3607 | float | RD | _FFT_ILZ3[33] | A | Interharmonic I L3
3609 | float | RD | _FFT_ILZ3[34] | A | Interharmonic I L3
3611 | float | RD | _FFT_ILZ3[35] | A | Interharmonic I L3
3613 | float | RD | _FFT_ILZ3[36] | A | Interharmonic I L3
3615 | float | RD | _FFT_ILZ3[37] | A | Interharmonic I L3
3617 | float | RD | _FFT_ILZ3[38] | A | Interharmonic I L3
3619 | float | RD | _FFT_ILZ3[39] | A | Interharmonic I L3
3621 | float | RD | _FFT_ILZ3[40] | A | Interharmonic I L3
3623 | float | RD | _FFT_ILZ3[41] | A | Interharmonic I L3
3625 | float | RD | _FFT_ILZ3[42] | A | Interharmonic I L3
3627 | float | RD | _FFT_ILZ3[43] | A | Interharmonic I L3
3629 | float | RD | _FFT_ILZ3[44] | A | Interharmonic I L3
3631 | float | RD | _FFT_ILZ3[45] | A | Interharmonic I L3
3633 | float | RD | _FFT_ILZ3[46] | A | Interharmonic I L3
3635 | float | RD | _FFT_ILZ3[47] | A | Interharmonic I L3
3637 | float | RD | _FFT_ILZ3[48] | A | Interharmonic I L3
3639 | float | RD | _FFT_ILZ3[49] | A | Interharmonic I L3
3641 | float | RD | _FFT_ILZ3[50] | A | Interharmonic I L3
3643 | float | RD | _FFT_ILZ3[51] | A | Interharmonic I L3
3645 | float | RD | _FFT_ILZ3[52] | A | Interharmonic I L3
3647 | float | RD | _FFT_ILZ3[53] | A | Interharmonic I L3
3649 | float | RD | _FFT_ILZ3[54] | A | Interharmonic I L3
3651 | float | RD | _FFT_ILZ3[55] | A | Interharmonic I L3
3653 | float | RD | _FFT_ILZ3[56] | A | Interharmonic I L3
3655 | float | RD | _FFT_ILZ3[57] | A | Interharmonic I L3
3657 | float | RD | _FFT_ILZ3[58] | A | Interharmonic I L3
3659 | float | RD | _FFT_ILZ3[59] | A | Interharmonic I L3
3661 | float | RD | _FFT_ILZ3[60] | A | Interharmonic I L3
3663 | float | RD | _FFT_ILZ3[61] | A | Interharmonic I L3
3665 | float | RD | _FFT_ILZ3[62] | A | Interharmonic I L3
3667 | float | RD | _FFT_ILZ4[0] | A | Interharmonic I L4
3669 | float | RD | _FFT_ILZ4[1] | A | Interharmonic I L4
3671 | float | RD | _FFT_ILZ4[2] | A | Interharmonic I L4
3673 | float | RD | _FFT_ILZ4[3] | A | Interharmonic I L4
3675 | float | RD | _FFT_ILZ4[4] | A | Interharmonic I L4
3677 | float | RD | _FFT_ILZ4[5] | A | Interharmonic I L4
3679 | float | RD | _FFT_ILZ4[6] | A | Interharmonic I L4
3681 | float | RD | _FFT_ILZ4[7] | A | Interharmonic I L4
3683 | float | RD | _FFT_ILZ4[8] | A | Interharmonic I L4
3685 | float | RD | _FFT_ILZ4[9] | A | Interharmonic I L4
3687 | float | RD | _FFT_ILZ4[10] | A | Interharmonic I L4
3689 | float | RD | _FFT_ILZ4[11] | A | Interharmonic I L4
3691 | float | RD | _FFT_ILZ4[12] | A | Interharmonic I L4
3693 | float | RD | _FFT_ILZ4[13] | A | Interharmonic I L4
3695 | float | RD | _FFT_ILZ4[14] | A | Interharmonic I L4
3697 | float | RD | _FFT_ILZ4[15] | A | Interharmonic I L4
3699 | float | RD | _FFT_ILZ4[16] | A | Interharmonic I L4
3701 | float | RD | _FFT_ILZ4[17] | A | Interharmonic I L4
3703 | float | RD | _FFT_ILZ4[18] | A | Interharmonic I L4
3705 | float | RD | _FFT_ILZ4[19] | A | Interharmonic I L4
3707 | float | RD | _FFT_ILZ4[20] | A | Interharmonic I L4
3709 | float | RD | _FFT_ILZ4[21] | A | Interharmonic I L4
3711 | float | RD | _FFT_ILZ4[22] | A | Interharmonic I L4
3713 | float | RD | _FFT_ILZ4[23] | A | Interharmonic I L4
3715 | float | RD | _FFT_ILZ4[24] | A | Interharmonic I L4
3717 | float | RD | _FFT_ILZ4[25] | A | Interharmonic I L4
3719 | float | RD | _FFT_ILZ4[26] | A | Interharmonic I L4
3721 | float | RD | _FFT_ILZ4[27] | A | Interharmonic I L4
3723 | float | RD | _FFT_ILZ4[28] | A | Interharmonic I L4
3725 | float | RD | _FFT_ILZ4[29] | A | Interharmonic I L4
3727 | float | RD | _FFT_ILZ4[30] | A | Interharmonic I L4
3729 | float | RD | _FFT_ILZ4[31] | A | Interharmonic I L4
3731 | float | RD | _FFT_ILZ4[32] | A | Interharmonic I L4
3733 | float | RD | _FFT_ILZ4[33] | A | Interharmonic I L4
3735 | float | RD | _FFT_ILZ4[34] | A | Interharmonic I L4
3737 | float | RD | _FFT_ILZ4[35] | A | Interharmonic I L4
3739 | float | RD | _FFT_ILZ4[36] | A | Interharmonic I L4
3741 | float | RD | _FFT_ILZ4[37] | A | Interharmonic I L4
3743 | float | RD | _FFT_ILZ4[38] | A | Interharmonic I L4
3745 | float | RD | _FFT_ILZ4[39] | A | Interharmonic I L4
3747 | float | RD | _FFT_ILZ4[40] | A | Interharmonic I L4
3749 | float | RD | _FFT_ILZ4[41] | A | Interharmonic I L4
3751 | float | RD | _FFT_ILZ4[42] | A | Interharmonic I L4
3753 | float | RD | _FFT_ILZ4[43] | A | Interharmonic I L4
3755 | float | RD | _FFT_ILZ4[44] | A | Interharmonic I L4
3757 | float | RD | _FFT_ILZ4[45] | A | Interharmonic I L4
3759 | float | RD | _FFT_ILZ4[46] | A | Interharmonic I L4
3761 | float | RD | _FFT_ILZ4[47] | A | Interharmonic I L4
3763 | float | RD | _FFT_ILZ4[48] | A | Interharmonic I L4
3765 | float | RD | _FFT_ILZ4[49] | A | Interharmonic I L4
3767 | float | RD | _FFT_ILZ4[50] | A | Interharmonic I L4
3769 | float | RD | _FFT_ILZ4[51] | A | Interharmonic I L4
3771 | float | RD | _FFT_ILZ4[52] | A | Interharmonic I L4
3773 | float | RD | _FFT_ILZ4[53] | A | Interharmonic I L4
3775 | float | RD | _FFT_ILZ4[54] | A | Interharmonic I L4
3777 | float | RD | _FFT_ILZ4[55] | A | Interharmonic I L4
3779 | float | RD | _FFT_ILZ4[56] | A | Interharmonic I L4
3781 | float | RD | _FFT_ILZ4[57] | A | Interharmonic I L4
3783 | float | RD | _FFT_ILZ4[58] | A | Interharmonic I L4
3785 | float | RD | _FFT_ILZ4[59] | A | Interharmonic I L4
3787 | float | RD | _FFT_ILZ4[60] | A | Interharmonic I L4
3789 | float | RD | _FFT_ILZ4[61] | A | Interharmonic I L4
3791 | float | RD | _FFT_ILZ4[62] | A | Interharmonic I L4